## Instructions
1 | 2 | 3 | 4 | 5 | 6 | 7 | 0. Run eQUEST prior to using spreadsheet; be sure to zero the EIR, HIR, and kW of any CHW/HW equipment that will be represented in TRNSYS. Leave the EM1 and FM1 hourly reports in, and add hourly reports so that all the following reports are run:
Time | Circulation Loop | Circulation Loop | Weather | Weather | Meter | Meter
Hour | CHW loop coil loads | HW loop coil loads | Outside dry-bulb | Outside wet-bulb | Electric Total | Fuel Total
hr | Btu/hr | Btu/hr | F | F | kW | Btu/hr
1 | 120563 | -215622 | 27 | 25 | 128.263 | 4051.92 | 1. Paste your hourly report from eQUEST onto the 'eQUEST Output' tab.
2 | 120336 | -221116 | 26 | 24 | 92.4522 | 4051.91
3 | 120171 | -228892 | 24 | 22 | 94.0586 | 4051.93 | 2. Copy columns A --> G into a blank notebook; save to the same directory as the TRNSYS model, with the name 'eQUEST_output_DHRC.txt'
4 | 119955 | -232156 | 23 | 22 | 94.6017 | 4051.99
5 | 119798 | -235136 | 22 | 21 | 95.0266 | 4052.08
6 | 119759 | -238247 | 21 | 20 | 95.3949 | 4052.16 | 3. Open the TRNSYS model. Using the calculator icon in the upper left, establish the following inputs (where unknown, leave defaults):
7 | 119679 | -240070 | 21 | 20 | 94.1662 | 4052.23
8 | 119627 | -240466 | 21 | 20 | 90.9951 | 4052.29
9 | 119646 | -243073 | 21 | 20 | 89.4999 | 4052.35 |  | Variable | Input method |  | TRNSYS variable
10 | 119859 | -210747 | 23 | 22 | 86.0694 | 4052.4 |  | Peak cooling, building | 2250.7 | MBH | Peak_Clg_Bldg_MBH
11 | 121852 | -191191 | 26 | 24 | 83.7116 | 4052.54 |  | Peak heating, building | 2685.41 | MBH | Peak_Htg_Bldg_MBH
12 | 120263 | -180512 | 28 | 26 | 83.107 | 4052.61 |  | Gas rate | manual | $/therm | GasRate_per_therm
13 | 122189 | -170105 | 29 | 27 | 82.1504 | 4052.63 |  | Electricity rate | manual | $/kWh | ElecRate_per_kWh
14 | 120431 | -157738 | 31 | 28 | 79.8842 | 4052.62 |  | Peak CHW load on geo plant | 2250.7 | MBH | Peak_CHW_MBH
15 | 122184 | -184884 | 32 | 28 | 83.7521 | 4052.62 |  | Peak HW load on geo plant | 1685.41 | MBH | Peak_HW_MBH
16 | 120581 | -188223 | 30 | 28 | 84.5917 | 4052.6 |  | Percent hybrid | manual | % (base 100) | Hybrid_Percent
17 | 120544 | -210854 | 29 | 26 | 90.5311 | 4052.62 |  | Length of GHX | manual | ft | Length_GHX
18 | 120419 | -226934 | 27 | 25 | 96.8884 | 4052.71 |  | Ground conductivity | manual | Btu/hr-ft-F | Ground_Conduct
19 | 120322 | -238841 | 25 | 23 | 98.9403 | 4052.8 |  | Ground temperature | manual | F | Ground_Temp
20 | 120212 | -252066 | 22 | 21 | 100.841 | 4052.93 |  | Ground diffusivity | manual | ft2/day | Ground_Diff
21 | 120012 | -260374 | 20 | 19 | 101.799 | 4053.07
22 | 126050 | -270277 | 18 | 17 | 104.045 | 4053.21 | 4. Run TRNSYS
23 | 119631 | -258881 | 16 | 15 | 101.111 | 4053.35
24 | 120547 | -295802 | 14 | 13 | 104.589 | 4053.48 | 5. Use Excel to open the 'To_Joint_Template.out' file (in the same folder as the TRNSYS model). Copy the six key results (all in row 3) over to the Joint Template, into their corresponding row in the 'Results Input' tab.
25 | 119153 | -312642 | 13 | 12 | 104.477 | 4053.54
26 | 122366 | -335767 | 12 | 11 | 107.402 | 4053.7
27 | 118754 | -332674 | 11 | 10 | 107.759 | 4053.88
28 | 128301 | -347856 | 10 | 10 | 110.921 | 4054.06
29 | 118368 | -319416 | 10 | 9 | 106.205 | 4054.21
30 | 120973 | -364077 | 9 | 8 | 111.534 | 4054.32
31 | 118006 | -364332 | 9 | 9 | 111.432 | 4054.35
32 | 120309 | -376493 | 10 | 9 | 110.61 | 4054.49
33 | 118001 | -320222 | 10 | 9 | 100.725 | 4054.65
34 | 119147 | -282985 | 13 | 12 | 94.1244 | 4054.8
35 | 118501 | -289271 | 15 | 14 | 94.6805 | 4054.87
36 | 118477 | -257567 | 18 | 16 | 90.9454 | 4054.8
37 | 120275 | -228347 | 20 | 18 | 87.672 | 4054.76
38 | 119035 | -207924 | 22 | 20 | 85.1111 | 4054.78
39 | 120555 | -198128 | 24 | 21 | 84.3299 | 4054.73
40 | 119325 | -201619 | 22 | 20 | 85.0706 | 4054.58
41 | 119019 | -226698 | 20 | 18 | 91.733 | 4054.49
42 | 118990 | -274462 | 18 | 16 | 102.621 | 4054.45
43 | 118639 | -298603 | 16 | 14 | 106.595 | 4054.64
44 | 118440 | -315770 | 13 | 12 | 109.689 | 4054.79
45 | 120631 | -327235 | 11 | 10 | 111.611 | 4054.97
46 | 118026 | -327227 | 9 | 8 | 112.972 | 4055.12
47 | 117813 | -321977 | 7 | 7 | 110.993 | 4055.25
48 | 119618 | -333519 | 5 | 5 | 112.541 | 4055.35
49 | 117670 | -335824 | 3 | 2 | 116.037 | 10681.4
50 | 118831 | -347277 | 0 | 0 | 117.844 | 10681.5
51 | 117292 | -350917 | -2 | -2 | 118.939 | 10681
52 | 118182 | -351101 | 1 | 0 | 119.102 | 10680.9
53 | 119986 | -351945 | 3 | 3 | 122.509 | 11854.6
54 | 166789 | -338896 | 6 | 6 | 157.072 | 28703.9
55 | 305303 | -1433240 | 6 | 5 | 320.349 | 84954.2
56 | 367828 | -1300390 | 5 | 5 | 339.061 | 103167
57 | 387677 | -1139240 | 5 | 4 | 321.783 | 142762
58 | 386128 | -1074430 | 7 | 5 | 315.601 | 167981
59 | 367853 | -1074460 | 8 | 7 | 308.621 | 171576
60 | 345883 | -974292 | 10 | 8 | 291.475 | 171573
61 | 342213 | -950717 | 10 | 8 | 288.632 | 171571
62 | 375524 | -912674 | 10 | 8 | 300.902 | 171568
63 | 394683 | -891492 | 10 | 7 | 305.113 | 169350
64 | 398254 | -910585 | 9 | 7 | 317.25 | 153953
65 | 388815 | -943384 | 9 | 7 | 323.665 | 125661
66 | 367033 | -1019410 | 8 | 6 | 310.466 | 94226.9
67 | 297345 | -1049960 | 6 | 4 | 243.697 | 58326.7
68 | 201758 | -19590.2 | 4 | 2 | 132.638 | 41720.9
69 | 168765 | -149477 | 2 | 0 | 116.306 | 37024.6
70 | 151793 | -223935 | 1 | 0 | 108.255 | 22716.8
71 | 140389 | -277702 | 1 | -1 | 109.792 | 12216.8
72 | 133460 | -299116 | 0 | -1 | 109.465 | 10630.8
73 | 131531 | -322900 | -2 | -3 | 113.307 | 10635.1
74 | 130251 | -338855 | -3 | -4 | 116.806 | 10638.6
75 | 129156 | -362905 | -5 | -6 | 121.929 | 10641.6
76 | 128145 | -376803 | -6 | -7 | 123.187 | 10644.3
77 | 129850 | -402389 | -7 | -8 | 128.762 | 11820.6
78 | 175604 | -381720 | -8 | -9 | 165.602 | 28672.4
79 | 312087 | -1574940 | -7 | -8 | 326.407 | 84925
80 | 374471 | -1447620 | -6 | -7 | 345.444 | 103138
81 | 394248 | -1249830 | -5 | -6 | 327.022 | 142741
82 | 392053 | -1168730 | -3 | -4 | 320.418 | 167962
83 | 373238 | -1140590 | -1 | -2 | 310.951 | 171557
84 | 346503 | -1001250 | 1 | 0 | 290.628 | 171556
85 | 346925 | -989077 | 2 | 0 | 273.038 | 171554
86 | 379839 | -920188 | 2 | 1 | 278.926 | 171552
87 | 399008 | -895142 | 3 | 1 | 284.631 | 169333
88 | 402271 | -966075 | 0 | -2 | 290.599 | 153937
89 | 393840 | -1095600 | -4 | -5 | 306.557 | 125647
90 | 369188 | -1202490 | -7 | -8 | 315.305 | 94213.9
91 | 320385 | -1194250 | -8 | -9 | 250.668 | 58314.6
92 | 203939 | -40766 | -10 | -10 | 133.365 | 41709.1
93 | 177187 | -168662 | -11 | -12 | 117.279 | 37012.7
94 | 154820 | -222363 | -12 | -13 | 109.873 | 22702.8
95 | 146794 | -281517 | -14 | -14 | 111.13 | 12202.1
96 | 136062 | -292794 | -15 | -15 | 110.043 | 10615.2
97 | 137116 | -321855 | -16 | -16 | 114.068 | 10618.9
98 | 132465 | -336032 | -17 | -17 | 117.453 | 10621.7
99 | 131042 | -396128 | -18 | -18 | 124.543 | 10624.1
100 | 129719 | -390349 | -18 | -19 | 124.948 | 10626.2
101 | 136538 | -463836 | -19 | -19 | 133.185 | 11803.2
102 | 176230 | -427696 | -19 | -19 | 169.53 | 28655.9
103 | 312393 | -1685320 | -16 | -16 | 329.958 | 84909.5
104 | 374823 | -1552780 | -13 | -14 | 350.04 | 103124
105 | 394761 | -1344900 | -10 | -11 | 333.75 | 142731
106 | 392619 | -1232730 | -5 | -6 | 323.661 | 167953
107 | 373920 | -1134840 | 0 | -1 | 310.46 | 171549
108 | 347287 | -945266 | 5 | 4 | 288.068 | 171548
109 | 347844 | -896470 | 8 | 6 | 283.984 | 171545
110 | 380985 | -808688 | 10 | 9 | 292.313 | 171541
111 | 400054 | -751993 | 13 | 11 | 277.918 | 169323
112 | 403332 | -787772 | 14 | 12 | 282.13 | 153926
113 | 393803 | -810128 | 14 | 13 | 314.141 | 125635
114 | 374039 | -851689 | 15 | 13 | 300.391 | 94202.7
115 | 296033 | -852350 | 16 | 14 | 231.797 | 58303.1
116 | 209330 | -19328.4 | 17 | 15 | 133.423 | 41697.2
117 | 176805 | -84196.4 | 18 | 15 | 117.221 | 37001.3
118 | 159409 | -128262 | 18 | 16 | 105.319 | 22691
119 | 146162 | -164481 | 17 | 16 | 96.3766 | 12190
120 | 140682 | -183039 | 17 | 16 | 92.5477 | 10603.3
121 | 139561 | -202807 | 16 | 15 | 95.3674 | 10607.4
122 | 137265 | -214647 | 15 | 14 | 96.9211 | 10610.5
123 | 136149 | -231795 | 14 | 13 | 98.3653 | 10613.3
124 | 135177 | -240270 | 13 | 12 | 99.5477 | 10615.6
125 | 137217 | -257156 | 11 | 10 | 105.037 | 11791.7
126 | 183699 | -228342 | 10 | 9 | 136.109 | 28643.3
127 | 317045 | -1163920 | 10 | 9 | 303.225 | 84895.7
128 | 379001 | -1066430 | 9 | 9 | 324.068 | 103109
129 | 398269 | -940523 | 9 | 9 | 310.019 | 142723
130 | 396255 | -865404 | 12 | 11 | 303.839 | 167942
131 | 377693 | -832883 | 15 | 14 | 294.843 | 171538
132 | 364091 | -755693 | 18 | 16 | 278.118 | 171537
133 | 351613 | -697300 | 21 | 19 | 254.892 | 171535
134 | 384918 | -605176 | 24 | 22 | 264.579 | 171532
135 | 403570 | -540796 | 27 | 25 | 266.234 | 169313
136 | 406549 | -517838 | 29 | 26 | 268.398 | 153916
137 | 397480 | -519454 | 30 | 28 | 279.528 | 125625
138 | 382880 | -529478 | 32 | 29 | 263.967 | 94191.3
139 | 296539 | -565257 | 32 | 30 | 212.653 | 58291.4
140 | 178953 | -16209.7 | 33 | 30 | 127.6 | 41685.5
141 | 159900 | -25380.5 | 33 | 30 | 112.313 | 36990.8
142 | 171524 | -35937.7 | 33 | 30 | 107.008 | 22678
143 | 153552 | -63739.5 | 32 | 30 | 97.7021 | 12175.4
144 | 147066 | -73312.9 | 32 | 29 | 93.7119 | 10588.3
145 | 144027 | -90810.5 | 31 | 28 | 88.768 | 10592
146 | 142166 | -106252 | 30 | 27 | 88.5912 | 10594.8
147 | 140849 | -122385 | 29 | 26 | 88.4397 | 10598.1
148 | 139813 | -135343 | 28 | 26 | 88.3208 | 10600.5
149 | 138713 | -147368 | 27 | 25 | 88.1937 | 10602.9
150 | 137719 | -159029 | 26 | 24 | 88.0776 | 10605
151 | 136786 | -169738 | 25 | 23 | 86.3687 | 10607.1
152 | 123879 | -999557 | 25 | 23 | 157.929 | 10609.1
153 | 127013 | -847437 | 24 | 22 | 146.042 | 10610.9
154 | 122753 | -681091 | 26 | 24 | 133.279 | 10596
155 | 122294 | -590689 | 29 | 26 | 127.058 | 10593.5
156 | 121833 | -528240 | 31 | 27 | 122.505 | 10591.8
157 | 121414 | -497010 | 31 | 28 | 104.229 | 10590.7
158 | 121011 | -472768 | 32 | 28 | 99.2657 | 10589.9
159 | 122226 | -17367.3 | 32 | 28 | 77.1651 | 10589.3
160 | 120344 | -22780.7 | 29 | 26 | 77.2187 | 10588.9
161 | 144254 | -44837.9 | 27 | 24 | 88.0767 | 10593.1
162 | 139306 | -55285.2 | 24 | 22 | 92.5316 | 10595.6
163 | 141222 | -77597.2 | 23 | 22 | 93.5649 | 10598.5
164 | 134038 | -85422.8 | 23 | 21 | 92.9641 | 10601.6
165 | 133254 | -111665 | 22 | 21 | 92.7244 | 10604.1
166 | 131100 | -128799 | 21 | 20 | 92.4804 | 10606.1
167 | 130732 | -149999 | 21 | 19 | 91.5511 | 10608.5
168 | 129660 | -161200 | 20 | 19 | 90.6456 | 10610.8
169 | 128894 | -172257 | 21 | 19 | 86.0335 | 3987.05
170 | 128339 | -180576 | 21 | 20 | 88.4977 | 3989.16
171 | 127761 | -184423 | 22 | 21 | 88.9565 | 3991.35
172 | 128120 | -188886 | 25 | 23 | 89.4588 | 3993.41
173 | 127208 | -185277 | 28 | 25 | 89.4092 | 3995.34
174 | 127385 | -179986 | 31 | 27 | 89.0106 | 3997.18
175 | 126918 | -175528 | 32 | 29 | 86.9334 | 3998.91
176 | 126683 | -170112 | 33 | 30 | 82.0103 | 4000.53
177 | 127050 | -144230 | 34 | 31 | 80.3672 | 4001.99
178 | 127661 | -109601 | 36 | 32 | 80.4934 | 4003.31
179 | 128425 | -89499.1 | 37 | 34 | 80.6053 | 4004.57
180 | 130032 | -80861.9 | 39 | 34 | 80.7889 | 4005.64
181 | 131061 | -75243.3 | 40 | 35 | 80.9352 | 4006.29
182 | 131162 | -67828.9 | 40 | 36 | 81.0079 | 4006.41
183 | 131836 | -65862.4 | 41 | 36 | 81.0976 | 4006.57
184 | 131205 | -65673.2 | 40 | 36 | 81.1882 | 4007.01
185 | 129681 | -70519 | 40 | 36 | 85.6047 | 4007.28
186 | 128190 | -81731.1 | 39 | 36 | 89.7022 | 4007.84
187 | 127245 | -88349 | 39 | 36 | 90.414 | 4008.7
188 | 126654 | -98029.2 | 38 | 36 | 90.3553 | 4009.91
189 | 126255 | -105788 | 38 | 36 | 90.3092 | 4011.03
190 | 126190 | -116996 | 37 | 35 | 90.2891 | 4012.19
191 | 125924 | -120383 | 37 | 35 | 89.4607 | 4013.24
192 | 125972 | -126579 | 36 | 34 | 88.6566 | 4014.24
193 | 125901 | -127155 | 35 | 33 | 91.6093 | 10641.2
194 | 125902 | -131921 | 35 | 32 | 91.5821 | 10642.1
195 | 125763 | -137960 | 34 | 31 | 91.5617 | 10642.2
196 | 125664 | -144381 | 33 | 30 | 91.5376 | 10642.8
197 | 128825 | -153926 | 31 | 29 | 95.3606 | 11817.1
198 | 176326 | -124246 | 30 | 27 | 136.52 | 28667.2
199 | 311470 | -849102 | 31 | 28 | 286.075 | 84918.1
200 | 373817 | -732149 | 31 | 27 | 307.617 | 103130
201 | 392773 | -567527 | 32 | 27 | 290.135 | 142737
202 | 391781 | -471628 | 34 | 29 | 264.699 | 167955
203 | 382472 | -414373 | 37 | 31 | 256.272 | 171550
204 | 385012 | -362588 | 39 | 32 | 242.39 | 171547
205 | 358409 | -325190 | 39 | 32 | 239.42 | 171544
206 | 398809 | -299804 | 38 | 32 | 258.313 | 171542
207 | 418993 | -294200 | 38 | 31 | 266.303 | 169323
208 | 403729 | -303423 | 36 | 30 | 266.83 | 153924
209 | 396845 | -373666 | 33 | 29 | 275.09 | 125631
210 | 385527 | -464673 | 31 | 27 | 259.984 | 94197.6
211 | 297146 | -502566 | 31 | 28 | 209.235 | 58297.9
212 | 176588 | -13765.5 | 31 | 28 | 127.418 | 41692.8
213 | 157639 | -19153.6 | 31 | 28 | 111.978 | 36998.1
214 | 167612 | -33528.4 | 31 | 29 | 106.834 | 22685.4
215 | 152198 | -46043.6 | 32 | 29 | 97.6555 | 12182.4
216 | 145426 | -60978.3 | 32 | 29 | 93.6403 | 10595.2
217 | 142727 | -70539.6 | 32 | 29 | 92.387 | 10598.9
218 | 140994 | -80997 | 31 | 29 | 92.2341 | 10601.6
219 | 139672 | -92382.9 | 31 | 29 | 92.1015 | 10604
220 | 138838 | -101980 | 31 | 29 | 92.0097 | 10606.1
221 | 141174 | -109306 | 30 | 29 | 96.2139 | 11781.8
222 | 188696 | -93293.9 | 30 | 28 | 137.251 | 28632.9
223 | 319908 | -744013 | 30 | 29 | 278.879 | 84884.9
224 | 381924 | -667293 | 30 | 29 | 303.771 | 103098
225 | 400555 | -556968 | 30 | 28 | 293.052 | 142716
226 | 398820 | -497335 | 32 | 30 | 264.176 | 167934
227 | 385435 | -407872 | 35 | 32 | 255.85 | 171530
228 | 375507 | -338364 | 37 | 33 | 241.535 | 171528
229 | 354421 | -331241 | 37 | 32 | 238.848 | 171526
230 | 387515 | -293118 | 36 | 32 | 257.038 | 171523
231 | 405818 | -282858 | 36 | 31 | 264.6 | 169304
232 | 408784 | -331866 | 34 | 30 | 266.839 | 153905
233 | 402992 | -376360 | 33 | 29 | 274.911 | 125613
234 | 390920 | -461045 | 31 | 28 | 260.121 | 94180.3
235 | 306145 | -518337 | 29 | 26 | 210.694 | 58280.5
236 | 180423 | -15087.9 | 26 | 24 | 127.807 | 41675.8
237 | 161352 | -21733.9 | 24 | 21 | 112.408 | 36981.3
238 | 171592 | -44859.7 | 24 | 21 | 106.838 | 22668.6
239 | 155903 | -69058.9 | 23 | 21 | 97.6639 | 12166.1
240 | 148945 | -85775.4 | 23 | 21 | 93.648 | 10579.6
241 | 146008 | -105650 | 22 | 20 | 92.7479 | 10583.9
242 | 144110 | -120078 | 21 | 20 | 92.5653 | 10587.3
243 | 142566 | -134890 | 20 | 19 | 92.3899 | 10590.3
244 | 141432 | -148547 | 21 | 19 | 92.2555 | 10592.9
245 | 143525 | -159204 | 21 | 20 | 95.9871 | 11769.1
246 | 190625 | -135170 | 22 | 20 | 136.902 | 28620.8
247 | 321274 | -887121 | 22 | 21 | 287.346 | 84873.2
248 | 383177 | -787193 | 23 | 22 | 310.969 | 103087
249 | 402015 | -674768 | 23 | 22 | 301.801 | 142706
250 | 399911 | -603934 | 24 | 23 | 291.238 | 167925
251 | 385915 | -585767 | 24 | 23 | 282.247 | 171522
252 | 371091 | -500994 | 25 | 24 | 264.04 | 171521
253 | 354642 | -487832 | 25 | 24 | 261.649 | 171519
254 | 387755 | -430335 | 26 | 24 | 257.179 | 171517
255 | 406178 | -418209 | 26 | 23 | 265.149 | 169298
256 | 408817 | -479607 | 22 | 20 | 267.409 | 153901
257 | 402094 | -585283 | 17 | 16 | 297.28 | 125611
258 | 387637 | -722444 | 13 | 12 | 292.48 | 94179.7
259 | 314996 | -742464 | 14 | 13 | 225.04 | 58281.9
260 | 180096 | -19262.4 | 15 | 14 | 127.211 | 41677.4
261 | 185710 | -45599.4 | 16 | 15 | 118.199 | 36981.7
262 | 167608 | -78358 | 17 | 16 | 106.177 | 22668.5
263 | 153534 | -107357 | 18 | 17 | 97.1558 | 12167.1
264 | 147190 | -125489 | 19 | 18 | 93.2139 | 10580.2
265 | 144845 | -134964 | 21 | 20 | 92.2568 | 10584.4
266 | 143379 | -144319 | 22 | 22 | 92.169 | 10587.8
267 | 142220 | -146417 | 24 | 23 | 92.1116 | 10590.7
268 | 142548 | -146177 | 27 | 25 | 92.1726 | 10593.2
269 | 143691 | -140927 | 29 | 27 | 96.0464 | 11769.2
270 | 191346 | -106978 | 32 | 28 | 137.164 | 28620.7
271 | 322171 | -717969 | 33 | 29 | 278.343 | 84872.8
272 | 383985 | -629934 | 33 | 29 | 301.761 | 103086
273 | 402525 | -502678 | 34 | 29 | 273.913 | 142703
274 | 400863 | -450087 | 36 | 31 | 268.323 | 167922
275 | 391981 | -434187 | 37 | 33 | 257.372 | 171517
276 | 393742 | -392641 | 39 | 34 | 242.997 | 171515
277 | 364300 | -371276 | 39 | 35 | 239.3 | 171513
278 | 406819 | -332235 | 39 | 35 | 259.968 | 171511
279 | 430013 | -325321 | 39 | 36 | 268.029 | 169293
280 | 409715 | -362851 | 34 | 31 | 270.73 | 153895
281 | 401931 | -445271 | 29 | 27 | 278.357 | 125603
282 | 395957 | -579146 | 24 | 22 | 285.958 | 94169.8
283 | 311670 | -634527 | 22 | 20 | 218.059 | 58270.8
284 | 181271 | -18045.2 | 20 | 18 | 127.552 | 41666.7
285 | 188698 | -36795.4 | 18 | 16 | 118.601 | 36972
286 | 169699 | -66530.2 | 18 | 16 | 106.414 | 22659.4
287 | 155314 | -105491 | 17 | 16 | 97.3394 | 12158.1
288 | 148709 | -128992 | 17 | 15 | 93.2894 | 10571.7
289 | 145959 | -150734 | 16 | 14 | 92.4146 | 10576.3
290 | 144144 | -169608 | 14 | 13 | 92.2388 | 10580
291 | 142607 | -188765 | 13 | 11 | 92.0569 | 10583.3
292 | 141230 | -207452 | 11 | 9 | 95.6635 | 10586.2
293 | 142803 | -229897 | 8 | 7 | 101.801 | 11762.7
294 | 189049 | -221887 | 6 | 5 | 136.277 | 28614.9
295 | 319892 | -1168060 | 5 | 4 | 303.043 | 84867.8
296 | 381816 | -1104780 | 5 | 3 | 325.937 | 103082
297 | 400995 | -956205 | 4 | 3 | 311.399 | 142701
298 | 398633 | -891590 | 5 | 4 | 305.999 | 167922
299 | 379769 | -866372 | 7 | 5 | 295.83 | 171519
300 | 354750 | -766954 | 8 | 6 | 277.672 | 171519
301 | 353042 | -736103 | 10 | 8 | 274.029 | 171518
302 | 385915 | -663055 | 12 | 10 | 284.717 | 171515
303 | 404775 | -634948 | 14 | 11 | 290.019 | 169297
304 | 407736 | -681385 | 12 | 9 | 275.997 | 153901
305 | 397577 | -775711 | 9 | 7 | 306.112 | 125611
306 | 380243 | -891615 | 7 | 5 | 301.504 | 94179.7
307 | 316958 | -932312 | 6 | 5 | 236.063 | 58281.3
308 | 212644 | -19524.7 | 6 | 4 | 133.352 | 41676.2
309 | 179579 | -103144 | 5 | 4 | 117.053 | 36980.4
310 | 163116 | -164249 | 4 | 3 | 105.174 | 22669.1
311 | 149467 | -208695 | 3 | 2 | 96.2517 | 12168.6
312 | 143618 | -235051 | 2 | 1 | 100.633 | 10582.3
313 | 140762 | -270746 | -1 | -2 | 100.69 | 10587
314 | 138757 | -294688 | -3 | -4 | 104.331 | 10590.8
315 | 136992 | -325646 | -6 | -7 | 109.251 | 10595
316 | 135369 | -348078 | -9 | -10 | 114.546 | 10598.5
317 | 133841 | -379347 | -11 | -12 | 119.313 | 10602
318 | 132392 | -406857 | -14 | -15 | 121.314 | 10605.4
319 | 131082 | -432290 | -15 | -16 | 121.82 | 10608.9
320 | 120854 | -1630510 | -16 | -17 | 200.372 | 10612.3
321 | 120059 | -1444810 | -17 | -18 | 188.453 | 10615.1
322 | 119340 | -1271390 | -15 | -16 | 175.482 | 10595.2
323 | 118651 | -1192500 | -14 | -14 | 169.701 | 10592.4
324 | 118026 | -1134200 | -12 | -13 | 164.907 | 10589.8
325 | 117419 | -1113470 | -12 | -13 | 161.821 | 10588.8
326 | 116834 | -1085000 | -11 | -12 | 157.92 | 10588.1
327 | 149367 | -42673.6 | -11 | -12 | 81.8847 | 10587.6
328 | 131941 | -184873 | -12 | -13 | 81.4846 | 10587.7
329 | 128069 | -236831 | -13 | -14 | 89.9954 | 10597.3
330 | 128687 | -342331 | -14 | -15 | 116.485 | 10604
331 | 124399 | -381017 | -15 | -16 | 125.198 | 10609.5
332 | 125185 | -420987 | -16 | -17 | 127.713 | 10614.2
333 | 122293 | -444149 | -17 | -18 | 129.89 | 10618.2
334 | 122649 | -474786 | -18 | -18 | 131.887 | 10621.9
335 | 120878 | -487955 | -18 | -19 | 131.854 | 10624.8
336 | 121815 | -507654 | -19 | -20 | 132.578 | 10626.8
337 | 119465 | -532007 | -19 | -20 | 129.312 | 4002.63
338 | 119700 | -549038 | -20 | -20 | 130.206 | 4004.27
339 | 118309 | -557557 | -20 | -21 | 130.83 | 4005.94
340 | 118783 | -571832 | -21 | -22 | 131.914 | 4007.46
341 | 117212 | -579484 | -22 | -23 | 132.659 | 4008.93
342 | 117098 | -593697 | -23 | -24 | 133.677 | 4010.33
343 | 116194 | -600593 | -23 | -23 | 132.724 | 4011.7
344 | 116217 | -599173 | -22 | -23 | 130.123 | 4013.01
345 | 115850 | -541696 | -22 | -23 | 124.917 | 4014.28
346 | 116088 | -482086 | -20 | -21 | 121.201 | 4015.51
347 | 116773 | -442719 | -18 | -19 | 118.247 | 4016.65
348 | 117131 | -414686 | -16 | -17 | 116.386 | 4017.6
349 | 116622 | -390201 | -15 | -16 | 114.452 | 4018.55
350 | 116689 | -373889 | -14 | -15 | 112.73 | 4019.4
351 | 117397 | -363817 | -13 | -14 | 111.179 | 4020.17
352 | 115984 | -360947 | -14 | -15 | 111.474 | 4020.92
353 | 115558 | -397740 | -15 | -16 | 118.467 | 4021.74
354 | 119287 | -480654 | -16 | -17 | 128.507 | 4022.7
355 | 114545 | -498876 | -17 | -17 | 131.213 | 4023.63
356 | 118665 | -537333 | -17 | -18 | 133.511 | 4024.63
357 | 113744 | -536720 | -18 | -19 | 133.915 | 4025.62
358 | 116431 | -560423 | -18 | -19 | 135.304 | 4026.57
359 | 113175 | -556249 | -18 | -19 | 134.396 | 4027.47
360 | 115604 | -571898 | -18 | -19 | 134.554 | 4028.32
361 | 112728 | -577863 | -16 | -17 | 132.579 | 4029.15
362 | 114496 | -584081 | -14 | -15 | 132.453 | 4029.92
363 | 112562 | -576032 | -12 | -13 | 131.871 | 4030.66
364 | 114320 | -572931 | -9 | -10 | 131.373 | 4031.35
365 | 112679 | -559344 | -6 | -7 | 130.417 | 4032.01
366 | 114720 | -549231 | -3 | -4 | 129.379 | 4032.63
367 | 112949 | -535113 | -2 | -3 | 126.863 | 4033.21
368 | 113091 | -521929 | 0 | -2 | 123.282 | 4033.78
369 | 114324 | -502059 | 1 | 0 | 121.052 | 4034.31
370 | 113566 | -470973 | 3 | 2 | 119.206 | 4034.82
371 | 115580 | -444672 | 6 | 4 | 116.861 | 4035.31
372 | 114263 | -422159 | 8 | 6 | 115.315 | 4035.75
373 | 114647 | -375708 | 11 | 9 | 111.694 | 4036.17
374 | 117318 | -350797 | 14 | 11 | 106.777 | 4036.54
375 | 115389 | -314809 | 17 | 14 | 99.2285 | 4036.89
376 | 118551 | -316755 | 17 | 14 | 98.8927 | 4037.19
377 | 115794 | -328486 | 17 | 15 | 105.763 | 4037.52
378 | 117237 | -352020 | 17 | 15 | 115.091 | 4037.84
379 | 115922 | -349712 | 18 | 16 | 115.821 | 4038.2
380 | 117553 | -350693 | 19 | 17 | 116.075 | 4038.58
381 | 116187 | -342081 | 20 | 18 | 114.912 | 4038.96
382 | 117472 | -335691 | 22 | 20 | 113.619 | 4039.31
383 | 116674 | -323421 | 24 | 22 | 110.94 | 4039.64
384 | 116854 | -311571 | 26 | 23 | 108.29 | 4039.93
385 | 117425 | -306022 | 26 | 24 | 111.618 | 10666.2
386 | 117727 | -296014 | 27 | 24 | 108.989 | 10666.5
387 | 119263 | -294040 | 27 | 25 | 108.626 | 10666.2
388 | 118086 | -289384 | 26 | 24 | 108.082 | 10666.3
389 | 121408 | -292702 | 25 | 24 | 112.419 | 11840.1
390 | 168712 | -248944 | 24 | 23 | 143.028 | 28689.7
391 | 306029 | -1145190 | 24 | 23 | 306.651 | 84940.2
392 | 368783 | -954507 | 25 | 23 | 322.026 | 103153
393 | 388095 | -802734 | 25 | 23 | 305.035 | 142752
394 | 387054 | -665885 | 28 | 25 | 295.291 | 167971
395 | 371311 | -609748 | 30 | 27 | 284.29 | 171566
396 | 353875 | -502547 | 33 | 29 | 264.145 | 171564
397 | 344232 | -466576 | 34 | 30 | 260.771 | 171561
398 | 377952 | -386607 | 36 | 31 | 257.116 | 171558
399 | 398852 | -358245 | 37 | 32 | 264.369 | 169339
400 | 399852 | -366743 | 36 | 32 | 266.06 | 153940
401 | 393090 | -402919 | 35 | 31 | 271.523 | 125648
402 | 379776 | -480686 | 34 | 30 | 280.505 | 94214
403 | 293896 | -539073 | 34 | 30 | 211.751 | 58313.6
404 | 173740 | -15354.7 | 33 | 30 | 127.361 | 41708.1
405 | 154801 | -22277.3 | 33 | 30 | 112.031 | 37013
406 | 162295 | -40450.7 | 33 | 30 | 106.389 | 22700.7
407 | 147189 | -66714.9 | 32 | 30 | 97.2576 | 12197.9
408 | 140704 | -77949.2 | 32 | 30 | 93.275 | 10610.7
409 | 138246 | -88063.5 | 33 | 31 | 92.4019 | 10614.1
410 | 137327 | -99736.9 | 33 | 32 | 92.3266 | 10616.8
411 | 136086 | -105304 | 34 | 33 | 92.2348 | 10619.1
412 | 136131 | -109452 | 36 | 34 | 92.2467 | 10621
413 | 138440 | -108190 | 37 | 36 | 96.0831 | 11796.3
414 | 186375 | -78188.3 | 39 | 38 | 137.301 | 28647.2
415 | 318733 | -647464 | 39 | 38 | 273.781 | 84898.6
416 | 417626 | -582320 | 40 | 38 | 298.453 | 103111
417 | 433692 | -462595 | 40 | 39 | 275.957 | 142727
418 | 430382 | -431426 | 40 | 39 | 268.373 | 167944
419 | 416694 | -404300 | 41 | 39 | 258.048 | 171539
420 | 405930 | -382729 | 41 | 39 | 243.498 | 171536
421 | 378789 | -346061 | 41 | 38 | 240.341 | 171533
422 | 417712 | -303102 | 41 | 38 | 260.04 | 171530
423 | 439988 | -290440 | 41 | 37 | 268.145 | 169311
424 | 414840 | -302116 | 37 | 33 | 267.327 | 153912
425 | 403244 | -393105 | 32 | 30 | 271.056 | 125619
426 | 393742 | -520353 | 28 | 26 | 282.327 | 94186.2
427 | 313370 | -614854 | 24 | 22 | 217.083 | 58287.3
428 | 179282 | -16292.8 | 19 | 18 | 127.572 | 41683
429 | 185584 | -42187.4 | 15 | 13 | 118.425 | 36988.9
430 | 166198 | -80348.3 | 13 | 11 | 106.115 | 22676.3
431 | 151552 | -128823 | 10 | 9 | 96.9236 | 12175.1
432 | 145040 | -167396 | 8 | 7 | 92.8449 | 10588.9
433 | 142479 | -198826 | 7 | 6 | 91.8051 | 10593.7
434 | 140698 | -221762 | 6 | 5 | 97.3572 | 10597.5
435 | 139145 | -239268 | 5 | 4 | 99.7243 | 10601
436 | 137784 | -253858 | 5 | 3 | 101.554 | 10604.1
437 | 139325 | -269660 | 4 | 3 | 108.476 | 11780.8
438 | 185485 | -251427 | 4 | 2 | 143.829 | 28633
439 | 318209 | -1238320 | 5 | 3 | 307.577 | 84885.8
440 | 380231 | -1146470 | 5 | 4 | 329.203 | 103100
441 | 399609 | -993600 | 6 | 5 | 319.446 | 142715
442 | 397240 | -976875 | 7 | 6 | 315.384 | 167936
443 | 380845 | -980391 | 7 | 6 | 304.895 | 171532
444 | 362148 | -912389 | 8 | 7 | 289.302 | 171532
445 | 351667 | -914462 | 8 | 7 | 286.532 | 171530
446 | 384497 | -846324 | 9 | 7 | 296.264 | 171527
447 | 403425 | -832938 | 9 | 8 | 293.875 | 169309
448 | 406483 | -822938 | 10 | 8 | 289.085 | 153913
449 | 396698 | -851993 | 10 | 9 | 314.819 | 125623
450 | 373303 | -888548 | 11 | 9 | 303.458 | 94190.9
451 | 304132 | -890802 | 11 | 10 | 234.658 | 58291.8
452 | 212090 | -19526.1 | 12 | 10 | 133.697 | 41686.1
453 | 178660 | -85928.9 | 12 | 10 | 117.328 | 36990.3
454 | 162309 | -135699 | 12 | 11 | 105.466 | 22679.2
455 | 148967 | -170235 | 13 | 11 | 96.49 | 12178.4
456 | 143291 | -190835 | 13 | 11 | 92.6682 | 10591.8
457 | 141248 | -203058 | 13 | 12 | 96.123 | 10596.1
458 | 141251 | -211453 | 13 | 12 | 96.9793 | 10599.4
459 | 138632 | -212846 | 13 | 12 | 97.4748 | 10602.3
460 | 143597 | -221532 | 13 | 13 | 98.7948 | 10604.9
461 | 139593 | -211425 | 14 | 13 | 101.102 | 11780.9
462 | 192003 | -209826 | 14 | 13 | 136.623 | 28632.4
463 | 318709 | -1100570 | 14 | 13 | 300.828 | 84884.1
464 | 380807 | -985180 | 15 | 14 | 321.475 | 103098
465 | 399919 | -859136 | 15 | 14 | 312.239 | 142713
466 | 397773 | -826250 | 16 | 14 | 304.414 | 167932
467 | 382806 | -833211 | 16 | 15 | 296.57 | 171529
468 | 361550 | -742751 | 17 | 15 | 278.74 | 171528
469 | 352559 | -712239 | 17 | 15 | 275.315 | 171526
470 | 385389 | -622579 | 17 | 15 | 283.683 | 171523
471 | 404119 | -612893 | 17 | 14 | 288.615 | 169306
472 | 407061 | -685170 | 14 | 12 | 294.2 | 153909
473 | 397133 | -783479 | 12 | 10 | 306.322 | 125619
474 | 385954 | -896444 | 9 | 7 | 303.184 | 94187.9
475 | 307956 | -914777 | 8 | 7 | 235.376 | 58289.1
476 | 212170 | -19591.3 | 7 | 6 | 133.527 | 41684.1
477 | 181347 | -92053.4 | 6 | 5 | 117.482 | 36988.2
478 | 162447 | -139962 | 6 | 5 | 105.714 | 22677
479 | 148932 | -163953 | 5 | 4 | 96.9581 | 12176.3
480 | 145865 | -191219 | 5 | 4 | 93.3408 | 10589.6
481 | 140700 | -201575 | 5 | 3 | 92.5261 | 10593.2
482 | 140631 | -218833 | 4 | 3 | 94.1791 | 10595.9
483 | 137582 | -224052 | 4 | 3 | 94.993 | 10598.9
484 | 137591 | -233628 | 4 | 3 | 96.0483 | 10601.2
485 | 135320 | -237126 | 4 | 3 | 96.7785 | 10603.3
486 | 135238 | -244476 | 4 | 3 | 97.7361 | 10605.2
487 | 133533 | -244118 | 6 | 5 | 96.3821 | 10607
488 | 121919 | -1200120 | 7 | 6 | 171.965 | 10608.6
489 | 121213 | -1086430 | 9 | 8 | 166.398 | 10609.9
490 | 120792 | -936411 | 13 | 11 | 153.791 | 10595.2
491 | 120350 | -877387 | 16 | 15 | 148.665 | 10592.8
492 | 119952 | -802400 | 20 | 19 | 142.12 | 10590.8
493 | 119558 | -763264 | 22 | 20 | 121.259 | 10589.8
494 | 119194 | -731013 | 23 | 22 | 116.295 | 10589.1
495 | 118887 | -19265.2 | 25 | 23 | 77.5164 | 10588.5
496 | 137948 | -64420.2 | 25 | 23 | 83.8709 | 10588.3
497 | 133814 | -98834.9 | 24 | 24 | 87.2275 | 10593.5
498 | 131647 | -134910 | 24 | 23 | 91.5626 | 10598.9
499 | 130717 | -151353 | 25 | 24 | 92.2674 | 10602.4
500 | 130384 | -160695 | 25 | 25 | 92.2426 | 10605.7
501 | 129429 | -163511 | 26 | 26 | 92.1746 | 10608.3
502 | 129854 | -166189 | 27 | 27 | 92.2131 | 10610.6
503 | 128640 | -166658 | 27 | 27 | 91.3577 | 10612.7
504 | 128425 | -166490 | 28 | 28 | 90.557 | 10614.7
505 | 128113 | -167818 | 29 | 29 | 86.055 | 3990.56
506 | 128046 | -169716 | 31 | 30 | 86.082 | 3992.28
507 | 127332 | -167115 | 32 | 31 | 86.0822 | 3994.11
508 | 127148 | -167487 | 32 | 31 | 86.1149 | 3995.72
509 | 126841 | -170659 | 31 | 31 | 86.1095 | 3997.26
510 | 126602 | -175379 | 31 | 31 | 86.0775 | 3998.68
511 | 126332 | -179448 | 31 | 30 | 87.066 | 4000.05
512 | 126125 | -181043 | 31 | 30 | 84.9859 | 4001.43
513 | 125987 | -174950 | 31 | 29 | 83.8126 | 4002.82
514 | 125751 | -168412 | 29 | 27 | 81.0601 | 4004.18
515 | 125491 | -162040 | 26 | 25 | 80.7179 | 4005.55
516 | 125254 | -166959 | 24 | 22 | 80.5767 | 4006.88
517 | 125089 | -156083 | 24 | 22 | 80.0196 | 4008.19
518 | 124834 | -153713 | 23 | 21 | 79.9704 | 4009.54
519 | 124653 | -160639 | 23 | 20 | 79.9241 | 4011.02
520 | 124466 | -178481 | 20 | 18 | 82.948 | 4012.48
521 | 123960 | -211043 | 18 | 16 | 90.0475 | 4013.9
522 | 123470 | -252907 | 15 | 13 | 100.972 | 4015.42
523 | 123022 | -275416 | 13 | 11 | 105.268 | 4016.64
524 | 122517 | -301889 | 10 | 9 | 109.323 | 4017.79
525 | 122056 | -317434 | 8 | 7 | 112.379 | 4018.92
526 | 121684 | -336184 | 7 | 6 | 116.623 | 4020
527 | 121312 | -345248 | 6 | 5 | 118.331 | 4021.03
528 | 120931 | -359044 | 5 | 4 | 118.825 | 4022.02
529 | 120959 | -366907 | 5 | 4 | 121.845 | 10649
530 | 121494 | -377469 | 4 | 3 | 122.455 | 10649.9
531 | 120533 | -379784 | 4 | 3 | 122.742 | 10650.2
532 | 121310 | -387497 | 4 | 3 | 123.085 | 10650.9
533 | 122998 | -390854 | 4 | 3 | 127.367 | 11825.3
534 | 169552 | -352739 | 4 | 3 | 160.657 | 28675.4
535 | 306575 | -1406290 | 5 | 3 | 318.944 | 84926.4
536 | 369176 | -1261640 | 5 | 4 | 336.669 | 103140
537 | 389027 | -1072530 | 6 | 4 | 322.935 | 142742
538 | 387324 | -1009470 | 7 | 5 | 311.664 | 167963
539 | 369009 | -967726 | 8 | 6 | 301.781 | 171558
540 | 342511 | -851987 | 9 | 7 | 283.009 | 171557
541 | 343410 | -820144 | 11 | 8 | 280.31 | 171554
542 | 376732 | -727433 | 12 | 10 | 289.048 | 171551
543 | 395938 | -694678 | 14 | 11 | 294.2 | 169332
544 | 399279 | -733300 | 12 | 10 | 298.553 | 153935
545 | 389911 | -805256 | 11 | 8 | 305.331 | 125644
546 | 377449 | -922440 | 9 | 7 | 304.594 | 94211.5
547 | 295200 | -930338 | 9 | 7 | 236.558 | 58311.8
548 | 204483 | -19392.4 | 8 | 7 | 133.055 | 41706.1
549 | 174386 | -100515 | 8 | 6 | 117.117 | 37009.7
550 | 154723 | -149440 | 8 | 7 | 105.254 | 22699.4
551 | 141853 | -183002 | 9 | 7 | 96.251 | 12198.6
552 | 136478 | -225418 | 9 | 7 | 98.5937 | 10611.6
553 | 134579 | -237548 | 10 | 8 | 99.4724 | 10615
554 | 135153 | -255019 | 10 | 8 | 101.257 | 10618.1
555 | 132581 | -256997 | 11 | 9 | 102.061 | 10620.9
556 | 133052 | -265343 | 12 | 10 | 102.98 | 10623.5
557 | 134168 | -267280 | 13 | 11 | 107.514 | 11799.6
558 | 180987 | -236517 | 14 | 12 | 135.8 | 28651.1
559 | 315266 | -1144870 | 15 | 13 | 304.463 | 84903.3
560 | 377670 | -990174 | 17 | 14 | 322.193 | 103116
561 | 396742 | -838231 | 18 | 15 | 314.317 | 142728
562 | 395047 | -801949 | 19 | 17 | 303.925 | 167947
563 | 379533 | -788644 | 20 | 19 | 295.909 | 171542
564 | 360631 | -704547 | 21 | 20 | 277.509 | 171541
565 | 350289 | -704550 | 21 | 20 | 275.94 | 171538
566 | 383479 | -644214 | 21 | 20 | 287.663 | 171535
567 | 402139 | -630460 | 21 | 20 | 291.94 | 169317
568 | 405014 | -667441 | 19 | 18 | 297.079 | 153920
569 | 395464 | -723158 | 17 | 16 | 308.304 | 125630
570 | 381327 | -807615 | 15 | 13 | 299.486 | 94197.3
571 | 310053 | -880874 | 11 | 10 | 233.877 | 58298.1
572 | 209747 | -19261.3 | 8 | 6 | 133.452 | 41692.9
573 | 176050 | -107998 | 4 | 3 | 116.953 | 36997.4
574 | 159708 | -178116 | 2 | 1 | 104.961 | 22686.4
575 | 146336 | -239951 | 1 | -1 | 103.044 | 12186.1
576 | 140473 | -274784 | -1 | -2 | 106.134 | 10600
577 | 138023 | -301628 | -2 | -3 | 109.797 | 10604.6
578 | 136335 | -320828 | -3 | -4 | 113.047 | 10608.5
579 | 134836 | -340175 | -4 | -5 | 116.756 | 10612
580 | 133541 | -359103 | -6 | -7 | 121.4 | 10615.2
581 | 134910 | -388592 | -8 | -9 | 127.932 | 11792
582 | 180393 | -375646 | -10 | -11 | 165.07 | 28644.4
583 | 314965 | -1572900 | -10 | -11 | 325.811 | 84897.5
584 | 377012 | -1488210 | -11 | -12 | 345.13 | 103111
585 | 396820 | -1300500 | -11 | -12 | 330.54 | 142723
586 | 394508 | -1243060 | -10 | -11 | 325.583 | 167944
587 | 381770 | -1237590 | -9 | -10 | 316.304 | 171540
588 | 348177 | -1094730 | -8 | -9 | 295.385 | 171540
589 | 348312 | -1127710 | -8 | -9 | 296.056 | 171538
590 | 380997 | -1096740 | -7 | -9 | 309.137 | 171535
591 | 400347 | -1094150 | -7 | -8 | 313.283 | 169317
592 | 403558 | -1156330 | -8 | -9 | 318.486 | 153921
593 | 393129 | -1242610 | -9 | -10 | 328.857 | 125632
594 | 382356 | -1317810 | -10 | -11 | 325.169 | 94200
595 | 327838 | -1294520 | -10 | -11 | 258.401 | 58300.6
596 | 205176 | -47231.5 | -10 | -11 | 133.989 | 41694.6
597 | 177336 | -234810 | -10 | -11 | 117.695 | 36998.2
598 | 155987 | -294554 | -10 | -11 | 121.946 | 22689.5
599 | 147358 | -350826 | -10 | -11 | 125.77 | 12189.8
600 | 137171 | -357490 | -10 | -11 | 123.407 | 10604.1
601 | 137964 | -383091 | -10 | -11 | 124.13 | 10609
602 | 133669 | -388234 | -10 | -11 | 124.603 | 10613
603 | 134904 | -409516 | -10 | -11 | 125.734 | 10616.7
604 | 131323 | -412208 | -10 | -11 | 126.125 | 10619.9
605 | 135029 | -438722 | -10 | -11 | 132.074 | 11796.7
606 | 178578 | -403702 | -10 | -11 | 167.469 | 28648.9
607 | 313620 | -1612310 | -10 | -11 | 327.445 | 84901.8
608 | 375792 | -1516390 | -10 | -11 | 348.4 | 103116
609 | 395677 | -1343330 | -10 | -11 | 331.527 | 142725
610 | 393336 | -1251910 | -8 | -9 | 324.984 | 167945
611 | 374111 | -1238840 | -7 | -8 | 315.648 | 171541
612 | 347413 | -1089500 | -5 | -6 | 295.63 | 171540
613 | 347756 | -1065610 | -4 | -5 | 292.188 | 171538
614 | 380487 | -1020500 | -3 | -5 | 304.931 | 171535
615 | 399768 | -1003150 | -2 | -4 | 309.056 | 169317
616 | 403130 | -1049910 | -3 | -4 | 312.362 | 153921
617 | 392826 | -1123150 | -3 | -5 | 320.334 | 125631
618 | 377109 | -1199960 | -4 | -6 | 317.634 | 94199.5
619 | 317842 | -1198650 | -5 | -6 | 252.151 | 58300
620 | 205570 | -45294.4 | -5 | -7 | 133.578 | 41694
621 | 175545 | -203276 | -6 | -7 | 117.258 | 36997.7
622 | 156195 | -260150 | -6 | -8 | 114.987 | 22688.5
623 | 147227 | -321741 | -7 | -8 | 118.84 | 12188.6
624 | 137415 | -332336 | -7 | -8 | 117.541 | 10602.7
625 | 137875 | -359153 | -7 | -8 | 122.041 | 10607.4
626 | 134007 | -361390 | -6 | -7 | 122.384 | 10611.3
627 | 134956 | -381704 | -6 | -7 | 123.784 | 10614.8
628 | 131771 | -382875 | -6 | -7 | 123.986 | 10618
629 | 135644 | -403811 | -7 | -8 | 129.115 | 11794.7
630 | 179170 | -369574 | -7 | -8 | 165.154 | 28646.8
631 | 314036 | -1520690 | -6 | -7 | 322.475 | 84899.6
632 | 376226 | -1391180 | -5 | -6 | 341.56 | 103113
633 | 395997 | -1218490 | -4 | -5 | 329.1 | 142723
634 | 393635 | -1197210 | -4 | -5 | 322.93 | 167943
635 | 374627 | -1186600 | -3 | -4 | 314.51 | 171539
636 | 356522 | -1114040 | -3 | -4 | 299.001 | 171539
637 | 348073 | -1100180 | -2 | -3 | 295.992 | 171536
638 | 380928 | -1055870 | -2 | -3 | 306.303 | 171533
639 | 400162 | -1029560 | -1 | -2 | 311.42 | 169315
640 | 403374 | -1042920 | -1 | -2 | 313.758 | 153919
641 | 393329 | -1060250 | 0 | -1 | 321.908 | 125629
642 | 370603 | -1118190 | 0 | -1 | 314.247 | 94197.1
643 | 307063 | -1103860 | 0 | -1 | 246.966 | 58297.6
644 | 206417 | -39571.8 | 0 | -1 | 132.613 | 41691.8
645 | 175655 | -167889 | 0 | -1 | 116.782 | 36995.6
646 | 157240 | -221651 | 0 | -1 | 110.064 | 22685.8
647 | 149072 | -267378 | 0 | -1 | 109.035 | 12185.7
648 | 138710 | -272767 | 0 | -1 | 107.64 | 10599.4
649 | 147643 | -303390 | -3 | -4 | 107.041 | 10603.9
650 | 134711 | -283382 | -5 | -6 | 104.477 | 10607.4
651 | 139347 | -318764 | -8 | -9 | 108.919 | 10611
652 | 132244 | -314100 | -9 | -10 | 109.622 | 10613.3
653 | 131077 | -341852 | -11 | -11 | 114.476 | 10615.5
654 | 129911 | -380295 | -12 | -13 | 119.746 | 10617.5
655 | 128863 | -379709 | -10 | -11 | 118.521 | 10619.4
656 | 118976 | -1549970 | -9 | -9 | 195.693 | 10622.3
657 | 118405 | -1340880 | -7 | -8 | 182.253 | 10624.7
658 | 117738 | -1163000 | -5 | -6 | 168.671 | 10603.1
659 | 117234 | -1068480 | -3 | -4 | 162.16 | 10600.1
660 | 116729 | -1003220 | -1 | -2 | 157.27 | 10598.5
661 | 116313 | -953444 | 1 | -1 | 153.111 | 10597.4
662 | 115916 | -919322 | 2 | 1 | 148.977 | 10596.6
663 | 149592 | -19522.4 | 4 | 2 | 82.4106 | 10595.9
664 | 133824 | -118394 | 2 | 0 | 81.3376 | 10595.6
665 | 129395 | -173932 | -1 | -2 | 84.6679 | 10603.8
666 | 126240 | -236549 | -3 | -4 | 98.9141 | 10609.5
667 | 125014 | -288698 | -4 | -5 | 109.019 | 10613.8
668 | 124436 | -318210 | -4 | -5 | 114.455 | 10618.2
669 | 123295 | -340416 | -5 | -6 | 119.924 | 10621.7
670 | 123216 | -359055 | -6 | -7 | 123.118 | 10625
671 | 121929 | -374492 | -6 | -7 | 123.699 | 10628
672 | 121353 | -394622 | -7 | -8 | 124.273 | 10630.8
673 | 120989 | -419288 | -5 | -6 | 120.702 | 4007.24
674 | 120509 | -428493 | -4 | -5 | 121.032 | 4008.81
675 | 120053 | -431453 | -2 | -3 | 121.123 | 4010.4
676 | 119708 | -437171 | -3 | -4 | 121.577 | 4011.76
677 | 119318 | -443304 | -4 | -5 | 122.095 | 4013.06
678 | 118951 | -452083 | -5 | -6 | 122.689 | 4014.29
679 | 118863 | -456989 | -4 | -5 | 121.281 | 4015.48
680 | 118545 | -440638 | -2 | -3 | 117.636 | 4016.61
681 | 118684 | -381804 | -1 | -2 | 112.746 | 4017.69
682 | 119251 | -325856 | 3 | 1 | 104.874 | 4018.73
683 | 121811 | -291065 | 6 | 5 | 98.3986 | 4019.65
684 | 120544 | -254986 | 10 | 8 | 91.8979 | 4020.41
685 | 121234 | -239521 | 12 | 10 | 89.3194 | 4020.95
686 | 121589 | -222897 | 14 | 11 | 87.102 | 4021.37
687 | 123566 | -220802 | 16 | 13 | 86.0212 | 4021.8
688 | 121073 | -219542 | 14 | 11 | 86.1669 | 4022.25
689 | 119986 | -241164 | 11 | 9 | 91.7486 | 4022.84
690 | 119082 | -277757 | 9 | 7 | 103.551 | 4023.66
691 | 119140 | -333471 | 7 | 5 | 115.16 | 4024.66
692 | 118333 | -358600 | 4 | 3 | 120.381 | 4025.85
693 | 117967 | -379187 | 2 | 0 | 121.8 | 4026.81
694 | 117815 | -394001 | 1 | -1 | 122.869 | 4027.71
695 | 117334 | -406877 | -1 | -2 | 123.055 | 4028.54
696 | 117043 | -418674 | -2 | -3 | 123.076 | 4029.35
697 | 117617 | -435492 | -4 | -5 | 127.433 | 10656.1
698 | 116850 | -447163 | -7 | -8 | 127.986 | 10656.9
699 | 116582 | -452634 | -9 | -10 | 128.564 | 10657.1
700 | 127549 | -462050 | -10 | -11 | 129.252 | 10657.6
701 | 118450 | -438282 | -12 | -12 | 132.245 | 11831.9
702 | 172859 | -456115 | -13 | -14 | 170.849 | 28681.9
703 | 302658 | -1685410 | -11 | -12 | 333.644 | 84932.7
704 | 365388 | -1532540 | -9 | -10 | 349.265 | 103146
705 | 385756 | -1269010 | -7 | -8 | 329.261 | 142747
706 | 384111 | -1135870 | -3 | -4 | 320.109 | 167968
707 | 365606 | -1073320 | 0 | -1 | 307.466 | 171563
708 | 339387 | -899423 | 4 | 2 | 285.605 | 171561
709 | 340351 | -865688 | 6 | 3 | 282.938 | 171559
710 | 373680 | -802936 | 7 | 5 | 294.217 | 171556
711 | 393063 | -766434 | 9 | 6 | 298.755 | 169337
712 | 396682 | -800667 | 7 | 4 | 302.406 | 153940
713 | 387143 | -907232 | 4 | 2 | 309.098 | 125649
714 | 366978 | -1033080 | 2 | 0 | 310.543 | 94216.6
715 | 303801 | -1042020 | 3 | 1 | 244.662 | 58316.9
716 | 200790 | -38161.3 | 3 | 2 | 132.365 | 41710.9
717 | 166967 | -142177 | 4 | 2 | 116.086 | 37014.4
718 | 151467 | -202666 | 5 | 3 | 104.485 | 22704.6
719 | 138787 | -239987 | 6 | 4 | 106.199 | 12204.1
720 | 133706 | -263106 | 7 | 5 | 106.175 | 10617.7
721 | 132003 | -275270 | 7 | 6 | 106.712 | 10621.8
722 | 131390 | -283413 | 8 | 7 | 106.94 | 10625
723 | 130170 | -289574 | 8 | 7 | 108.127 | 10627.8
724 | 129493 | -294744 | 9 | 8 | 108.986 | 10630.4
725 | 131771 | -304460 | 9 | 8 | 115.178 | 11806.4
726 | 178458 | -267382 | 10 | 9 | 146.974 | 28657.9
727 | 313383 | -1234670 | 11 | 10 | 310.149 | 84910.1
728 | 375740 | -1082440 | 12 | 11 | 327.518 | 103123
729 | 395071 | -920170 | 13 | 12 | 315.599 | 142732
730 | 393244 | -839959 | 15 | 13 | 304.702 | 167952
731 | 374898 | -747611 | 17 | 15 | 291.293 | 171547
732 | 356398 | -636752 | 19 | 17 | 272.549 | 171545
733 | 348979 | -592762 | 21 | 18 | 269.268 | 171543
734 | 382226 | -523066 | 22 | 20 | 279.966 | 171540
735 | 400999 | -481217 | 24 | 21 | 264.14 | 169321
736 | 404164 | -515452 | 23 | 21 | 285.87 | 153924
737 | 397236 | -562831 | 23 | 21 | 290.903 | 125633
738 | 387220 | -629817 | 22 | 20 | 289.856 | 94199.9
739 | 309454 | -676478 | 20 | 19 | 222.022 | 58300.1
740 | 176371 | -11898.2 | 19 | 18 | 127.037 | 41694.6
741 | 182002 | -33135.3 | 18 | 17 | 118.03 | 36998.9
742 | 163232 | -62681.9 | 17 | 16 | 106.547 | 22685.1
743 | 148872 | -87298.2 | 16 | 15 | 97.4382 | 12182.6
744 | 142503 | -114541 | 15 | 14 | 93.3273 | 10595.4
745 | 139978 | -147244 | 13 | 12 | 92.367 | 11033.7
746 | 138426 | -165123 | 12 | 11 | 92.1581 | 11036.6
747 | 137130 | -187398 | 11 | 9 | 91.9394 | 11039.4
748 | 140187 | -206851 | 9 | 8 | 96.7834 | 11041.8
749 | 137768 | -210273 | 8 | 7 | 101.764 | 12271.8
750 | 187813 | -199934 | 7 | 6 | 135.535 | 29897.3
751 | 316831 | -1136890 | 6 | 5 | 299.081 | 88732.9
752 | 378867 | -1076740 | 6 | 5 | 324.286 | 107783
753 | 398224 | -971093 | 6 | 5 | 315.635 | 149221
754 | 396007 | -933426 | 8 | 7 | 310.192 | 175600
755 | 382410 | -964456 | 8 | 7 | 305.413 | 179362
756 | 358276 | -871061 | 9 | 8 | 287.211 | 179361
757 | 350532 | -881903 | 9 | 8 | 286.14 | 179359
758 | 383549 | -814621 | 10 | 9 | 296.648 | 179356
759 | 402373 | -802117 | 10 | 9 | 301.359 | 177037
760 | 405519 | -798260 | 11 | 10 | 303.472 | 160933
761 | 395586 | -832473 | 11 | 9 | 310.401 | 131343
762 | 371851 | -878132 | 11 | 10 | 299.581 | 98467.4
763 | 302423 | -882929 | 11 | 9 | 233.373 | 60919.4
764 | 210700 | -19393.2 | 11 | 9 | 133.621 | 43551.2
765 | 177147 | -87821.9 | 10 | 9 | 117.233 | 38639.8
766 | 160863 | -139490 | 10 | 9 | 105.33 | 23671.3
767 | 147569 | -173966 | 10 | 9 | 96.407 | 12687.9
768 | 151880 | -196382 | 10 | 9 | 93.4826 | 11028.3
769 | 139915 | -178993 | 10 | 9 | 92.1415 | 11032.6
770 | 143351 | -197786 | 11 | 10 | 92.4523 | 11035.9
771 | 137370 | -198006 | 12 | 11 | 95.5312 | 11038
772 | 141389 | -228215 | 12 | 11 | 97.9312 | 11040
773 | 138447 | -225941 | 13 | 11 | 103.914 | 12269.3
774 | 185138 | -190549 | 13 | 11 | 135.165 | 29895.1
775 | 317828 | -1096370 | 13 | 11 | 298.332 | 88731.1
776 | 379732 | -980488 | 14 | 11 | 319.616 | 107780
777 | 399360 | -857148 | 14 | 13 | 309.193 | 149217
778 | 397047 | -798472 | 16 | 15 | 303.014 | 175595
779 | 378677 | -776041 | 18 | 16 | 294.358 | 179357
780 | 365769 | -685103 | 20 | 18 | 276.52 | 179356
781 | 352112 | -668601 | 20 | 19 | 273.854 | 179354
782 | 385161 | -614378 | 20 | 19 | 285.848 | 179351
783 | 403836 | -584106 | 21 | 20 | 289.012 | 177031
784 | 406854 | -610130 | 20 | 19 | 292.11 | 160927
785 | 397285 | -634131 | 20 | 19 | 299.089 | 131337
786 | 385795 | -681693 | 20 | 19 | 287.992 | 98461.5
787 | 308474 | -697181 | 19 | 19 | 221.128 | 60913.2
788 | 178460 | -12121.9 | 19 | 18 | 127.223 | 43544.9
789 | 184651 | -32223.2 | 19 | 18 | 118.444 | 38633.4
790 | 165962 | -56947.2 | 19 | 18 | 106.802 | 23662.3
791 | 151718 | -77180.9 | 19 | 18 | 97.8221 | 12677.4
792 | 145391 | -94322.2 | 20 | 19 | 93.9384 | 11016.7
793 | 143064 | -111812 | 20 | 19 | 92.8111 | 11020
794 | 141594 | -141268 | 19 | 18 | 92.4647 | 11022.6
795 | 140226 | -156076 | 16 | 15 | 92.231 | 11024.7
796 | 139055 | -182516 | 14 | 13 | 92.0545 | 11027.4
797 | 140604 | -212742 | 10 | 9 | 100.005 | 12257.6
798 | 186653 | -207702 | 5 | 4 | 135.158 | 29883.4
799 | 317944 | -1202780 | -1 | -2 | 301.132 | 88719.6
800 | 379954 | -1128090 | 0 | -2 | 322.25 | 107770
801 | 399604 | -967579 | 1 | 0 | 311.488 | 149210
802 | 397153 | -913459 | 3 | 1 | 306.911 | 175590
803 | 378125 | -905470 | 4 | 2 | 297.165 | 179353
804 | 351143 | -792684 | 5 | 3 | 277.117 | 179353
805 | 351438 | -768989 | 7 | 5 | 256.355 | 179351
806 | 384288 | -716437 | 8 | 6 | 268.384 | 179348
807 | 403164 | -728923 | 7 | 5 | 275.66 | 177029
808 | 406144 | -764881 | 6 | 4 | 279.473 | 160925
809 | 396069 | -854666 | 4 | 2 | 281.387 | 131336
810 | 376155 | -1013050 | -1 | -2 | 280.982 | 98461
811 | 314969 | -991704 | 2 | 1 | 236.865 | 60913.6
812 | 209820 | -19523.8 | -2 | -3 | 133.03 | 43546.1
813 | 176699 | -122289 | -1 | -2 | 116.738 | 38633.9
814 | 176922 | -188613 | -3 | -4 | 106.432 | 23665.7
815 | 147066 | -188231 | -5 | -6 | 96.7636 | 12682.7
816 | 148914 | -230708 | -6 | -7 | 99.5397 | 11023.5
817 | 138620 | -236599 | -6 | -7 | 97.348 | 11026.9
818 | 165651 | -306325 | -9 | -10 | 104.704 | 11029.7
819 | 135291 | -260399 | -10 | -11 | 101.686 | 11032.7
820 | 147310 | -300646 | -12 | -12 | 105.225 | 11036.5
821 | 132948 | -281025 | -10 | -11 | 104.475 | 11038.4
822 | 139043 | -313489 | -13 | -13 | 107.26 | 11040.6
823 | 130768 | -307791 | -13 | -13 | 105.506 | 11042.6
824 | 119939 | -1407170 | -14 | -15 | 182.952 | 11044.4
825 | 119357 | -1186540 | -8 | -9 | 169.806 | 11045.8
826 | 118758 | -1000320 | -4 | -5 | 156.63 | 11029.9
827 | 118234 | -908960 | 0 | -1 | 150.142 | 11027.3
828 | 117769 | -844597 | 3 | 1 | 144.628 | 11025.1
829 | 117398 | -779806 | 8 | 6 | 122.507 | 11023.9
830 | 117165 | -706952 | 13 | 10 | 115.434 | 11023.1
831 | 173984 | -19523.7 | 15 | 12 | 85.1119 | 11022.7
832 | 137078 | -50045.3 | 17 | 14 | 82.7554 | 11022.3
833 | 141766 | -79293.2 | 14 | 12 | 85.1591 | 11027.7
834 | 130539 | -99863.1 | 18 | 15 | 87.6254 | 11031.7
835 | 129083 | -133462 | 18 | 15 | 90.8142 | 11034.3
836 | 127998 | -164043 | 17 | 15 | 92.0973 | 11037.1
837 | 127377 | -179562 | 17 | 14 | 91.9691 | 11039.1
838 | 127013 | -204860 | 15 | 15 | 96.2504 | 11042.1
839 | 126299 | -212746 | 15 | 14 | 96.7049 | 11044.6
840 | 126923 | -222831 | 15 | 14 | 97.1763 | 11047
841 | 125211 | -232700 | 14 | 14 | 93.5374 | 4119.03
842 | 124703 | -249927 | 14 | 13 | 95.2453 | 4121.39
843 | 124298 | -259215 | 14 | 13 | 96.1006 | 4123.76
844 | 123907 | -268684 | 14 | 13 | 98.0221 | 4125.93
845 | 123636 | -275189 | 15 | 14 | 98.5958 | 4128.2
846 | 123326 | -272826 | 15 | 15 | 97.2872 | 4130.3
847 | 131946 | -279745 | 16 | 15 | 97.1992 | 4132.34
848 | 122858 | -248758 | 18 | 17 | 91.2278 | 4134.31
849 | 128147 | -270127 | 18 | 17 | 92.706 | 4136.16
850 | 122709 | -235944 | 20 | 19 | 89.6558 | 4137.33
851 | 126392 | -231828 | 21 | 20 | 88.3522 | 4139.14
852 | 122724 | -210853 | 22 | 21 | 86.6948 | 4140.66
853 | 125020 | -210810 | 22 | 21 | 86.0939 | 4141.88
854 | 122626 | -203694 | 23 | 21 | 85.3938 | 4142.98
855 | 124023 | -209879 | 22 | 21 | 82.8503 | 4144.02
856 | 122363 | -219682 | 22 | 20 | 83.3554 | 4145.04
857 | 123007 | -241674 | 21 | 20 | 90.1159 | 4146.03
858 | 121918 | -251982 | 20 | 18 | 95.0043 | 4147.02
859 | 122491 | -266010 | 19 | 17 | 100.376 | 4148.01
860 | 121505 | -273356 | 18 | 16 | 103.082 | 4149
861 | 121192 | -286991 | 16 | 15 | 104.852 | 4149.96
862 | 121043 | -292751 | 16 | 15 | 105.826 | 4150.9
863 | 121783 | -300914 | 16 | 14 | 106.316 | 4151.8
864 | 120693 | -302077 | 16 | 14 | 105.815 | 4152.69
865 | 121799 | -313332 | 15 | 14 | 112.485 | 11083.8
866 | 120829 | -314298 | 15 | 14 | 111.653 | 11084.7
867 | 120760 | -319645 | 15 | 14 | 112.501 | 11084.9
868 | 120557 | -325076 | 14 | 13 | 113.53 | 11085.5
869 | 123516 | -324971 | 15 | 13 | 117.308 | 12313.8
870 | 174603 | -284361 | 15 | 13 | 146.595 | 29937.6
871 | 306871 | -1269270 | 13 | 11 | 310.219 | 88772.1
872 | 369511 | -1129050 | 13 | 11 | 329.339 | 107822
873 | 389078 | -971649 | 13 | 11 | 313.443 | 149245
874 | 387599 | -865701 | 15 | 13 | 304.811 | 175624
875 | 369666 | -798935 | 17 | 15 | 293.425 | 179385
876 | 344639 | -695720 | 19 | 16 | 275.178 | 179383
877 | 344133 | -648478 | 21 | 18 | 271.896 | 179380
878 | 377513 | -583478 | 22 | 19 | 282.885 | 179377
879 | 396270 | -593191 | 20 | 17 | 289.059 | 177056
880 | 399657 | -614734 | 19 | 16 | 291.81 | 160951
881 | 390433 | -692549 | 18 | 15 | 293.393 | 131361
882 | 383796 | -841260 | 13 | 11 | 295.327 | 98484.5
883 | 309390 | -923161 | 8 | 6 | 234.419 | 60936
884 | 204688 | -19524.7 | 5 | 4 | 133.527 | 43568.2
885 | 170999 | -91628.1 | 4 | 3 | 117.017 | 38656.7
886 | 171350 | -152138 | 4 | 3 | 106.445 | 23688.7
887 | 141814 | -165956 | 3 | 2 | 96.6596 | 12704.6
888 | 144066 | -217421 | -3 | -4 | 98.377 | 11045.2
889 | 134031 | -225214 | -5 | -6 | 99.9315 | 11048.4
890 | 137054 | -249372 | -5 | -6 | 101.97 | 11050.9
891 | 131680 | -257741 | -7 | -8 | 104.182 | 11053
892 | 132913 | -280781 | -10 | -11 | 107.171 | 11054.7
893 | 132227 | -292650 | -10 | -10 | 114.52 | 12284
894 | 177941 | -286176 | -13 | -14 | 150.555 | 29908.7
895 | 312126 | -1434880 | -15 | -15 | 312.298 | 88743.9
896 | 374518 | -1372490 | -13 | -14 | 335.646 | 107793
897 | 394793 | -1067310 | -5 | -6 | 316.636 | 149229
898 | 392583 | -963697 | -1 | -2 | 309.469 | 175610
899 | 373684 | -914390 | 2 | 1 | 298.102 | 179371
900 | 347062 | -756872 | 6 | 5 | 276.688 | 179370
901 | 348002 | -667098 | 13 | 10 | 271.484 | 179368
902 | 381260 | -566429 | 17 | 14 | 280.055 | 179364
903 | 400209 | -529680 | 19 | 15 | 265.475 | 177043
904 | 403410 | -533735 | 20 | 16 | 267.129 | 160938
905 | 396502 | -601209 | 19 | 15 | 267.327 | 131348
906 | 386446 | -746549 | 13 | 10 | 287.372 | 98470.7
907 | 335483 | -868594 | 4 | 3 | 229.344 | 60922.1
908 | 209256 | -8479.99 | 6 | 5 | 132.417 | 43554.5
909 | 176704 | -55674.5 | 5 | 4 | 116.941 | 38642.9
910 | 159995 | -92220.2 | 3 | 2 | 105.768 | 23671.7
911 | 146072 | -129157 | 0 | -1 | 97.1209 | 12686.6
912 | 140425 | -157329 | -1 | -2 | 93.4985 | 11025.6
913 | 138207 | -172802 | -1 | -1 | 92.7826 | 11028.8
914 | 136529 | -198790 | -7 | -8 | 96.8773 | 11031
915 | 135266 | -216071 | -7 | -8 | 98.5657 | 11033
916 | 134254 | -222820 | -5 | -6 | 99.7975 | 11034.7
917 | 136114 | -234454 | -4 | -4 | 104.766 | 12263.9
918 | 182541 | -210692 | -2 | -3 | 136.219 | 29888.5
919 | 315048 | -1191810 | -5 | -6 | 297.802 | 88723.6
920 | 377231 | -1142080 | -3 | -3 | 321.833 | 107773
921 | 396975 | -921578 | 1 | 0 | 307.774 | 149216
922 | 394818 | -828332 | 5 | 4 | 301.593 | 175596
923 | 376070 | -772633 | 8 | 6 | 289.335 | 179358
924 | 353849 | -666326 | 10 | 8 | 251.352 | 179357
925 | 349785 | -632990 | 13 | 11 | 249.31 | 179355
926 | 383015 | -558742 | 15 | 13 | 260.306 | 179351
927 | 401940 | -513372 | 18 | 15 | 264.572 | 177030
928 | 404939 | -563309 | 16 | 13 | 268.379 | 160925
929 | 398702 | -691544 | 12 | 10 | 272.336 | 131334
930 | 377942 | -790285 | 10 | 8 | 270.515 | 98458.6
931 | 315381 | -807664 | 9 | 8 | 225.42 | 60911
932 | 211073 | -9498.12 | 6 | 5 | 132.869 | 43543.5
933 | 178602 | -49795.1 | 8 | 7 | 117.631 | 38632.3
934 | 161962 | -83668.7 | 6 | 5 | 105.765 | 23661.1
935 | 147851 | -120995 | 2 | 1 | 97.3317 | 12676.4
936 | 141984 | -149534 | 0 | -1 | 93.5309 | 11015.3
937 | 139719 | -171725 | -3 | -4 | 92.8838 | 11018.8
938 | 138099 | -190005 | -6 | -6 | 92.8076 | 11021.3
939 | 136661 | -209071 | -7 | -8 | 97.1097 | 11023.4
940 | 135464 | -223861 | -8 | -8 | 99.0728 | 11025.3
941 | 136982 | -240704 | -8 | -9 | 105.224 | 12254.7
942 | 182991 | -230798 | -10 | -11 | 136.295 | 29879.6
943 | 315769 | -1217250 | -8 | -9 | 298.577 | 88714.9
944 | 377597 | -1152290 | -5 | -6 | 320.918 | 107764
945 | 397481 | -931964 | -1 | -2 | 308.465 | 149209
946 | 395016 | -862909 | 1 | 0 | 303.163 | 175589
947 | 376356 | -774805 | 7 | 5 | 289.411 | 179351
948 | 354719 | -637371 | 12 | 10 | 269.429 | 179352
949 | 350471 | -564560 | 18 | 15 | 265.446 | 179349
950 | 383750 | -475087 | 21 | 17 | 257.669 | 179344
951 | 402212 | -454365 | 22 | 17 | 264.835 | 177023
952 | 405657 | -488130 | 21 | 17 | 265.687 | 160917
953 | 401949 | -588732 | 19 | 15 | 267.991 | 131327
954 | 390824 | -692142 | 17 | 14 | 266.59 | 98450.6
955 | 309006 | -711681 | 17 | 14 | 220.521 | 60902.4
956 | 213389 | -19393.4 | 17 | 14 | 134.419 | 43535.2
957 | 180833 | -49362 | 17 | 15 | 118.208 | 38624.1
958 | 163917 | -82979.1 | 17 | 15 | 106.099 | 23654.6
959 | 149895 | -112894 | 18 | 17 | 97.0189 | 12670.5
960 | 143898 | -128067 | 20 | 19 | 93.0413 | 11010.4
961 | 143673 | -143412 | 21 | 20 | 92.3446 | 11014.9
962 | 140618 | -145075 | 22 | 21 | 92.1678 | 11018.2
963 | 140322 | -154313 | 23 | 22 | 92.1535 | 11021.4
964 | 138525 | -156843 | 24 | 23 | 92.0658 | 11024
965 | 141052 | -155626 | 26 | 25 | 95.8951 | 12254
966 | 194047 | -126967 | 26 | 25 | 136.125 | 29879.4
967 | 319700 | -823073 | 27 | 26 | 281.637 | 88715.1
968 | 381886 | -728731 | 27 | 27 | 305.496 | 107765
969 | 400143 | -657165 | 25 | 24 | 297.744 | 149205
970 | 397770 | -616290 | 24 | 21 | 290.904 | 175583
971 | 388586 | -639057 | 23 | 20 | 283.533 | 179345
972 | 371269 | -599572 | 21 | 18 | 249.468 | 179344
973 | 352998 | -571457 | 20 | 17 | 246.688 | 179343
974 | 385971 | -530860 | 20 | 17 | 259.544 | 179341
975 | 404606 | -517280 | 20 | 17 | 264.855 | 177021
976 | 407538 | -546052 | 19 | 16 | 267.759 | 160918
977 | 399782 | -636522 | 16 | 14 | 269.107 | 131329
978 | 384797 | -766729 | 13 | 10 | 269.039 | 98453.4
979 | 318073 | -827437 | 11 | 9 | 226.627 | 60906.2
980 | 213004 | -19458.4 | 7 | 5 | 133.765 | 43538.8
981 | 180023 | -72661.4 | 6 | 5 | 117.409 | 38627.8
982 | 172792 | -126285 | 5 | 4 | 106.534 | 23658.4
983 | 149527 | -139329 | 4 | 3 | 97.2072 | 12675.1
984 | 148714 | -165143 | 4 | 3 | 93.7388 | 11015.6
985 | 141151 | -179727 | 3 | 2 | 88.5888 | 11019.1
986 | 142147 | -191109 | 5 | 4 | 88.6697 | 11021.8
987 | 138251 | -196365 | 7 | 6 | 91.5791 | 11024.7
988 | 136986 | -205424 | 8 | 7 | 91.2199 | 11026.9
989 | 140934 | -244495 | 8 | 7 | 95.0994 | 11028.9
990 | 134736 | -238205 | 9 | 7 | 94.3751 | 11030.8
991 | 137833 | -256833 | 12 | 10 | 93.3595 | 11033.9
992 | 122089 | -1180130 | 12 | 10 | 169.382 | 11036.4
993 | 121543 | -970573 | 17 | 14 | 155.604 | 11038.9
994 | 121288 | -763256 | 22 | 19 | 139.714 | 11025.3
995 | 122444 | -626786 | 29 | 26 | 112.394 | 11022
996 | 122024 | -543949 | 32 | 28 | 105.005 | 11019.9
997 | 140959 | -485331 | 36 | 31 | 101.002 | 11018.7
998 | 157154 | -454200 | 38 | 33 | 98.7635 | 11017.9
999 | 119818 | -14040.6 | 40 | 34 | 77.0538 | 11017.3
1000 | 119758 | -18319.5 | 40 | 35 | 76.7055 | 11017
1001 | 132524 | -26052.6 | 39 | 35 | 80.3952 | 11020.8
1002 | 143835 | -34538 | 33 | 31 | 88.4373 | 11022.6
1003 | 138471 | -40189.9 | 33 | 31 | 91.5477 | 11024.8
1004 | 135821 | -59019.8 | 28 | 28 | 93.1388 | 11027.4
1005 | 134244 | -66371.1 | 33 | 32 | 92.9241 | 11029.6
1006 | 135889 | -79817.5 | 32 | 31 | 93.0344 | 11031.9
1007 | 131693 | -83675.6 | 31 | 30 | 91.9511 | 11034.1
1008 | 137177 | -95191.7 | 30 | 30 | 91.6578 | 11036.3
1009 | 129909 | -90141.5 | 29 | 29 | 86.7566 | 4107.91
1010 | 131382 | -107105 | 28 | 28 | 86.868 | 4109.83
1011 | 128752 | -116124 | 25 | 25 | 86.7139 | 4111.36
1012 | 129009 | -130235 | 22 | 22 | 86.7397 | 4112.85
1013 | 127649 | -143931 | 18 | 18 | 86.6571 | 4114.25
1014 | 127895 | -145860 | 19 | 19 | 85.4884 | 4115.6
1015 | 127113 | -147636 | 21 | 21 | 83.0466 | 4116.88
1016 | 127100 | -150009 | 21 | 21 | 81.5587 | 4118.08
1017 | 126560 | -139175 | 22 | 22 | 80.9263 | 4119.22
1018 | 126553 | -120513 | 23 | 23 | 80.9715 | 4120.32
1019 | 126413 | -103280 | 26 | 26 | 80.4776 | 4121.37
1020 | 127657 | -74346.5 | 28 | 28 | 80.0195 | 4122.32
1021 | 128780 | -65716.2 | 31 | 30 | 79.7843 | 4123.19
1022 | 130121 | -51051.1 | 39 | 35 | 79.4137 | 4123.98
1023 | 131264 | -42796.5 | 42 | 38 | 79.1863 | 4123.74
1024 | 131324 | -42960.4 | 39 | 36 | 79.0961 | 4123.99
1025 | 130645 | -46522.2 | 38 | 35 | 79.2559 | 4123.84
1026 | 129092 | -60013.7 | 33 | 31 | 83.5057 | 4124.03
1027 | 127984 | -65914.2 | 33 | 31 | 87.2788 | 4124.48
1028 | 126586 | -80578.2 | 26 | 26 | 88.9725 | 4125.27
1029 | 126041 | -97100 | 26 | 26 | 88.9959 | 4126.24
1030 | 125444 | -117036 | 21 | 21 | 89.092 | 4127.12
1031 | 125267 | -130043 | 20 | 20 | 88.3687 | 4128.12
1032 | 124944 | -139519 | 19 | 18 | 87.6131 | 4128.89
1033 | 124965 | -143422 | 17 | 17 | 90.6022 | 11060
1034 | 124972 | -144764 | 19 | 19 | 90.6334 | 11060.7
1035 | 124817 | -146263 | 20 | 20 | 90.5987 | 11060.6
1036 | 124726 | -145256 | 22 | 22 | 90.5812 | 11061
1037 | 127757 | -148414 | 22 | 22 | 94.4474 | 12289
1038 | 175371 | -124372 | 23 | 23 | 133.972 | 29912.6
1039 | 309944 | -870102 | 24 | 24 | 285.235 | 88746.7
1040 | 372486 | -796667 | 25 | 25 | 309.142 | 107795
1041 | 391613 | -673952 | 25 | 25 | 297.347 | 149231
1042 | 390131 | -619478 | 26 | 26 | 293.017 | 175608
1043 | 378751 | -608925 | 27 | 27 | 284.497 | 179369
1044 | 364155 | -563566 | 27 | 27 | 268.344 | 179367
1045 | 346113 | -589445 | 26 | 25 | 267.743 | 179365
1046 | 379562 | -559076 | 25 | 23 | 281.407 | 179362
1047 | 398495 | -542664 | 25 | 23 | 266.757 | 177041
1048 | 401666 | -556512 | 25 | 23 | 269.191 | 160937
1049 | 394437 | -618954 | 23 | 21 | 274.228 | 131347
1050 | 379704 | -673581 | 22 | 20 | 285.635 | 98470.6
1051 | 299273 | -695022 | 22 | 20 | 220.432 | 60922.7
1052 | 174511 | -16675.5 | 21 | 19 | 127.151 | 43554.7
1053 | 178677 | -46233.8 | 19 | 17 | 117.991 | 38643.8
1054 | 160338 | -86089.9 | 18 | 17 | 105.889 | 23673.5
1055 | 146436 | -112754 | 18 | 16 | 96.8721 | 12689.5
1056 | 149514 | -134576 | 18 | 16 | 93.7992 | 11029.6
1057 | 138740 | -125955 | 18 | 16 | 92.1736 | 11033.7
1058 | 140768 | -152114 | 16 | 15 | 92.3603 | 11036.8
1059 | 136314 | -153930 | 15 | 14 | 91.7731 | 11038.7
1060 | 150499 | -179604 | 15 | 14 | 92.8329 | 11040.5
1061 | 137530 | -159683 | 15 | 14 | 96.1685 | 12269.6
1062 | 195323 | -155760 | 15 | 14 | 136.826 | 29895.2
1063 | 316827 | -985036 | 15 | 14 | 289.35 | 88730.1
1064 | 378851 | -954415 | 13 | 12 | 314.466 | 107779
1065 | 397991 | -856191 | 13 | 12 | 305.27 | 149218
1066 | 396036 | -805529 | 15 | 13 | 301.904 | 175597
1067 | 380172 | -816736 | 15 | 14 | 294.907 | 179359
1068 | 361072 | -716082 | 18 | 16 | 277.029 | 179358
1069 | 351222 | -695888 | 19 | 17 | 274.317 | 179356
1070 | 384205 | -570285 | 19 | 17 | 280.813 | 179353
1071 | 403105 | -526048 | 21 | 19 | 284.75 | 177034
1072 | 405980 | -544665 | 21 | 18 | 286.705 | 160930
1073 | 400935 | -622924 | 20 | 18 | 287.649 | 131340
1074 | 389243 | -714367 | 18 | 16 | 286.299 | 98463.7
1075 | 311179 | -740801 | 17 | 15 | 222.937 | 60915.6
1076 | 194537 | -14704 | 14 | 13 | 131.419 | 43548
1077 | 182140 | -44635.4 | 13 | 12 | 118.651 | 38636.7
1078 | 163794 | -77667.4 | 12 | 11 | 106.652 | 23666.7
1079 | 149684 | -109007 | 10 | 10 | 97.5992 | 12682.2
1080 | 143822 | -134020 | 11 | 10 | 93.7385 | 11021.6
1081 | 141652 | -143511 | 12 | 11 | 92.5248 | 11025.2
1082 | 156836 | -174594 | 11 | 10 | 93.6604 | 11027.7
1083 | 138747 | -164309 | 8 | 8 | 92.6213 | 11029.9
1084 | 143977 | -191477 | 7 | 6 | 92.974 | 11032.9
1085 | 139398 | -196625 | 7 | 6 | 99.8977 | 12262.1
1086 | 185779 | -189852 | 5 | 4 | 135.511 | 29887
1087 | 317711 | -1131990 | 4 | 3 | 296.916 | 88722.3
1088 | 380057 | -1007810 | 8 | 7 | 318.014 | 107772
1089 | 399277 | -857289 | 11 | 10 | 304.75 | 149212
1090 | 397416 | -785941 | 15 | 14 | 301.337 | 175591
1091 | 379013 | -745949 | 20 | 18 | 292.33 | 179353
1092 | 366256 | -631096 | 24 | 22 | 272.194 | 179352
1093 | 352636 | -606061 | 25 | 23 | 249.959 | 179350
1094 | 385639 | -554505 | 25 | 23 | 262.078 | 179347
1095 | 404301 | -541299 | 25 | 23 | 266.883 | 177026
1096 | 407190 | -543696 | 25 | 23 | 268.34 | 160922
1097 | 401277 | -595705 | 24 | 23 | 273.519 | 131332
1098 | 386052 | -633359 | 24 | 24 | 272.755 | 98456.1
1099 | 303344 | -647673 | 24 | 23 | 217.403 | 60908.2
1100 | 180563 | -16864.3 | 24 | 24 | 127.849 | 43540.2
1101 | 186382 | -22531.4 | 24 | 24 | 118.467 | 38629.4
1102 | 167256 | -56584.8 | 24 | 24 | 106.567 | 23659
1103 | 152927 | -75971.3 | 25 | 25 | 97.4395 | 12674
1104 | 147834 | -92438.2 | 26 | 26 | 93.5696 | 11014.2
1105 | 147252 | -104464 | 26 | 26 | 92.9602 | 11018.2
1106 | 142892 | -103142 | 27 | 27 | 92.7929 | 11021.5
1107 | 141682 | -118314 | 26 | 26 | 92.5462 | 11024.2
1108 | 141471 | -137213 | 25 | 25 | 92.3961 | 11026
1109 | 142789 | -143408 | 24 | 24 | 96.1955 | 12255.4
1110 | 205189 | -122033 | 26 | 25 | 137.341 | 29880.8
1111 | 320759 | -799714 | 26 | 24 | 279.914 | 88716.5
1112 | 382735 | -743195 | 26 | 24 | 300.757 | 107766
1113 | 401691 | -562174 | 28 | 26 | 288.622 | 149206
1114 | 399650 | -476165 | 30 | 27 | 264.722 | 175584
1115 | 396158 | -517710 | 29 | 26 | 278.26 | 179346
1116 | 372720 | -434904 | 30 | 27 | 241.954 | 179345
1117 | 354799 | -404255 | 31 | 27 | 239.851 | 179343
1118 | 387294 | -460501 | 22 | 22 | 257.045 | 179340
1119 | 406227 | -344937 | 32 | 28 | 264.561 | 177021
1120 | 409022 | -351503 | 32 | 28 | 285.029 | 160917
1121 | 403081 | -405967 | 30 | 26 | 281.342 | 131325
1122 | 395820 | -537688 | 25 | 23 | 256.689 | 98448.1
1123 | 314404 | -598864 | 23 | 21 | 213.84 | 60899.6
1124 | 180526 | -17272 | 23 | 21 | 127.663 | 43532.9
1125 | 193007 | -27435.2 | 17 | 16 | 119.523 | 38622.2
1126 | 169372 | -43206.6 | 17 | 16 | 107.054 | 23651.9
1127 | 154887 | -68917.6 | 17 | 16 | 98.1294 | 12667.3
1128 | 148107 | -84086.7 | 18 | 17 | 93.8229 | 11007.1
1129 | 159094 | -121405 | 15 | 15 | 94.0098 | 11010.6
1130 | 143602 | -110715 | 16 | 15 | 92.5554 | 11013.5
1131 | 160497 | -147471 | 14 | 14 | 93.9866 | 11016.8
1132 | 140852 | -138926 | 12 | 12 | 92.7832 | 11018.7
1133 | 149572 | -167599 | 11 | 10 | 97.0436 | 12249.3
1134 | 189499 | -137824 | 11 | 10 | 136.531 | 29874.1
1135 | 320446 | -959189 | 12 | 12 | 286.455 | 88709.6
1136 | 382230 | -892088 | 14 | 14 | 309.689 | 107759
1137 | 401176 | -775800 | 16 | 16 | 302.051 | 149202
1138 | 399255 | -645852 | 22 | 20 | 292.98 | 175581
1139 | 387045 | -623692 | 25 | 23 | 284.059 | 179343
1140 | 371723 | -527886 | 29 | 26 | 265.582 | 179342
1141 | 354515 | -499561 | 31 | 28 | 242.74 | 179340
1142 | 387959 | -341505 | 35 | 31 | 257.775 | 179337
1143 | 422316 | -295059 | 39 | 33 | 266.159 | 177018
1144 | 435343 | -285937 | 40 | 34 | 268.589 | 160912
1145 | 411188 | -328914 | 37 | 32 | 262.261 | 131320
1146 | 386818 | -378460 | 36 | 31 | 253.314 | 98442.5
1147 | 306869 | -449481 | 35 | 30 | 204.034 | 60893.8
1148 | 181456 | -10595.2 | 35 | 30 | 126.599 | 43526
1149 | 162289 | -15527.1 | 35 | 31 | 111.449 | 38615.5
1150 | 177033 | -21516.3 | 35 | 31 | 107.236 | 23644.8
1151 | 160684 | -26491.6 | 38 | 34 | 97.9333 | 12658.8
1152 | 153765 | -31895.5 | 38 | 34 | 94.4121 | 10998.5
1153 | 150223 | -36156.4 | 38 | 35 | 89.2313 | 11002.3
1154 | 148114 | -42500.2 | 38 | 35 | 89.2552 | 11005.1
1155 | 146137 | -46881.2 | 37 | 35 | 89.0698 | 11008.2
1156 | 144971 | -55698 | 36 | 35 | 89.1004 | 11010.7
1157 | 146962 | -63415.5 | 36 | 35 | 89.3462 | 11013
1158 | 142419 | -58380.8 | 37 | 35 | 86.6152 | 11015.2
1159 | 143668 | -79451.3 | 34 | 33 | 85.4193 | 11017.2
1160 | 127212 | -750719 | 32 | 32 | 137.055 | 11018.8
1161 | 164941 | -650650 | 34 | 33 | 132.168 | 11020.6
1162 | 144435 | -486523 | 36 | 34 | 121.185 | 11014.6
1163 | 178473 | -456051 | 39 | 36 | 118.816 | 11011
1164 | 174765 | -428902 | 40 | 37 | 116.733 | 11009.7
1165 | 168665 | -443410 | 39 | 36 | 116.956 | 11008.9
1166 | 169137 | -451152 | 39 | 36 | 98.2209 | 11008.6
1167 | 124796 | -9853.59 | 39 | 36 | 76.9222 | 11008.5
1168 | 122453 | -11663.3 | 38 | 35 | 76.6395 | 11008.6
1169 | 136942 | -17889 | 36 | 33 | 79.9595 | 11010.7
1170 | 142623 | -28425.2 | 33 | 31 | 87.2212 | 11013.6
1171 | 139816 | -43624.2 | 28 | 27 | 91.9384 | 11015.6
1172 | 137613 | -59832.6 | 29 | 28 | 93.3033 | 11018.3
1173 | 142323 | -79000.9 | 26 | 26 | 93.8023 | 11021
1174 | 134526 | -82090.3 | 24 | 24 | 92.3893 | 11023.5
1175 | 144322 | -105049 | 25 | 25 | 93.1025 | 11025.9
1176 | 132973 | -96558 | 24 | 23 | 90.6326 | 11027.7
1177 | 134298 | -118021 | 23 | 22 | 87.1831 | 4099.69
1178 | 131416 | -122764 | 23 | 22 | 86.1186 | 4101.05
1179 | 133536 | -145780 | 22 | 21 | 86.6334 | 4102.73
1180 | 130084 | -153059 | 20 | 19 | 86.5981 | 4104.19
1181 | 129470 | -153197 | 20 | 19 | 86.7002 | 4106.56
1182 | 128906 | -167055 | 19 | 18 | 85.1777 | 4108.59
1183 | 129942 | -199905 | 17 | 17 | 85.6689 | 4109.95
1184 | 127892 | -174511 | 21 | 20 | 82.7085 | 4111.41
1185 | 132263 | -140415 | 26 | 23 | 80.2209 | 4113.73
1186 | 129073 | -102655 | 28 | 24 | 80.4217 | 4115.74
1187 | 132674 | -89961.9 | 31 | 26 | 80.7486 | 4117.77
1188 | 131996 | -83101.7 | 32 | 26 | 80.8851 | 4119.01
1189 | 132668 | -67710.4 | 35 | 28 | 81.104 | 4119.77
1190 | 135931 | -60165.9 | 38 | 30 | 81.3638 | 4120.41
1191 | 134306 | -52636.4 | 39 | 31 | 80.7301 | 4120.68
1192 | 134977 | -47964.9 | 40 | 32 | 80.6146 | 4120.83
1193 | 133968 | -46948 | 40 | 32 | 80.3629 | 4121.01
1194 | 132247 | -58165.2 | 32 | 28 | 84.2844 | 4121.35
1195 | 130454 | -67382.5 | 31 | 27 | 88.2822 | 4121.93
1196 | 128925 | -77054.6 | 28 | 26 | 89.8465 | 4122.8
1197 | 127411 | -91187.4 | 26 | 24 | 89.8026 | 4123.96
1198 | 126668 | -106222 | 27 | 25 | 89.4349 | 4125.04
1199 | 128241 | -135702 | 26 | 24 | 89.5134 | 4126.13
1200 | 125899 | -143510 | 26 | 24 | 88.531 | 4127.16
1201 | 133884 | -161089 | 25 | 24 | 86.9052 | 4129.06
1202 | 125099 | -147634 | 24 | 23 | 86.071 | 4130.63
1203 | 128303 | -166433 | 26 | 25 | 86.2111 | 4132.21
1204 | 124777 | -165439 | 27 | 26 | 86.1567 | 4133.03
1205 | 124616 | -156698 | 28 | 27 | 86.2752 | 4134.73
1206 | 125631 | -166803 | 26 | 25 | 85.1974 | 4136.15
1207 | 124151 | -169744 | 25 | 24 | 82.724 | 4136.98
1208 | 124635 | -161809 | 26 | 25 | 80.7041 | 4137.91
1209 | 124301 | -122906 | 29 | 27 | 79.9472 | 4138.73
1210 | 137286 | -103320 | 37 | 33 | 81.4043 | 4139.5
1211 | 127201 | -66342.3 | 40 | 35 | 79.595 | 4140.1
1212 | 132320 | -67847.7 | 42 | 36 | 81.1164 | 4141.26
1213 | 127807 | -57228.1 | 44 | 38 | 79.9413 | 4140.73
1214 | 129309 | -57574.1 | 44 | 38 | 80.6956 | 4141.11
1215 | 126943 | -58027.3 | 43 | 37 | 80.1901 | 4141.51
1216 | 126608 | -66946.9 | 43 | 37 | 80.7746 | 4142.05
1217 | 125998 | -73029.3 | 42 | 37 | 81.5106 | 4142.69
1218 | 128406 | -82799.7 | 40 | 35 | 84.8572 | 4143.32
1219 | 125217 | -88055.8 | 40 | 36 | 87.7952 | 4144.15
1220 | 125121 | -102246 | 37 | 35 | 89.4001 | 4144.95
1221 | 125042 | -114436 | 36 | 36 | 90.258 | 4145.58
1222 | 124784 | -119374 | 36 | 36 | 90.4385 | 4146.13
1223 | 124658 | -114472 | 36 | 36 | 88.4858 | 4147.04
1224 | 126132 | -131488 | 36 | 36 | 88.7276 | 4147.91
1225 | 124783 | -126378 | 37 | 36 | 91.1865 | 11078.6
1226 | 124951 | -134305 | 36 | 35 | 91.1709 | 11079.6
1227 | 124837 | -136623 | 36 | 35 | 91.1609 | 11079.7
1228 | 124735 | -141779 | 36 | 34 | 91.1381 | 11080.2
1229 | 128175 | -144109 | 36 | 34 | 95.4147 | 12308.4
1230 | 175959 | -112645 | 36 | 34 | 135.341 | 29932.1
1231 | 311484 | -801421 | 35 | 34 | 282.556 | 88766.4
1232 | 374034 | -713077 | 34 | 34 | 305.423 | 107815
1233 | 393062 | -562725 | 35 | 35 | 293.101 | 149242
1234 | 396175 | -529087 | 35 | 35 | 287.823 | 175619
1235 | 380638 | -486428 | 36 | 36 | 277.418 | 179379
1236 | 374207 | -444790 | 36 | 35 | 241.902 | 179377
1237 | 348041 | -454420 | 34 | 34 | 259.363 | 179374
1238 | 381206 | -430387 | 32 | 32 | 256.875 | 179371
1239 | 400045 | -421196 | 32 | 32 | 264.584 | 177050
1240 | 403221 | -421753 | 33 | 33 | 266.285 | 160945
1241 | 396408 | -452344 | 33 | 33 | 265.682 | 131354
1242 | 379078 | -473417 | 34 | 34 | 273.679 | 98476.5
1243 | 294434 | -523649 | 33 | 33 | 209.244 | 60927.2
1244 | 176499 | -11103.3 | 33 | 33 | 126.391 | 43558.7
1245 | 157586 | -17864.7 | 33 | 33 | 111.71 | 38648.4
1246 | 166940 | -31814.2 | 33 | 33 | 106.894 | 23678.3
1247 | 151384 | -51584.5 | 33 | 33 | 97.7039 | 12692.8
1248 | 144608 | -65568.6 | 32 | 32 | 93.6494 | 11032.5
1249 | 141669 | -78961.7 | 31 | 31 | 92.7348 | 11036.1
1250 | 140084 | -94560.8 | 30 | 29 | 92.5634 | 11038.8
1251 | 139028 | -106233 | 30 | 29 | 92.4526 | 11041.4
1252 | 138115 | -118219 | 30 | 28 | 92.3468 | 11043.5
1253 | 140581 | -129259 | 29 | 27 | 96.1143 | 12273.1
1254 | 187721 | -117098 | 26 | 25 | 135.922 | 29898.1
1255 | 319242 | -861558 | 25 | 24 | 284.423 | 88733.6
1256 | 381266 | -790802 | 24 | 22 | 300.984 | 107783
1257 | 400093 | -647939 | 23 | 21 | 293.529 | 149222
1258 | 398157 | -576444 | 24 | 22 | 289.645 | 175599
1259 | 387915 | -577907 | 24 | 22 | 281.908 | 179361
1260 | 372595 | -508816 | 25 | 22 | 265.154 | 179360
1261 | 353339 | -483720 | 26 | 23 | 262.032 | 179358
1262 | 386384 | -436667 | 26 | 22 | 257.556 | 179355
1263 | 404958 | -429370 | 26 | 22 | 264.429 | 177035
1264 | 407745 | -454225 | 25 | 21 | 266.063 | 160931
1265 | 401277 | -521881 | 23 | 20 | 263.474 | 131341
1266 | 394991 | -650986 | 19 | 17 | 272.954 | 98464.8
1267 | 314812 | -712323 | 17 | 15 | 221.454 | 60916.9
1268 | 179154 | -19394.8 | 17 | 15 | 127.146 | 43549.7
1269 | 184131 | -45883.2 | 17 | 15 | 118.087 | 38638.6
1270 | 165843 | -85524.5 | 15 | 13 | 106.032 | 23668.6
1271 | 161468 | -113293 | 15 | 13 | 98.0016 | 12684.7
1272 | 145290 | -117612 | 13 | 12 | 93.6098 | 11024.9
1273 | 147026 | -142807 | 11 | 10 | 93.0451 | 11029.2
1274 | 141449 | -151075 | 10 | 10 | 92.7078 | 11031.7
1275 | 142100 | -165752 | 10 | 9 | 92.7649 | 11033.9
1276 | 138930 | -172165 | 9 | 8 | 92.5696 | 11035.7
1277 | 140691 | -189908 | 8 | 7 | 96.4054 | 12265
1278 | 187102 | -173445 | 7 | 6 | 135.706 | 29889.8
1279 | 318687 | -1102950 | 6 | 5 | 295.873 | 88725
1280 | 380954 | -978222 | 9 | 8 | 308.489 | 107774
1281 | 400202 | -766913 | 12 | 10 | 299.616 | 149214
1282 | 398036 | -672534 | 15 | 12 | 293.389 | 175593
1283 | 383987 | -664061 | 17 | 14 | 285.485 | 179355
1284 | 368180 | -596993 | 18 | 15 | 269.289 | 179355
1285 | 352818 | -580711 | 19 | 16 | 267.609 | 179353
1286 | 385908 | -521708 | 20 | 16 | 279.155 | 179350
1287 | 404300 | -513308 | 20 | 15 | 284.263 | 177030
1288 | 407855 | -532438 | 20 | 16 | 286.738 | 160926
1289 | 400246 | -609107 | 18 | 15 | 287.173 | 131337
1290 | 385958 | -737161 | 14 | 11 | 284.194 | 98460.6
1291 | 320290 | -804260 | 12 | 10 | 227.237 | 60913
1292 | 213913 | -19591.6 | 11 | 9 | 134.01 | 43545.5
1293 | 181033 | -66963.8 | 9 | 8 | 117.654 | 38634.3
1294 | 178406 | -109159 | 9 | 8 | 107.135 | 23664.9
1295 | 150142 | -115492 | 8 | 7 | 97.4804 | 12681.3
1296 | 149946 | -146569 | 8 | 7 | 94.0511 | 11021.6
1297 | 142196 | -153924 | 6 | 5 | 92.938 | 11024.9
1298 | 143053 | -179185 | 6 | 5 | 92.9904 | 11027.3
1299 | 139261 | -189953 | 5 | 4 | 92.2442 | 11029.4
1300 | 144115 | -227305 | 4 | 3 | 97.5004 | 11031.2
1301 | 139553 | -233416 | 4 | 3 | 104.283 | 12260.5
1302 | 209526 | -238151 | 4 | 3 | 137.357 | 29886.8
1303 | 317965 | -1179550 | 4 | 3 | 300.722 | 88723
1304 | 379999 | -1128220 | 5 | 4 | 316.965 | 107774
1305 | 399561 | -893625 | 9 | 7 | 306.134 | 149212
1306 | 397438 | -785875 | 13 | 10 | 299.648 | 175591
1307 | 378862 | -746435 | 16 | 13 | 289.898 | 179353
1308 | 362458 | -650843 | 18 | 15 | 271.802 | 179353
1309 | 352404 | -611676 | 20 | 17 | 268.074 | 179351
1310 | 385435 | -555160 | 21 | 18 | 260.941 | 179348
1311 | 404161 | -545548 | 22 | 18 | 266.753 | 177028
1312 | 407132 | -546161 | 22 | 18 | 267.868 | 160924
1313 | 402630 | -632203 | 20 | 16 | 268.36 | 131334
1314 | 394200 | -743575 | 17 | 14 | 276.959 | 98458
1315 | 313811 | -793742 | 14 | 12 | 225.797 | 60910.4
1316 | 213923 | -19658.3 | 12 | 10 | 134.159 | 43542.9
1317 | 180885 | -56936.9 | 12 | 10 | 117.756 | 38631.9
1318 | 169502 | -98717.9 | 12 | 10 | 106.51 | 23662.4
1319 | 150191 | -120932 | 10 | 9 | 97.3888 | 12678.7
1320 | 148238 | -147833 | 9 | 8 | 93.8345 | 11018.9
1321 | 141756 | -162294 | 8 | 7 | 88.7443 | 11022.4
1322 | 142243 | -177477 | 8 | 7 | 88.7897 | 11025
1323 | 138726 | -185947 | 7 | 6 | 88.5648 | 11027.9
1324 | 138663 | -198809 | 6 | 5 | 92.1396 | 11030
1325 | 136341 | -201985 | 7 | 6 | 92.838 | 11032
1326 | 136034 | -209678 | 7 | 6 | 92.4368 | 11033.8
1327 | 134325 | -212375 | 7 | 6 | 90.5982 | 11035.5
1328 | 122273 | -1093670 | 8 | 7 | 161.745 | 11037.1
1329 | 121633 | -915963 | 11 | 9 | 152.341 | 11038.3
1330 | 121148 | -728680 | 16 | 13 | 138.944 | 11026.4
1331 | 120673 | -649813 | 18 | 15 | 132.592 | 11023.3
1332 | 120321 | -566659 | 23 | 19 | 126.375 | 11021.3
1333 | 119828 | -532910 | 24 | 19 | 104.007 | 11020.2
1334 | 119568 | -510597 | 26 | 21 | 102.368 | 11019.5
1335 | 122610 | -17195.7 | 26 | 20 | 77.1471 | 11018.9
1336 | 147121 | -34581.3 | 27 | 21 | 83.5328 | 11018.7
1337 | 143253 | -46527.5 | 26 | 21 | 83.2772 | 11021.9
1338 | 138473 | -55996.7 | 21 | 17 | 87.0465 | 11025
1339 | 143275 | -77294.1 | 18 | 16 | 92.179 | 11028
1340 | 132612 | -83924.6 | 18 | 15 | 92.7403 | 11030.6
1341 | 148471 | -118257 | 18 | 16 | 93.9802 | 11033.4
1342 | 129699 | -117987 | 16 | 15 | 92.347 | 11035.3
1343 | 136893 | -153543 | 16 | 14 | 91.9836 | 11038.2
1344 | 128333 | -163501 | 14 | 13 | 90.6023 | 11039.7
1345 | 127876 | -186693 | 13 | 12 | 88.0154 | 4112.03
1346 | 133672 | -206219 | 11 | 10 | 90.7882 | 4114.16
1347 | 126258 | -198290 | 11 | 10 | 90.8582 | 4116.54
1348 | 125700 | -222047 | 10 | 9 | 91.7391 | 4118.9
1349 | 126671 | -245928 | 11 | 10 | 94.2584 | 4120.35
1350 | 124795 | -250756 | 12 | 11 | 94.6319 | 4121.91
1351 | 124367 | -260963 | 13 | 12 | 93.0335 | 4124.37
1352 | 124088 | -254712 | 15 | 14 | 90.5282 | 4126.52
1353 | 124312 | -225337 | 19 | 17 | 86.824 | 4128.68
1354 | 126341 | -186886 | 23 | 21 | 83.7562 | 4130.77
1355 | 124928 | -147379 | 29 | 26 | 79.8854 | 4132.67
1356 | 125933 | -126703 | 32 | 28 | 80.0867 | 4134.34
1357 | 126048 | -105057 | 36 | 31 | 80.2296 | 4135.59
1358 | 129627 | -99335 | 37 | 32 | 80.6114 | 4136.49
1359 | 126519 | -88390 | 38 | 33 | 80.4824 | 4137.3
1360 | 127567 | -95511.4 | 39 | 34 | 80.7628 | 4137.93
1361 | 125531 | -99304.5 | 38 | 33 | 81.1988 | 4138.56
1362 | 125123 | -111303 | 37 | 33 | 84.2629 | 4139.46
1363 | 124819 | -131517 | 36 | 32 | 88.5364 | 4140.43
1364 | 124682 | -141696 | 35 | 32 | 90.1099 | 4141.42
1365 | 124533 | -149848 | 34 | 32 | 90.0891 | 4142.49
1366 | 124389 | -156338 | 33 | 31 | 90.0637 | 4143.5
1367 | 124274 | -160470 | 33 | 31 | 89.2206 | 4144.5
1368 | 125033 | -166866 | 32 | 30 | 88.4739 | 4145.47
1369 | 124331 | -162051 | 32 | 30 | 91.3737 | 11076.7
1370 | 125168 | -173459 | 31 | 30 | 91.4042 | 11077.8
1371 | 124243 | -176462 | 30 | 29 | 94.063 | 11077.9
1372 | 124117 | -180487 | 29 | 28 | 94.2747 | 11078.6
1373 | 131484 | -185581 | 27 | 27 | 98.7015 | 12306.9
1374 | 174553 | -142782 | 25 | 25 | 135.317 | 29930.8
1375 | 309862 | -973525 | 24 | 24 | 291.126 | 88765.4
1376 | 372611 | -830204 | 26 | 26 | 307.944 | 107814
1377 | 392036 | -667159 | 29 | 28 | 294.938 | 149240
1378 | 390578 | -594809 | 31 | 30 | 290.779 | 175618
1379 | 377577 | -546852 | 34 | 32 | 281.183 | 179377
1380 | 372231 | -463496 | 37 | 34 | 242.216 | 179375
1381 | 361994 | -414118 | 39 | 36 | 239.924 | 179372
1382 | 416014 | -365213 | 41 | 37 | 260.63 | 179369
1383 | 444752 | -347741 | 42 | 38 | 269.408 | 177048
1384 | 439185 | -344055 | 41 | 37 | 269.996 | 160941
1385 | 425856 | -370060 | 40 | 36 | 266.421 | 131349
1386 | 379992 | -384558 | 39 | 36 | 252.342 | 98470.4
1387 | 317265 | -474383 | 37 | 34 | 205.355 | 60920.8
1388 | 179500 | -8801.2 | 38 | 35 | 125.88 | 43552.6
1389 | 157461 | -8403.49 | 37 | 35 | 107.238 | 38642.7
1390 | 159066 | -17698.1 | 39 | 37 | 102.793 | 23672.8
1391 | 153991 | -25073.6 | 38 | 36 | 97.0227 | 12686.4
1392 | 146914 | -34233.5 | 37 | 35 | 93.2897 | 11025.7
1393 | 143782 | -49628 | 33 | 32 | 92.3542 | 11029.1
1394 | 146128 | -56859.8 | 32 | 31 | 92.898 | 11031.8
1395 | 140480 | -55538.6 | 34 | 33 | 91.3647 | 11034.1
1396 | 139424 | -65125.1 | 34 | 33 | 91.2832 | 11036.1
1397 | 148827 | -74627.1 | 37 | 34 | 97.247 | 12265.2
1398 | 189715 | -54344.5 | 34 | 32 | 134.598 | 29889.7
1399 | 320063 | -664877 | 32 | 31 | 273.091 | 88725.3
1400 | 405020 | -558700 | 38 | 34 | 288.502 | 107774
1401 | 400650 | -447239 | 35 | 32 | 264.468 | 149216
1402 | 398623 | -449563 | 34 | 30 | 264.337 | 175592
1403 | 395166 | -500799 | 32 | 29 | 278.156 | 179354
1404 | 379953 | -511528 | 29 | 26 | 264.483 | 179352
1405 | 354014 | -491294 | 30 | 27 | 260.469 | 179350
1406 | 387053 | -467516 | 29 | 26 | 257.768 | 179348
1407 | 405626 | -449988 | 29 | 26 | 264.82 | 177027
1408 | 408392 | -441091 | 29 | 26 | 265.8 | 160922
1409 | 405579 | -507314 | 28 | 26 | 266.578 | 131332
1410 | 387457 | -546338 | 28 | 26 | 259.23 | 98455.8
1411 | 305873 | -587179 | 27 | 25 | 213.153 | 60907.7
1412 | 180082 | -14570.4 | 26 | 24 | 127.781 | 43539.8
1413 | 177842 | -23418.6 | 24 | 22 | 115.689 | 38629.4
1414 | 168779 | -44923 | 22 | 21 | 106.731 | 23659.1
1415 | 154363 | -77856.7 | 21 | 20 | 97.581 | 12674
1416 | 147545 | -101897 | 20 | 19 | 93.5345 | 11014.3
1417 | 144718 | -124043 | 18 | 16 | 92.6148 | 11053.4
1418 | 143005 | -150591 | 17 | 15 | 92.3959 | 11056.9
1419 | 141523 | -170123 | 15 | 13 | 92.227 | 11060
1420 | 140331 | -182246 | 16 | 13 | 92.0713 | 11062.7
1421 | 142351 | -192190 | 17 | 14 | 95.781 | 12297.3
1422 | 189304 | -165950 | 19 | 16 | 135.461 | 29984.8
1423 | 320376 | -955961 | 20 | 17 | 289.785 | 89027.9
1424 | 382380 | -850947 | 22 | 18 | 303.962 | 108145
1425 | 401287 | -711858 | 23 | 18 | 301.688 | 149730
1426 | 399542 | -641575 | 25 | 20 | 293.126 | 176201
1427 | 384304 | -574272 | 28 | 22 | 281.099 | 179976
1428 | 371138 | -473639 | 30 | 24 | 247.715 | 179974
1429 | 354820 | -430821 | 31 | 26 | 239.77 | 179972
1430 | 387993 | -379750 | 33 | 27 | 257.354 | 179970
1431 | 406350 | -341371 | 34 | 28 | 269.954 | 177641
1432 | 409372 | -353335 | 34 | 28 | 284.921 | 161480
1433 | 404799 | -412805 | 33 | 28 | 262.916 | 131784
1434 | 388391 | -454881 | 33 | 28 | 252.78 | 98791.3
1435 | 299737 | -490069 | 33 | 28 | 205.924 | 61110.6
1436 | 181278 | -12687.3 | 32 | 28 | 127.375 | 43681.7
1437 | 162114 | -18502.6 | 32 | 27 | 112.19 | 38753.9
1438 | 174960 | -26080 | 32 | 28 | 107.444 | 23731.3
1439 | 158453 | -40128.3 | 31 | 28 | 98.1996 | 12707
1440 | 151382 | -57203.3 | 31 | 27 | 94.1689 | 11041.1
1441 | 148386 | -66086.3 | 30 | 27 | 93.1469 | 11045
1442 | 146309 | -78093.3 | 30 | 27 | 92.9653 | 11048
1443 | 144744 | -90591.4 | 29 | 26 | 92.817 | 11050.8
1444 | 143505 | -96929.2 | 29 | 26 | 92.6977 | 11053.2
1445 | 145667 | -106581 | 29 | 26 | 96.5556 | 12287.4
1446 | 197570 | -87386.1 | 29 | 26 | 136.915 | 29974.7
1447 | 322813 | -673012 | 31 | 28 | 271.844 | 89017.3
1448 | 384853 | -599432 | 33 | 30 | 286.465 | 108134
1449 | 403374 | -422891 | 35 | 32 | 264.822 | 149722
1450 | 418871 | -373573 | 38 | 34 | 265.413 | 176192
1451 | 419913 | -317288 | 40 | 36 | 257.758 | 179966
1452 | 427905 | -276424 | 43 | 37 | 244.939 | 179963
1453 | 397522 | -250076 | 43 | 37 | 242.176 | 179961
1454 | 438602 | -228710 | 42 | 37 | 262.105 | 179958
1455 | 462611 | -217785 | 42 | 36 | 270.418 | 177630
1456 | 452254 | -215694 | 40 | 35 | 270.207 | 161468
1457 | 433794 | -247661 | 39 | 34 | 264.241 | 131771
1458 | 385701 | -307642 | 37 | 33 | 251.234 | 98778.3
1459 | 317111 | -376621 | 37 | 33 | 180.276 | 61097.6
1460 | 184394 | 0 | 36 | 32 | 121.799 | 43669.3
1461 | 163743 | -9744.58 | 36 | 32 | 109.997 | 38741.5
1462 | 150249 | -15353.9 | 35 | 31 | 99.7912 | 23718
1463 | 166741 | -18313 | 33 | 29 | 97.5829 | 12692.8
1464 | 157116 | -29124 | 32 | 28 | 94.1361 | 11026.1
1465 | 153383 | -38076.3 | 31 | 27 | 93.6747 | 11029.8
1466 | 150527 | -53210 | 29 | 26 | 93.5355 | 11033.1
1467 | 148211 | -64096.7 | 28 | 24 | 93.2723 | 11036.1
1468 | 146421 | -78983.2 | 27 | 23 | 93.0539 | 11038.8
1469 | 148083 | -97836.2 | 25 | 22 | 96.7382 | 12273.4
1470 | 195144 | -91021 | 24 | 21 | 136.499 | 29961.1
1471 | 323782 | -762285 | 24 | 21 | 276.104 | 89004.3
1472 | 384709 | -716007 | 24 | 20 | 292.714 | 108122
1473 | 403280 | -565492 | 24 | 20 | 287.622 | 149713
1474 | 401474 | -512350 | 25 | 21 | 284.673 | 176185
1475 | 394854 | -507491 | 26 | 22 | 276.742 | 179961
1476 | 384729 | -448296 | 27 | 22 | 243.417 | 179961
1477 | 356122 | -423850 | 28 | 23 | 240.11 | 179959
1478 | 389082 | -380610 | 28 | 23 | 257.405 | 179957
1479 | 407464 | -358168 | 29 | 23 | 283.602 | 177630
1480 | 410255 | -394381 | 27 | 23 | 284.962 | 161469
1481 | 404758 | -448669 | 26 | 21 | 280.763 | 131774
1482 | 397808 | -554998 | 24 | 20 | 251.431 | 98782.3
1483 | 313282 | -584444 | 23 | 20 | 193.496 | 61102.4
1484 | 181575 | -17329.3 | 23 | 19 | 127.716 | 43674.2
1485 | 173848 | -25399.4 | 22 | 18 | 115.764 | 38746.3
1486 | 173831 | -44646.7 | 21 | 18 | 107.067 | 23722.6
1487 | 157795 | -68313.1 | 21 | 17 | 97.8219 | 12699.3
1488 | 150765 | -88843.1 | 20 | 16 | 93.7838 | 11033.6
1489 | 147426 | -110102 | 20 | 17 | 88.7544 | 11037.7
1490 | 145429 | -126530 | 19 | 16 | 88.5734 | 11041.2
1491 | 143588 | -137562 | 19 | 16 | 88.4088 | 11045
1492 | 143313 | -151898 | 19 | 16 | 88.3774 | 11048.1
1493 | 141055 | -158857 | 19 | 16 | 88.2221 | 11051
1494 | 139909 | -168221 | 19 | 16 | 86.9034 | 11053.6
1495 | 138935 | -174263 | 20 | 17 | 84.3948 | 11056.1
1496 | 124961 | -1001340 | 21 | 18 | 156.464 | 11058.5
1497 | 127038 | -872204 | 22 | 18 | 148.549 | 11060.6
1498 | 123753 | -719235 | 24 | 19 | 135.956 | 11051
1499 | 123187 | -669963 | 25 | 21 | 131.634 | 11047.1
1500 | 122686 | -621279 | 27 | 22 | 109.011 | 11045.7
1501 | 122293 | -567909 | 29 | 24 | 105.493 | 11044.8
1502 | 121893 | -528938 | 30 | 25 | 102.822 | 11044.5
1503 | 123002 | -15620.4 | 32 | 25 | 77.1472 | 11044.2
1504 | 121316 | -20618.3 | 32 | 26 | 77.0361 | 11044.2
1505 | 146130 | -35985.7 | 31 | 25 | 83.568 | 11047.9
1506 | 141224 | -39680.8 | 31 | 25 | 87.4773 | 11050.7
1507 | 138400 | -55177.6 | 30 | 25 | 91.6691 | 11053.3
1508 | 136073 | -71771.7 | 29 | 24 | 93.0702 | 11056.5
1509 | 134563 | -88827.8 | 28 | 24 | 92.9208 | 11059
1510 | 133441 | -101902 | 27 | 23 | 92.8067 | 11061.5
1511 | 132640 | -115926 | 26 | 23 | 91.9269 | 11063.8
1512 | 132824 | -125172 | 25 | 21 | 91.1904 | 11066.1
1513 | 131219 | -127765 | 25 | 21 | 86.6948 | 4113.52
1514 | 130615 | -129545 | 24 | 21 | 86.7249 | 4115.51
1515 | 130831 | -133479 | 24 | 21 | 86.7747 | 4117.39
1516 | 129608 | -136306 | 24 | 21 | 86.7112 | 4118.88
1517 | 129132 | -144372 | 24 | 21 | 86.5738 | 4120.35
1518 | 128638 | -160538 | 24 | 21 | 85.1908 | 4121.72
1519 | 128253 | -165261 | 25 | 22 | 82.6451 | 4123.05
1520 | 128127 | -163831 | 27 | 23 | 80.2438 | 4124.71
1521 | 127859 | -127004 | 28 | 24 | 80.1004 | 4126.43
1522 | 130069 | -96428.5 | 30 | 26 | 80.6476 | 4128.21
1523 | 129913 | -82530.5 | 31 | 27 | 80.6765 | 4129.84
1524 | 131045 | -77271.7 | 33 | 28 | 80.7782 | 4131.09
1525 | 131477 | -73283.9 | 33 | 28 | 80.8553 | 4131.61
1526 | 131274 | -69437.3 | 32 | 28 | 80.8733 | 4132.62
1527 | 131400 | -69819 | 32 | 27 | 80.8765 | 4133.32
1528 | 131019 | -74384.7 | 30 | 26 | 80.8419 | 4134.28
1529 | 129944 | -84255.7 | 28 | 24 | 80.7406 | 4135.1
1530 | 128181 | -100005 | 26 | 21 | 83.9277 | 4136.24
1531 | 126646 | -127324 | 24 | 20 | 88.4413 | 4137.58
1532 | 125710 | -162251 | 22 | 19 | 89.9018 | 4139.33
1533 | 125232 | -186307 | 20 | 17 | 92.4071 | 4141.32
1534 | 124771 | -205202 | 18 | 16 | 94.4365 | 4143.18
1535 | 124339 | -220197 | 17 | 14 | 96.0509 | 4144.94
1536 | 123914 | -236251 | 15 | 12 | 96.5709 | 4146.7
1537 | 123858 | -248007 | 14 | 11 | 101.454 | 11103.1
1538 | 124615 | -263778 | 12 | 10 | 103.012 | 11104.8
1539 | 123308 | -269256 | 11 | 9 | 104.444 | 11105.8
1540 | 129958 | -275470 | 11 | 9 | 105.938 | 11107.3
1541 | 125803 | -259385 | 11 | 9 | 107.185 | 12340.6
1542 | 172730 | -247306 | 11 | 9 | 139.907 | 30026.9
1543 | 308751 | -1195150 | 14 | 11 | 304.178 | 89068.3
1544 | 371393 | -1028690 | 16 | 14 | 310.531 | 108184
1545 | 390939 | -790774 | 19 | 16 | 301.29 | 149757
1546 | 389509 | -683259 | 22 | 19 | 294.492 | 176228
1547 | 373430 | -630330 | 25 | 21 | 284.147 | 180001
1548 | 358839 | -531234 | 28 | 24 | 266.052 | 179999
1549 | 346213 | -483188 | 30 | 25 | 262.182 | 179997
1550 | 379858 | -402058 | 32 | 27 | 257.73 | 179993
1551 | 398403 | -358781 | 34 | 28 | 264.055 | 177665
1552 | 401964 | -371953 | 33 | 28 | 265.476 | 161503
1553 | 395849 | -403693 | 33 | 28 | 261.736 | 131807
1554 | 383197 | -478831 | 32 | 27 | 248.156 | 98814.6
1555 | 295551 | -520401 | 32 | 28 | 209.719 | 61133.3
1556 | 175379 | -14994.2 | 32 | 28 | 127.453 | 43704.2
1557 | 156503 | -20857.6 | 32 | 27 | 112.195 | 38776.4
1558 | 166184 | -35367.6 | 31 | 27 | 106.722 | 23753.6
1559 | 150599 | -50833.8 | 31 | 27 | 97.5248 | 12729.4
1560 | 143911 | -70236.2 | 30 | 27 | 93.4924 | 11063.2
1561 | 140940 | -87312.7 | 27 | 24 | 92.1676 | 11066.9
1562 | 139121 | -107204 | 25 | 21 | 91.9323 | 11069.6
1563 | 137890 | -133721 | 22 | 19 | 91.732 | 11072.2
1564 | 136709 | -162565 | 18 | 15 | 91.5335 | 11074.6
1565 | 138587 | -192312 | 14 | 11 | 95.5511 | 12308.8
1566 | 184896 | -193958 | 10 | 7 | 134.978 | 29996.2
1567 | 317078 | -1123590 | 9 | 6 | 297.42 | 89039.1
1568 | 379012 | -1078300 | 7 | 5 | 311.632 | 108156
1569 | 398228 | -911371 | 6 | 4 | 306.279 | 149740
1570 | 396008 | -876451 | 6 | 4 | 303.916 | 176212
1571 | 377147 | -881548 | 7 | 4 | 295.976 | 179988
1572 | 352696 | -798293 | 7 | 4 | 278.12 | 179988
1573 | 350643 | -770726 | 9 | 6 | 256.228 | 179986
1574 | 383522 | -729894 | 10 | 8 | 269.032 | 179983
1575 | 402509 | -680834 | 12 | 9 | 273.091 | 177655
1576 | 405532 | -709317 | 11 | 8 | 275.898 | 161495
1577 | 395567 | -788253 | 9 | 6 | 276.199 | 131801
1578 | 370075 | -881008 | 8 | 5 | 265.987 | 98809.6
1579 | 320996 | -946802 | 6 | 4 | 214.616 | 61129.7
1580 | 210076 | -19523.3 | 5 | 2 | 133.141 | 43700.5
1581 | 176683 | -107228 | 3 | 1 | 116.821 | 38771.7
1582 | 160284 | -163928 | 2 | 0 | 104.958 | 23750.9
1583 | 146864 | -216384 | 0 | -1 | 100.207 | 12729.3
1584 | 141189 | -239049 | -1 | -3 | 100.642 | 11064.2
1585 | 148705 | -255575 | -1 | -3 | 102.273 | 11068.7
1586 | 137341 | -237212 | -1 | -3 | 100.711 | 11072.3
1587 | 139283 | -289203 | -1 | -3 | 105.67 | 11075.4
1588 | 134662 | -294470 | -2 | -4 | 108.3 | 11077.3
1589 | 138993 | -328504 | -3 | -4 | 117.749 | 12312
1590 | 182121 | -302839 | -4 | -5 | 151.33 | 29999.9
1591 | 316221 | -1363350 | 0 | -2 | 310.474 | 89043.3
1592 | 378570 | -1195560 | 4 | 2 | 317.989 | 108161
1593 | 398015 | -946389 | 8 | 6 | 308.452 | 149741
1594 | 396115 | -830718 | 12 | 10 | 301.769 | 176212
1595 | 377664 | -758029 | 17 | 14 | 290.635 | 179986
1596 | 358311 | -632991 | 21 | 17 | 270.941 | 179985
1597 | 351547 | -585897 | 23 | 19 | 248.061 | 179983
1598 | 384638 | -525409 | 24 | 20 | 259.835 | 179980
1599 | 403363 | -478106 | 26 | 21 | 265.284 | 177651
1600 | 406436 | -479720 | 26 | 21 | 266.324 | 161490
1601 | 399250 | -525706 | 25 | 21 | 263.61 | 131796
1602 | 388884 | -595871 | 25 | 20 | 254.975 | 98803.7
1603 | 308799 | -653910 | 24 | 20 | 218.056 | 61123.5
1604 | 178511 | -19327.7 | 24 | 19 | 127.235 | 43694.6
1605 | 184689 | -37688.1 | 23 | 18 | 118.325 | 38766.5
1606 | 165844 | -65722.5 | 23 | 19 | 106.177 | 23743.9
1607 | 151580 | -94782.3 | 23 | 19 | 97.1048 | 12720.9
1608 | 145197 | -113683 | 23 | 18 | 93.1598 | 11055.3
1609 | 143325 | -130627 | 23 | 19 | 92.2584 | 11059.3
1610 | 141531 | -143405 | 23 | 19 | 92.1234 | 11062.6
1611 | 140557 | -154015 | 23 | 19 | 92.0448 | 11065.4
1612 | 139316 | -161581 | 23 | 20 | 91.954 | 11067.8
1613 | 141541 | -169637 | 23 | 20 | 95.827 | 12301.9
1614 | 188564 | -145117 | 23 | 20 | 135.534 | 29989.2
1615 | 320277 | -889667 | 25 | 21 | 284.973 | 89031.8
1616 | 382167 | -776584 | 26 | 23 | 296.357 | 108149
1617 | 400991 | -594062 | 28 | 24 | 289.806 | 149732
1618 | 399366 | -474186 | 32 | 27 | 264.792 | 176202
1619 | 391151 | -418400 | 35 | 30 | 257.029 | 179977
1620 | 387263 | -333423 | 39 | 32 | 242.774 | 179975
1621 | 374554 | -291750 | 41 | 34 | 240.729 | 179973
1622 | 436926 | -252936 | 43 | 36 | 261.934 | 179970
1623 | 464379 | -224175 | 45 | 37 | 271.026 | 177641
1624 | 452277 | -209984 | 45 | 38 | 271.362 | 161478
1625 | 460304 | -233374 | 45 | 38 | 267.629 | 131781
1626 | 424799 | -262693 | 45 | 38 | 249.402 | 98787.4
1627 | 346748 | -336745 | 44 | 37 | 182.77 | 61105.9
1628 | 183462 | 0 | 44 | 37 | 121.779 | 43676.8
1629 | 162783 | -8258.99 | 43 | 37 | 109.809 | 38748.9
1630 | 149485 | -12614.7 | 42 | 37 | 99.2908 | 23726
1631 | 138384 | -13884.7 | 42 | 37 | 90.801 | 12700.5
1632 | 160497 | -18007.9 | 41 | 36 | 93.8071 | 11033.6
1633 | 154795 | -20130.2 | 39 | 36 | 92.9219 | 11036.4
1634 | 151907 | -27012.3 | 36 | 35 | 93.1009 | 11039.2
1635 | 149155 | -36202 | 34 | 34 | 93.2331 | 11041.8
1636 | 147175 | -41950.2 | 35 | 34 | 93.3275 | 11044
1637 | 149112 | -50344.1 | 35 | 34 | 97.0472 | 12278.3
1638 | 196937 | -40233.2 | 36 | 35 | 137.141 | 29965.6
1639 | 323686 | -479981 | 38 | 36 | 257.699 | 89008.4
1640 | 415091 | -446142 | 40 | 38 | 262.589 | 108125
1641 | 438858 | -308537 | 42 | 40 | 268.355 | 149716
1642 | 463234 | -259592 | 45 | 42 | 270.309 | 176185
1643 | 439737 | -222705 | 47 | 43 | 260.836 | 179959
1644 | 434975 | -184743 | 50 | 45 | 248.008 | 179956
1645 | 402006 | -153917 | 51 | 46 | 245.411 | 179954
1646 | 462729 | -122046 | 53 | 47 | 268.033 | 179951
1647 | 499975 | -92702.9 | 54 | 48 | 275.886 | 177622
1648 | 490083 | -79658.6 | 53 | 47 | 273.115 | 161459
1649 | 464630 | -92054.8 | 51 | 47 | 267.019 | 131762
1650 | 414824 | -119184 | 50 | 46 | 248.113 | 98769
1651 | 340876 | -229783 | 45 | 43 | 182.985 | 61088.1
1652 | 184075 | 0 | 41 | 39 | 117.645 | 43659.9
1653 | 164863 | -7691.33 | 36 | 36 | 111.185 | 38732.8
1654 | 151271 | 0 | 36 | 35 | 91.7282 | 23707.8
1655 | 140208 | -11660.7 | 35 | 35 | 90.6977 | 12681.6
1656 | 153325 | -9853.66 | 35 | 35 | 89.7399 | 11014.4
1657 | 160587 | -16912.3 | 35 | 34 | 88.6289 | 11016.7
1658 | 156632 | -23957.8 | 34 | 33 | 88.5397 | 11019.3
1659 | 153734 | -29321 | 34 | 32 | 89.0614 | 11022.8
1660 | 151236 | -37153.6 | 32 | 31 | 89.2417 | 11026
1661 | 149040 | -44279.1 | 31 | 29 | 89.4097 | 11028.8
1662 | 146985 | -55140 | 29 | 27 | 87.9699 | 11031.7
1663 | 145507 | -63287 | 30 | 29 | 85.1675 | 11034.4
1664 | 127244 | -696299 | 31 | 30 | 132.744 | 11037.1
1665 | 144493 | -642821 | 32 | 30 | 131.553 | 11039.5
1666 | 139269 | -526294 | 34 | 32 | 122.557 | 11037.7
1667 | 133602 | -441112 | 35 | 33 | 98.0125 | 11034.9
1668 | 143843 | -393808 | 37 | 33 | 94.8005 | 11034.7
1669 | 155500 | -374261 | 38 | 34 | 93.4654 | 11034.5
1670 | 170744 | -360837 | 40 | 35 | 92.5145 | 11034.5
1671 | 127300 | -9771.08 | 41 | 36 | 76.4638 | 11034.5
1672 | 123236 | -9666.15 | 40 | 35 | 74.4277 | 11034.7
1673 | 122945 | -13799 | 39 | 35 | 75.8431 | 11036.4
1674 | 135585 | -19709.2 | 38 | 34 | 83.1714 | 11037.7
1675 | 149098 | -24993.6 | 37 | 33 | 91.7089 | 11039.2
1676 | 144756 | -29577.4 | 35 | 31 | 93.3584 | 11041.4
1677 | 142090 | -36234.9 | 34 | 30 | 93.5516 | 11044.1
1678 | 140193 | -46660.8 | 32 | 29 | 93.533 | 11046.4
1679 | 138576 | -57976 | 31 | 27 | 92.5322 | 11048.8
1680 | 137079 | -70006.6 | 29 | 25 | 91.556 | 11051.2
1681 | 135606 | -83329.1 | 28 | 25 | 86.8779 | 4098.82
1682 | 134557 | -99631.7 | 28 | 25 | 86.7308 | 4101.12
1683 | 133672 | -108589 | 27 | 25 | 86.6365 | 4103.58
1684 | 132875 | -119932 | 26 | 25 | 86.5405 | 4105.91
1685 | 132169 | -128363 | 26 | 24 | 85.2504 | 4108.2
1686 | 131459 | -137458 | 25 | 24 | 82.7748 | 4110.4
1687 | 130894 | -140196 | 26 | 25 | 81.4446 | 4112.6
1688 | 131177 | -141537 | 26 | 25 | 81.229 | 4114.75
1689 | 130176 | -128145 | 27 | 26 | 81.2189 | 4116.85
1690 | 130774 | -124418 | 28 | 27 | 81.216 | 4118.88
1691 | 129886 | -108053 | 30 | 28 | 80.8685 | 4120.78
1692 | 131194 | -104143 | 31 | 29 | 81.0539 | 4122.49
1693 | 129605 | -96744.4 | 32 | 30 | 81.0023 | 4124.17
1694 | 130506 | -94517.4 | 33 | 31 | 81.1025 | 4125.66
1695 | 129246 | -89939.7 | 34 | 31 | 81.1392 | 4127.14
1696 | 129102 | -92710.1 | 34 | 32 | 81.2839 | 4128.55
1697 | 128691 | -99493.5 | 34 | 32 | 83.5801 | 4129.92
1698 | 128719 | -111797 | 34 | 32 | 88.2 | 4131.24
1699 | 127844 | -120063 | 33 | 32 | 90.3558 | 4132.55
1700 | 127681 | -124942 | 33 | 32 | 90.3432 | 4133.93
1701 | 128992 | -129424 | 32 | 32 | 90.4881 | 4135.29
1702 | 127072 | -126472 | 32 | 32 | 89.6475 | 4136.65
1703 | 126883 | -125144 | 32 | 32 | 88.7864 | 4137.92
1704 | 126999 | -132936 | 32 | 32 | 91.6622 | 11093.7
1705 | 126907 | -136091 | 32 | 32 | 91.6149 | 11094.6
1706 | 126810 | -148803 | 32 | 32 | 91.5665 | 11095
1707 | 126596 | -152133 | 32 | 31 | 91.5371 | 11095.9
1708 | 129855 | -156277 | 32 | 31 | 95.3712 | 12328.8
1709 | 177494 | -127772 | 31 | 30 | 135.236 | 30015
1710 | 311721 | -848656 | 31 | 29 | 283.994 | 89056.7
1711 | 374270 | -738843 | 31 | 29 | 307.251 | 108173
1712 | 393141 | -614671 | 31 | 29 | 295.338 | 149750
1713 | 391662 | -577622 | 31 | 29 | 289.464 | 176219
1714 | 382404 | -562787 | 32 | 30 | 281.835 | 179993
1715 | 366469 | -500573 | 33 | 30 | 263.6 | 179991
1716 | 348209 | -470504 | 34 | 30 | 260.228 | 179989
1717 | 381950 | -402767 | 35 | 31 | 257.367 | 179986
1718 | 400419 | -367231 | 35 | 32 | 264.114 | 177657
1719 | 403555 | -357211 | 36 | 32 | 265.538 | 161495
1720 | 398288 | -396179 | 35 | 32 | 261.165 | 131800
1721 | 384654 | -464911 | 34 | 31 | 243.705 | 98806
1722 | 294234 | -504151 | 33 | 31 | 204.777 | 61124.9
1723 | 176786 | -11414.4 | 33 | 31 | 126.561 | 43695.8
1724 | 157852 | -17968.8 | 32 | 30 | 111.736 | 38768.3
1725 | 168787 | -30712.6 | 32 | 30 | 107.031 | 23745.6
1726 | 152967 | -44007 | 31 | 29 | 97.8187 | 12721.4
1727 | 146195 | -60486.7 | 31 | 29 | 93.7822 | 11055.4
1728 | 143206 | -70485.1 | 30 | 28 | 92.4545 | 11059.1
1729 | 141544 | -88885.7 | 29 | 27 | 92.2799 | 11061.9
1730 | 140187 | -105101 | 27 | 26 | 92.1384 | 11064.6
1731 | 139053 | -118510 | 26 | 25 | 92.0082 | 11066.9
1732 | 141493 | -127542 | 27 | 26 | 96.179 | 12300.9
1733 | 188947 | -104494 | 28 | 27 | 136.055 | 29988.1
1734 | 319782 | -768723 | 29 | 27 | 278.165 | 89030.6
1735 | 381964 | -680926 | 30 | 28 | 304.318 | 108147
1736 | 400592 | -573175 | 30 | 29 | 293.842 | 149733
1737 | 398675 | -535378 | 31 | 29 | 287.592 | 176203
1738 | 389223 | -519968 | 32 | 30 | 279.271 | 179978
1739 | 374854 | -464515 | 33 | 30 | 242.371 | 179976
1740 | 353949 | -439281 | 34 | 30 | 239.402 | 179975
1741 | 387407 | -359492 | 34 | 30 | 256.937 | 179971
1742 | 405735 | -331895 | 35 | 30 | 264.478 | 177643
1743 | 408500 | -320647 | 35 | 30 | 265.874 | 161481
1744 | 404001 | -334443 | 35 | 30 | 261.153 | 131785
1745 | 388603 | -387410 | 35 | 30 | 241.265 | 98792.2
1746 | 302526 | -430896 | 35 | 30 | 194.45 | 61111.2
1747 | 180984 | -11106.4 | 32 | 29 | 126.813 | 43682.1
1748 | 161775 | -15371.9 | 30 | 28 | 111.371 | 38754.4
1749 | 175187 | -23397.3 | 27 | 26 | 107.479 | 23731.8
1750 | 158208 | -43708.4 | 26 | 25 | 98.2148 | 12707.3
1751 | 150981 | -62668.6 | 26 | 25 | 94.1378 | 11041.5
1752 | 147504 | -73858.9 | 25 | 24 | 93.1677 | 11045.7
1753 | 145565 | -90372.9 | 26 | 25 | 92.9703 | 11048.8
1754 | 144102 | -100517 | 27 | 26 | 92.7996 | 11051.8
1755 | 142792 | -108453 | 28 | 26 | 92.6662 | 11054.4
1756 | 144969 | -119181 | 27 | 26 | 96.4153 | 12288.7
1757 | 192328 | -102615 | 27 | 25 | 136.241 | 29976.1
1758 | 322180 | -801312 | 26 | 25 | 279.406 | 89018.8
1759 | 383666 | -719831 | 27 | 25 | 305.292 | 108136
1760 | 402252 | -609237 | 27 | 24 | 290.939 | 149723
1761 | 400144 | -537782 | 28 | 24 | 286.503 | 176194
1762 | 389390 | -496877 | 30 | 26 | 277.124 | 179970
1763 | 375693 | -413255 | 33 | 28 | 242.204 | 179969
1764 | 355643 | -357740 | 35 | 29 | 239.798 | 179967
1765 | 388942 | -306749 | 35 | 29 | 257.516 | 179964
1766 | 407099 | -288108 | 35 | 29 | 264.639 | 177636
1767 | 411875 | -291837 | 35 | 28 | 272.707 | 161475
1768 | 405804 | -336056 | 33 | 28 | 261.289 | 131779
1769 | 387865 | -406727 | 32 | 27 | 241.859 | 98786.3
1770 | 303388 | -471363 | 30 | 25 | 197.577 | 61105.9
1771 | 181663 | -14037 | 28 | 24 | 127.946 | 43677.3
1772 | 162528 | -20303.2 | 26 | 23 | 112.623 | 38749.4
1773 | 175419 | -36084.4 | 24 | 21 | 107.288 | 23726.4
1774 | 158853 | -54144.4 | 23 | 21 | 98.0279 | 12702.3
1775 | 151613 | -72390.9 | 23 | 20 | 93.9688 | 11036.7
1776 | 148296 | -85753.5 | 22 | 20 | 93.0212 | 11041
1777 | 152359 | -97883.7 | 22 | 20 | 93.4949 | 11044.5
1778 | 144617 | -96249.5 | 22 | 20 | 92.8814 | 11047.5
1779 | 144240 | -120167 | 22 | 20 | 92.6552 | 11050
1780 | 145261 | -132305 | 22 | 20 | 96.3712 | 12283.9
1781 | 196176 | -122046 | 21 | 20 | 136.348 | 29971.4
1782 | 322136 | -862045 | 21 | 20 | 282.662 | 89014.2
1783 | 383803 | -778476 | 23 | 22 | 306.727 | 108132
1784 | 402686 | -645230 | 25 | 23 | 293.627 | 149719
1785 | 400585 | -571915 | 27 | 25 | 288.967 | 176191
1786 | 388343 | -526221 | 30 | 27 | 278.98 | 179966
1787 | 376278 | -431194 | 33 | 29 | 242.351 | 179965
1788 | 355776 | -402436 | 36 | 31 | 239.832 | 179964
1789 | 388826 | -392260 | 33 | 29 | 257.616 | 179961
1790 | 406973 | -414859 | 30 | 27 | 283.786 | 177633
1791 | 409621 | -458237 | 27 | 24 | 285.086 | 161472
1792 | 402822 | -502524 | 26 | 23 | 280.817 | 131777
1793 | 396714 | -602067 | 24 | 21 | 248.982 | 98785.5
1794 | 311297 | -644076 | 23 | 20 | 189.733 | 61105.6
1795 | 181100 | -17545.4 | 22 | 19 | 127.59 | 43677.5
1796 | 189295 | -37090.5 | 20 | 17 | 118.739 | 38749.6
1797 | 169819 | -61336.6 | 19 | 16 | 106.515 | 23726.5
1798 | 155320 | -95017.5 | 18 | 15 | 97.3713 | 12703.8
1799 | 148701 | -130054 | 17 | 14 | 93.3764 | 11038.4
1800 | 145954 | -147894 | 16 | 13 | 92.4705 | 11042.9
1801 | 144235 | -169769 | 15 | 12 | 92.3203 | 11046.7
1802 | 142690 | -186909 | 13 | 11 | 92.1674 | 11049.9
1803 | 141305 | -203881 | 12 | 10 | 95.1773 | 11052.9
1804 | 143028 | -220012 | 11 | 9 | 100.614 | 12287.6
1805 | 189429 | -207619 | 9 | 7 | 135.311 | 29975.4
1806 | 319862 | -1127670 | 8 | 6 | 297.924 | 89018.7
1807 | 381988 | -1034670 | 10 | 7 | 318.437 | 108136
1808 | 401184 | -879838 | 11 | 9 | 305.612 | 149722
1809 | 398874 | -799802 | 13 | 10 | 299.945 | 176194
1810 | 380343 | -767673 | 15 | 12 | 289.947 | 179970
1811 | 364517 | -646144 | 18 | 14 | 251.702 | 179970
1812 | 353692 | -604124 | 20 | 16 | 248.611 | 179968
1813 | 386780 | -536100 | 21 | 16 | 259.919 | 179965
1814 | 405424 | -514640 | 21 | 17 | 264.9 | 177639
1815 | 408221 | -510347 | 22 | 17 | 265.941 | 161478
1816 | 400719 | -554084 | 21 | 17 | 264.094 | 131784
1817 | 391110 | -634406 | 20 | 16 | 268.965 | 98792.6
1818 | 311319 | -671354 | 19 | 15 | 209.575 | 61112.9
1819 | 179663 | -19723.4 | 17 | 14 | 127.099 | 43684.2
1820 | 186314 | -44107.5 | 16 | 13 | 118.202 | 38755.8
1821 | 167411 | -85138.2 | 14 | 12 | 106.114 | 23732.8
1822 | 152933 | -119429 | 13 | 11 | 97.061 | 12710.2
1823 | 147833 | -147819 | 11 | 10 | 93.2113 | 11044.8
1824 | 143592 | -166091 | 10 | 9 | 88.252 | 11049.2
1825 | 150807 | -187698 | 9 | 8 | 88.9701 | 11052.8
1826 | 140354 | -175550 | 9 | 8 | 88.4249 | 11056.4
1827 | 143073 | -192889 | 8 | 7 | 88.6713 | 11059.3
1828 | 137860 | -196234 | 7 | 6 | 91.9395 | 11061.3
1829 | 138868 | -213376 | 6 | 5 | 92.3581 | 11063.3
1830 | 135576 | -216439 | 5 | 4 | 90.62 | 11065.2
1831 | 123064 | -1129870 | 8 | 7 | 165.801 | 11066.9
1832 | 122394 | -977010 | 12 | 10 | 156.889 | 11068.3
1833 | 121785 | -833507 | 15 | 13 | 145.956 | 11057.4
1834 | 121321 | -742778 | 18 | 15 | 138.938 | 11053.3
1835 | 120869 | -664053 | 22 | 18 | 132.333 | 11051.6
1836 | 120470 | -610711 | 25 | 20 | 109.012 | 11050.5
1837 | 120158 | -559000 | 27 | 22 | 105.404 | 11049.9
1838 | 119899 | -18469.9 | 30 | 23 | 76.7745 | 11049.5
1839 | 148297 | -35649.2 | 32 | 25 | 83.4211 | 11049.4
1840 | 144484 | -39852.2 | 32 | 25 | 83.1958 | 11053.6
1841 | 140112 | -42784.2 | 31 | 25 | 84.8734 | 11056.5
1842 | 137112 | -52191.6 | 31 | 24 | 90.4832 | 11059.4
1843 | 135010 | -72587.9 | 31 | 25 | 92.9336 | 11061.9
1844 | 133380 | -85657.8 | 31 | 25 | 92.8191 | 11064.4
1845 | 132122 | -95476.3 | 31 | 25 | 92.7212 | 11066.7
1846 | 131576 | -104472 | 31 | 25 | 91.8808 | 11068.9
1847 | 130768 | -112733 | 31 | 25 | 91.0142 | 11071
1848 | 129976 | -122897 | 31 | 25 | 86.4315 | 4118.3
1849 | 129599 | -129544 | 31 | 25 | 86.3768 | 4120.11
1850 | 129134 | -136504 | 30 | 26 | 86.3321 | 4122.07
1851 | 128640 | -142104 | 30 | 25 | 86.2702 | 4123.87
1852 | 128456 | -150475 | 30 | 25 | 86.2376 | 4125.63
1853 | 127912 | -155501 | 30 | 25 | 84.9945 | 4127.33
1854 | 127539 | -160829 | 30 | 25 | 82.5588 | 4129.04
1855 | 127394 | -160904 | 31 | 26 | 81.1894 | 4130.69
1856 | 127811 | -150892 | 33 | 28 | 81.022 | 4132.3
1857 | 127240 | -138544 | 34 | 28 | 81.3084 | 4133.87
1858 | 127022 | -121553 | 34 | 29 | 80.9655 | 4135.38
1859 | 127382 | -104552 | 35 | 29 | 80.7431 | 4136.79
1860 | 127537 | -102147 | 35 | 29 | 80.8827 | 4138.08
1861 | 127026 | -97143.3 | 35 | 29 | 80.8045 | 4139.28
1862 | 127147 | -95648.6 | 35 | 30 | 80.8431 | 4140.35
1863 | 126714 | -98360.5 | 35 | 29 | 80.9453 | 4141.48
1864 | 126560 | -103289 | 35 | 30 | 81.0715 | 4142.57
1865 | 126346 | -115224 | 35 | 30 | 83.3824 | 4143.67
1866 | 126074 | -127647 | 35 | 30 | 87.9042 | 4144.79
1867 | 126089 | -137586 | 35 | 30 | 90.211 | 4145.92
1868 | 125753 | -143066 | 35 | 30 | 90.189 | 4147.05
1869 | 125558 | -148130 | 35 | 30 | 90.1623 | 4148.15
1870 | 125573 | -152875 | 34 | 31 | 89.3549 | 4149.22
1871 | 125295 | -160123 | 32 | 31 | 88.5164 | 4150.3
1872 | 125416 | -165289 | 31 | 31 | 91.4552 | 11106
1873 | 125408 | -170979 | 31 | 31 | 91.4272 | 11107.1
1874 | 125249 | -174032 | 31 | 31 | 93.6328 | 11107.4
1875 | 125442 | -177203 | 31 | 31 | 94.0262 | 11108.2
1876 | 128388 | -177502 | 31 | 31 | 95.2669 | 12340.9
1877 | 176062 | -140099 | 32 | 31 | 135.124 | 30026.9
1878 | 311192 | -874855 | 32 | 31 | 286.528 | 89068.3
1879 | 373828 | -756634 | 32 | 32 | 307.789 | 108184
1880 | 392737 | -612663 | 33 | 32 | 291.598 | 149758
1881 | 391399 | -564195 | 33 | 33 | 288.68 | 176227
1882 | 382508 | -557580 | 33 | 33 | 281.45 | 180000
1883 | 365459 | -489785 | 34 | 33 | 262.825 | 179998
1884 | 348072 | -467611 | 34 | 34 | 259.92 | 179996
1885 | 381396 | -409966 | 34 | 34 | 256.874 | 179993
1886 | 399978 | -391074 | 34 | 34 | 264.256 | 177665
1887 | 403114 | -394467 | 34 | 34 | 265.749 | 161502
1888 | 396958 | -419657 | 34 | 33 | 261.558 | 131807
1889 | 383970 | -486192 | 33 | 33 | 262.986 | 98813.8
1890 | 293718 | -516515 | 33 | 33 | 204.014 | 61132.5
1891 | 176465 | -10991.7 | 33 | 33 | 126.31 | 43703.4
1892 | 157539 | -17192 | 33 | 33 | 111.518 | 38775.6
1893 | 168030 | -29747.2 | 33 | 33 | 106.958 | 23752.8
1894 | 152026 | -44575.6 | 33 | 32 | 97.767 | 12728.5
1895 | 145383 | -60083.8 | 33 | 32 | 93.757 | 11062.3
1896 | 142447 | -68399.3 | 33 | 32 | 92.4131 | 11065.9
1897 | 140915 | -81332.8 | 33 | 32 | 92.2621 | 11068.6
1898 | 139730 | -92343.5 | 33 | 32 | 92.1501 | 11071.1
1899 | 138788 | -101962 | 33 | 32 | 92.0659 | 11073.2
1900 | 141358 | -108759 | 33 | 32 | 96.281 | 12307.1
1901 | 189000 | -89114.9 | 33 | 32 | 136.176 | 29994
1902 | 320012 | -704615 | 33 | 31 | 274.801 | 89036.3
1903 | 382212 | -630125 | 34 | 32 | 298.656 | 108153
1904 | 400825 | -521558 | 34 | 32 | 289.352 | 149738
1905 | 398839 | -459543 | 35 | 32 | 264.134 | 176207
1906 | 388732 | -432292 | 36 | 33 | 256.135 | 179982
1907 | 372843 | -375505 | 36 | 33 | 241.091 | 179980
1908 | 354375 | -376571 | 37 | 33 | 239.129 | 179978
1909 | 387938 | -332670 | 37 | 33 | 257.126 | 179974
1910 | 413799 | -338551 | 37 | 33 | 265.552 | 177645
1911 | 412976 | -338406 | 37 | 33 | 266.698 | 161483
1912 | 403874 | -371834 | 36 | 33 | 262.272 | 131788
1913 | 386671 | -418302 | 36 | 33 | 242.878 | 98794.4
1914 | 307992 | -470885 | 35 | 32 | 200.536 | 61113.5
1915 | 181051 | -10013.7 | 33 | 31 | 126.333 | 43684.4
1916 | 161818 | -15113.6 | 31 | 29 | 111.344 | 38757.2
1917 | 175034 | -22690.8 | 29 | 27 | 107.336 | 23734.5
1918 | 158168 | -39648.3 | 28 | 27 | 98.1946 | 12710.1
1919 | 150821 | -64179.1 | 26 | 25 | 94.0967 | 11044.3
1920 | 147380 | -74490.5 | 25 | 24 | 93.218 | 11048.4
1921 | 150988 | -90756.9 | 25 | 24 | 93.6268 | 11051.6
1922 | 143812 | -90594.7 | 24 | 24 | 92.7548 | 11054.6
1923 | 142918 | -117297 | 24 | 24 | 92.7761 | 11057
1924 | 144623 | -128660 | 24 | 24 | 96.4211 | 12290.8
1925 | 191802 | -115709 | 24 | 24 | 136.128 | 29978.2
1926 | 321931 | -832811 | 24 | 23 | 281.467 | 89020.9
1927 | 383780 | -741774 | 26 | 25 | 303.182 | 108138
1928 | 402581 | -605416 | 28 | 27 | 290.803 | 149726
1929 | 400509 | -556942 | 30 | 28 | 289.271 | 176197
1930 | 387217 | -498264 | 33 | 31 | 276.874 | 179972
1931 | 371056 | -372207 | 37 | 34 | 241.41 | 179970
1932 | 366146 | -300003 | 40 | 36 | 240.01 | 179968
1933 | 425682 | -264080 | 42 | 38 | 260.691 | 179965
1934 | 470163 | -238055 | 45 | 40 | 271.235 | 177637
1935 | 455366 | -202047 | 47 | 41 | 272.229 | 161474
1936 | 463642 | -215085 | 46 | 41 | 268.187 | 131777
1937 | 433498 | -252948 | 45 | 41 | 245.043 | 98783.2
1938 | 349171 | -326976 | 44 | 40 | 174.324 | 61101.8
1939 | 182863 | 0 | 41 | 38 | 117.349 | 43672.6
1940 | 163465 | -12964.9 | 38 | 36 | 112.492 | 38744.9
1941 | 150009 | -9244.72 | 35 | 33 | 96.246 | 23721.8
1942 | 167644 | -17863.4 | 34 | 33 | 97.7116 | 12696.3
1943 | 157743 | -22817.4 | 34 | 32 | 93.5394 | 11029.8
1944 | 155332 | -29953.6 | 33 | 31 | 93.0944 | 11033.3
1945 | 151168 | -35042.7 | 31 | 30 | 92.5867 | 11036.6
1946 | 148949 | -40039.2 | 30 | 29 | 91.8926 | 11039.2
1947 | 147421 | -47154.7 | 28 | 28 | 91.8822 | 11041.6
1948 | 148579 | -57186.8 | 27 | 27 | 95.658 | 12275.4
1949 | 195767 | -52980.6 | 25 | 25 | 135.097 | 29962.4
1950 | 322908 | -690666 | 24 | 24 | 272.629 | 89004.8
1951 | 385270 | -612604 | 27 | 27 | 293.78 | 108121
1952 | 404056 | -454311 | 31 | 30 | 265.364 | 149714
1953 | 401929 | -386521 | 34 | 32 | 264.511 | 176184
1954 | 417214 | -345687 | 38 | 34 | 258.096 | 179958
1955 | 423627 | -288550 | 41 | 36 | 244.41 | 179956
1956 | 406988 | -235921 | 45 | 38 | 243.383 | 179953
1957 | 460264 | -220555 | 45 | 38 | 264.426 | 179950
1958 | 482846 | -216019 | 45 | 38 | 272.741 | 177622
1959 | 470354 | -209056 | 45 | 38 | 273.581 | 161460
1960 | 474604 | -244907 | 44 | 38 | 269.583 | 131763
1961 | 426923 | -275091 | 43 | 37 | 245.144 | 98770.6
1962 | 344366 | -343538 | 42 | 37 | 177.573 | 61090.3
1963 | 183862 | 0 | 41 | 36 | 117.588 | 43661.9
1964 | 164455 | -11673.4 | 40 | 36 | 112.124 | 38734.1
1965 | 150977 | 0 | 39 | 35 | 91.7146 | 23710
1966 | 139890 | -20284.9 | 39 | 36 | 92.4954 | 12684.3
1967 | 164075 | -12222 | 40 | 36 | 89.9337 | 11017.5
1968 | 160743 | -20403.5 | 40 | 36 | 93.0659 | 11020.4
1969 | 155996 | -19416.7 | 40 | 36 | 92.0596 | 11023.4
1970 | 153921 | -23391.3 | 39 | 36 | 92.5862 | 11026.2
1971 | 151684 | -26673.6 | 39 | 36 | 92.3383 | 11028.5
1972 | 153620 | -29599.2 | 40 | 37 | 96.4593 | 12262.7
1973 | 201640 | -26195.5 | 40 | 37 | 136.033 | 29949.9
1974 | 325087 | -419107 | 41 | 37 | 240.191 | 88992.7
1975 | 430089 | -429077 | 42 | 38 | 270.934 | 108110
1976 | 452491 | -329093 | 43 | 39 | 269.705 | 149702
1977 | 460547 | -274589 | 44 | 40 | 269.834 | 176173
1978 | 441976 | -231628 | 46 | 41 | 260.61 | 179948
1979 | 430640 | -191817 | 49 | 43 | 247.06 | 179946
1980 | 400220 | -147824 | 51 | 45 | 244.985 | 179944
1981 | 449869 | -125793 | 52 | 45 | 266.419 | 179941
1982 | 480176 | -107371 | 52 | 46 | 274.949 | 177613
1983 | 467724 | -77544.8 | 53 | 46 | 272.295 | 161451
1984 | 467641 | -82986.1 | 52 | 46 | 266.94 | 131755
1985 | 418863 | -103161 | 51 | 47 | 243.08 | 98762
1986 | 327719 | -175452 | 50 | 46 | 174.708 | 61081.5
1987 | 185722 | 0 | 49 | 46 | 117.525 | 43653.4
1988 | 166072 | 0 | 49 | 46 | 103.055 | 38726.4
1989 | 152678 | -8036.54 | 48 | 46 | 99.3657 | 23700.3
1990 | 141474 | 0 | 48 | 46 | 83.2902 | 12673.6
1991 | 136622 | -11879 | 49 | 46 | 87.7024 | 11005.9
1992 | 134964 | 0 | 49 | 47 | 74.9838 | 11008.2
1993 | 133879 | -12819.7 | 49 | 47 | 82.9 | 11010
1994 | 132840 | 0 | 50 | 46 | 74.887 | 11012.4
1995 | 150477 | -14382.6 | 50 | 46 | 86.1569 | 11014
1996 | 131357 | 0 | 48 | 44 | 74.8335 | 11015.7
1997 | 161250 | -16584.4 | 45 | 43 | 88.3144 | 11017.2
1998 | 156557 | -9510.42 | 43 | 41 | 81.3337 | 11018.7
1999 | 136130 | -443124 | 43 | 41 | 117.736 | 11020.6
2000 | 198538 | -453633 | 42 | 41 | 118.495 | 11022.8
2001 | 185681 | -401522 | 42 | 41 | 115.63 | 11024.7
2002 | 194077 | -386651 | 42 | 41 | 94.6751 | 11022.9
2003 | 187048 | -379594 | 41 | 41 | 94.0426 | 11023.8
2004 | 183207 | -362340 | 41 | 40 | 92.9115 | 11024.2
2005 | 184011 | -366120 | 41 | 41 | 93.2972 | 11024.9
2006 | 125120 | 0 | 42 | 41 | 69.3169 | 11025.6
2007 | 124949 | -13233.3 | 42 | 42 | 78.0337 | 11026.5
2008 | 124418 | 0 | 41 | 41 | 69.4355 | 11027
2009 | 124111 | -19505.6 | 41 | 41 | 80.5249 | 11028.8
2010 | 153145 | -13846.9 | 40 | 40 | 87.2989 | 11030.2
2011 | 150618 | -21154.4 | 39 | 39 | 93.0264 | 11031.7
2012 | 146631 | -21911.8 | 39 | 39 | 92.2842 | 11033.8
2013 | 144762 | -26273.5 | 38 | 38 | 92.8125 | 11036.2
2014 | 142946 | -28386.3 | 38 | 38 | 91.832 | 11038.3
2015 | 141548 | -31106.6 | 38 | 38 | 91.2837 | 11040.4
2016 | 140008 | -33221.7 | 38 | 38 | 86.6701 | 4087.82
2017 | 138850 | -43066.1 | 38 | 37 | 86.8384 | 4089.88
2018 | 138091 | -49683.8 | 37 | 37 | 86.8288 | 4092.06
2019 | 137283 | -54019.5 | 37 | 37 | 86.7025 | 4094.1
2020 | 139917 | -57982.4 | 37 | 37 | 86.9835 | 4096.08
2021 | 136050 | -54426.2 | 37 | 37 | 84.7098 | 4097.94
2022 | 136485 | -58479.3 | 37 | 37 | 82.3875 | 4099.7
2023 | 135066 | -55128.3 | 38 | 38 | 80.4265 | 4101.15
2024 | 134692 | -51937.3 | 38 | 38 | 79.8449 | 4102.57
2025 | 134485 | -50635 | 39 | 39 | 80.8166 | 4103.93
2026 | 134292 | -42575.2 | 39 | 38 | 80.5573 | 4105.2
2027 | 134571 | -37559.6 | 38 | 38 | 80.2897 | 4106.64
2028 | 134284 | -41853.1 | 38 | 38 | 80.6277 | 4108.18
2029 | 134084 | -37482.5 | 38 | 38 | 80.3557 | 4109.4
2030 | 134080 | -37633.1 | 38 | 38 | 80.4191 | 4110.66
2031 | 133404 | -46356.2 | 38 | 38 | 81.0403 | 4112.19
2032 | 132598 | -46405.9 | 38 | 37 | 80.8002 | 4113.36
2033 | 132263 | -54546 | 38 | 37 | 83.2572 | 4114.76
2034 | 131980 | -67622.4 | 38 | 38 | 87.893 | 4116.37
2035 | 131137 | -78324.7 | 38 | 37 | 90.2701 | 4117.73
2036 | 130820 | -87604.5 | 37 | 37 | 90.418 | 4119.3
2037 | 130373 | -94280.7 | 37 | 37 | 90.5751 | 4120.74
2038 | 130027 | -99096.9 | 37 | 37 | 89.8608 | 4122.19
2039 | 129644 | -104654 | 36 | 36 | 89.0178 | 4123.66
2040 | 129732 | -104784 | 36 | 36 | 91.9645 | 11079.8
2041 | 130057 | -108310 | 36 | 36 | 91.969 | 11081.2
2042 | 129461 | -112445 | 35 | 35 | 91.9322 | 11081.8
2043 | 129273 | -115256 | 35 | 35 | 91.8997 | 11082.9
2044 | 132521 | -117797 | 35 | 35 | 95.7316 | 12315.9
2045 | 180541 | -92894.5 | 35 | 35 | 135.751 | 30002.1
2046 | 313195 | -710803 | 35 | 35 | 275.076 | 89043.9
2047 | 382304 | -628808 | 36 | 36 | 297.497 | 108160
2048 | 414180 | -497567 | 38 | 37 | 266.902 | 149741
2049 | 422232 | -447423 | 39 | 38 | 266.764 | 176210
2050 | 417905 | -411086 | 41 | 39 | 258.674 | 179983
2051 | 412880 | -369573 | 42 | 40 | 243.981 | 179981
2052 | 392719 | -328811 | 44 | 41 | 242.073 | 179978
2053 | 447308 | -265233 | 45 | 42 | 263.27 | 179974
2054 | 462495 | -244385 | 47 | 43 | 271.753 | 177645
2055 | 452144 | -209257 | 48 | 43 | 272.47 | 161482
2056 | 460342 | -251072 | 47 | 43 | 269.357 | 131785
2057 | 426934 | -274566 | 47 | 43 | 246.677 | 98791.1
2058 | 351789 | -344634 | 46 | 42 | 178.477 | 61109.3
2059 | 179005 | 0 | 44 | 41 | 117.292 | 43679.8
2060 | 159883 | -9439.55 | 41 | 40 | 111.002 | 38751.9
2061 | 146402 | 0 | 39 | 38 | 91.5059 | 23729.7
2062 | 151564 | -20239.9 | 39 | 38 | 95.4645 | 12704.1
2063 | 155035 | -13892.9 | 38 | 38 | 89.5354 | 11037.4
2064 | 154937 | -23197.2 | 38 | 38 | 92.2385 | 11040.3
2065 | 148862 | -23383.4 | 38 | 37 | 90.9997 | 11043.2
2066 | 147876 | -26128 | 38 | 37 | 90.6106 | 11045.8
2067 | 145776 | -28283.7 | 38 | 38 | 90.4565 | 11047.7
2068 | 147735 | -30822.1 | 38 | 37 | 94.599 | 12281.3
2069 | 195947 | -23468.4 | 38 | 37 | 133.996 | 29967.9
2070 | 322464 | -453286 | 38 | 38 | 260.798 | 89009.9
2071 | 417396 | -464018 | 39 | 38 | 272.028 | 108126
2072 | 448561 | -376232 | 41 | 39 | 272.105 | 149718
2073 | 452951 | -351686 | 42 | 40 | 269.868 | 176186
2074 | 441152 | -300938 | 45 | 42 | 260.274 | 179959
2075 | 426199 | -225203 | 49 | 44 | 246.753 | 179957
2076 | 394730 | -157119 | 52 | 46 | 244.74 | 179955
2077 | 436486 | -125610 | 53 | 46 | 265.56 | 179952
2078 | 462146 | -100837 | 54 | 47 | 271.405 | 177623
2079 | 465139 | -76368.4 | 55 | 47 | 271.616 | 161461
2080 | 461171 | -85872.9 | 53 | 46 | 265.232 | 131764
2081 | 422771 | -110109 | 52 | 45 | 242.788 | 98770.7
2082 | 324086 | -183557 | 50 | 44 | 174.275 | 61089.7
2083 | 184164 | 0 | 46 | 42 | 117.255 | 43661.2
2084 | 164615 | 0 | 43 | 40 | 102.988 | 38733.9
2085 | 151075 | -8457.44 | 39 | 37 | 99.4335 | 23709.1
2086 | 140059 | 0 | 38 | 37 | 83.2257 | 12682.8
2087 | 135184 | -18383.7 | 37 | 36 | 88.7463 | 11015.6
2088 | 162926 | -11305.8 | 36 | 35 | 89.253 | 11018.6
2089 | 159052 | -22328.9 | 36 | 35 | 93.0729 | 11021.2
2090 | 155113 | -22934 | 37 | 35 | 92.2344 | 11024.1
2091 | 153226 | -28700 | 37 | 36 | 92.8116 | 11026.8
2092 | 154219 | -31235.4 | 36 | 35 | 96.4341 | 12261.2
2093 | 205150 | -30936.8 | 35 | 34 | 136.723 | 29948.8
2094 | 324926 | -488488 | 34 | 34 | 259.697 | 88991.7
2095 | 399272 | -439552 | 38 | 37 | 265.417 | 108109
2096 | 450411 | -308407 | 43 | 39 | 269.464 | 149702
2097 | 463717 | -237985 | 47 | 42 | 270.974 | 176173
2098 | 434705 | -181618 | 50 | 44 | 261.484 | 179947
2099 | 418986 | -143905 | 53 | 46 | 247.632 | 179944
2100 | 404452 | -97728.3 | 56 | 49 | 246.909 | 179942
2101 | 448650 | -75805.7 | 57 | 50 | 264.04 | 179939
2102 | 481383 | -57891.1 | 58 | 51 | 270.102 | 177612
2103 | 496865 | -33488.8 | 59 | 52 | 271.157 | 161450
2104 | 490257 | -26394.5 | 59 | 52 | 266.562 | 131755
2105 | 448013 | -30914.7 | 59 | 53 | 243.863 | 98761.4
2106 | 338228 | -65188.5 | 59 | 53 | 171.58 | 61080.8
2107 | 186701 | 0 | 59 | 53 | 117.346 | 43652.6
2108 | 167091 | 0 | 59 | 54 | 103.102 | 38725.5
2109 | 153739 | 0 | 59 | 55 | 91.8407 | 23698.6
2110 | 142604 | 0 | 59 | 55 | 83.3415 | 12670.8
2111 | 137562 | 0 | 60 | 54 | 79.6351 | 11002.3
2112 | 136219 | 0 | 60 | 54 | 78.9739 | 11003.6
2113 | 135344 | 0 | 60 | 54 | 78.9338 | 11004.7
2114 | 134578 | 0 | 60 | 54 | 78.899 | 11005.5
2115 | 133876 | 0 | 60 | 54 | 78.8671 | 11006.1
2116 | 137167 | 0 | 60 | 55 | 82.5975 | 12238.6
2117 | 183990 | 0 | 61 | 55 | 121.463 | 29924.3
2118 | 368798 | -54546 | 61 | 55 | 246.376 | 88965.4
2119 | 507815 | -33460.4 | 62 | 56 | 279.027 | 108081
2120 | 552960 | -22582.7 | 64 | 56 | 276.648 | 149678
2121 | 601598 | -18677.2 | 65 | 57 | 278.717 | 176152
2122 | 698245 | -13095.8 | 69 | 59 | 280.279 | 179927
2123 | 707185 | -9970.12 | 72 | 61 | 268.601 | 179926
2124 | 914444 | -11400.4 | 76 | 63 | 283.57 | 179925
2125 | 975912 | -8573.67 | 77 | 63 | 288.119 | 179924
2126 | 1067780 | -9890.14 | 78 | 64 | 311.626 | 177599
2127 | 1131120 | -10639.4 | 79 | 64 | 300.565 | 161439
2128 | 1044500 | -7435.84 | 77 | 63 | 291.906 | 131744
2129 | 910884 | -4987.52 | 76 | 62 | 264.725 | 98751.6
2130 | 585311 | -4431.09 | 74 | 61 | 180.212 | 61070.9
2131 | 190433 | 0 | 73 | 61 | 118.308 | 43642.1
2132 | 170124 | 0 | 72 | 60 | 103.563 | 38714.7
2133 | 156872 | 0 | 71 | 60 | 92.208 | 23682.6
2134 | 145622 | 0 | 66 | 58 | 82.4005 | 12652.9
2135 | 140383 | 0 | 60 | 55 | 78.2431 | 10982.6
2136 | 138624 | 0 | 55 | 52 | 79.2023 | 10982.7
2137 | 137659 | 0 | 54 | 51 | 79.1579 | 10982.8
2138 | 136830 | 0 | 54 | 51 | 79.1202 | 10983.4
2139 | 135987 | 0 | 53 | 51 | 79.0819 | 10984.2
2140 | 138708 | 0 | 51 | 50 | 82.6679 | 12217.2
2141 | 185071 | 0 | 50 | 49 | 121.203 | 29903.3
2142 | 337246 | -42099.4 | 48 | 47 | 241.007 | 88944.8
2143 | 468118 | -66989.2 | 50 | 49 | 269.751 | 108061
2144 | 515263 | -75005.8 | 51 | 50 | 270.715 | 149665
2145 | 532596 | -58239.9 | 53 | 51 | 271.514 | 176140
2146 | 533107 | -31770.6 | 56 | 52 | 263.822 | 179916
2147 | 513789 | -11629.5 | 59 | 52 | 249.816 | 179916
2148 | 581805 | -11305.2 | 62 | 52 | 255.817 | 179916
2149 | 644305 | -10226.6 | 62 | 52 | 276.797 | 179916
2150 | 700340 | -9747.49 | 63 | 52 | 297.376 | 177590
2151 | 666743 | -9256.44 | 63 | 51 | 296.357 | 161430
2152 | 626875 | -9333.61 | 62 | 51 | 275.131 | 131736
2153 | 554864 | -8578.21 | 62 | 50 | 251.566 | 98742.9
2154 | 375282 | -8336.44 | 61 | 49 | 175.99 | 61062.9
2155 | 189552 | 0 | 54 | 46 | 117.174 | 43635.5
2156 | 169484 | 0 | 48 | 43 | 103.212 | 38709
2157 | 155879 | 0 | 44 | 41 | 91.9388 | 23677.5
2158 | 144562 | 0 | 43 | 40 | 83.4308 | 12649.3
2159 | 139589 | 0 | 42 | 39 | 79.7271 | 10980.4
2160 | 137727 | -6996.67 | 41 | 39 | 82.0052 | 10982.2
2161 | 136472 | 0 | 40 | 38 | 75.0519 | 10777.6
2162 | 135446 | -12375.3 | 39 | 37 | 82.9777 | 10780
2163 | 134536 | 0 | 38 | 37 | 74.9638 | 10782.2
2164 | 156850 | -18263.3 | 37 | 36 | 87.6349 | 10784.2
2165 | 152936 | -6616.22 | 37 | 35 | 81.0804 | 10786.4
2166 | 167682 | -14685.9 | 35 | 34 | 81.829 | 10788.4
2167 | 133119 | -379560 | 34 | 32 | 92.8753 | 10790.7
2168 | 146068 | -386211 | 35 | 33 | 95.0583 | 10793.2
2169 | 131353 | -345346 | 34 | 32 | 92.5874 | 10796.3
2170 | 137892 | -344936 | 35 | 33 | 92.5468 | 10796.6
2171 | 129609 | -339116 | 34 | 34 | 91.8199 | 10798.2
2172 | 128670 | -339058 | 34 | 34 | 91.7221 | 10799.4
2173 | 133794 | -335770 | 35 | 35 | 91.4002 | 10800.6
2174 | 128799 | -8503.29 | 35 | 35 | 76.6906 | 10801.8
2175 | 125754 | -9105.97 | 36 | 36 | 75.5642 | 10803.1
2176 | 126221 | -13459.8 | 36 | 36 | 76.2332 | 10803.9
2177 | 145119 | -14474.7 | 36 | 36 | 81.8484 | 10806.3
2178 | 160320 | -18871 | 36 | 36 | 90.4525 | 10808
2179 | 152451 | -16431.5 | 36 | 36 | 92.2206 | 10809.8
2180 | 151773 | -24531.6 | 36 | 36 | 93.305 | 10812
2181 | 149581 | -24887.3 | 34 | 34 | 93.0706 | 10814.4
2182 | 146685 | -22827.9 | 33 | 33 | 91.2492 | 10816.8
2183 | 146311 | -24145 | 34 | 34 | 90.3397 | 10819.2
2184 | 143793 | -25347.6 | 34 | 34 | 85.4541 | 4010.88
2185 | 142673 | -35495.9 | 31 | 31 | 85.648 | 4012.79
2186 | 141029 | -41505.5 | 31 | 31 | 85.5009 | 4014.79
2187 | 140114 | -48179 | 32 | 32 | 85.2044 | 4016.69
2188 | 140272 | -60919.4 | 32 | 32 | 87.329 | 4018.62
2189 | 142315 | -66611.9 | 32 | 32 | 86.2501 | 4020.47
2190 | 137899 | -59872.8 | 32 | 32 | 82.1464 | 4022.96
2191 | 138156 | -49666 | 35 | 35 | 79.6627 | 4025.17
2192 | 144015 | -47200.7 | 40 | 39 | 81.5463 | 4026.73
2193 | 142095 | -30247.3 | 44 | 41 | 80.5466 | 4028.29
2194 | 131556 | -15303.9 | 46 | 42 | 76.7261 | 4029.83
2195 | 133206 | -12655.9 | 48 | 43 | 76.7532 | 4030.07
2196 | 132186 | -10062.6 | 52 | 46 | 76.6042 | 4029.85
2197 | 132204 | -8846.85 | 52 | 46 | 76.68 | 4029.16
2198 | 145318 | -12695.3 | 52 | 46 | 79.9541 | 4029.9
2199 | 119661 | -5415.08 | 54 | 46 | 71.708 | 4029.95
2200 | 134076 | -5581.74 | 55 | 47 | 77.1319 | 4030.78
2201 | 145291 | -3770.68 | 53 | 46 | 78.6077 | 4031.31
2202 | 119780 | -10532.2 | 51 | 45 | 80.6138 | 4031.25
2203 | 147205 | -10237.6 | 51 | 45 | 89.4856 | 4032.09
2204 | 144957 | -13299.6 | 47 | 43 | 89.3946 | 4032.96
2205 | 140380 | -14080.3 | 47 | 42 | 89.1053 | 4033.81
2206 | 139617 | -20397.9 | 44 | 41 | 88.2201 | 4035.12
2207 | 141343 | -18802.6 | 48 | 43 | 87.5133 | 4036.16
2208 | 138828 | -16589.6 | 46 | 43 | 90.3322 | 10847.9
2209 | 137611 | -19880.1 | 43 | 41 | 90.2536 | 10849.3
2210 | 141592 | -25454.8 | 42 | 40 | 90.6039 | 10849.4
2211 | 136522 | -24094.8 | 42 | 41 | 90.1779 | 10850.1
2212 | 140718 | -25843.4 | 43 | 41 | 94.0297 | 12057.5
2213 | 188278 | -21992.8 | 40 | 40 | 133.336 | 29376.2
2214 | 315601 | -435000 | 41 | 41 | 259.62 | 87191.6
2215 | 407757 | -441473 | 40 | 40 | 272.039 | 105910
2216 | 410466 | -377259 | 38 | 38 | 271.707 | 146635
2217 | 415869 | -377367 | 38 | 38 | 267.448 | 172554
2218 | 394138 | -391038 | 37 | 37 | 257.383 | 176250
2219 | 385960 | -371559 | 37 | 37 | 242.364 | 176248
2220 | 351028 | -352285 | 37 | 37 | 238.491 | 176246
2221 | 392975 | -322632 | 37 | 37 | 258.527 | 176244
2222 | 417893 | -312917 | 37 | 37 | 266.404 | 173965
2223 | 422955 | -307815 | 38 | 37 | 268.155 | 158139
2224 | 417400 | -314992 | 38 | 37 | 263.318 | 129060
2225 | 383609 | -352883 | 37 | 37 | 241.232 | 96752.1
2226 | 312548 | -408946 | 37 | 36 | 196.463 | 59853.8
2227 | 179056 | 0 | 36 | 36 | 121.273 | 42787
2228 | 159834 | -10907.2 | 35 | 35 | 109.892 | 37961.5
2229 | 146646 | -15793.8 | 35 | 35 | 99.4683 | 23250.1
2230 | 162046 | -25320.1 | 35 | 35 | 97.1967 | 12454.1
2231 | 153548 | -31131.9 | 35 | 35 | 93.4852 | 10822.1
2232 | 150348 | -37803.8 | 35 | 35 | 92.6529 | 10825.7
2233 | 147873 | -47798.8 | 33 | 33 | 92.6576 | 10828.9
2234 | 146003 | -57883.9 | 32 | 32 | 92.6056 | 10831.7
2235 | 144509 | -72329.3 | 31 | 31 | 92.5932 | 10834.2
2236 | 146755 | -78321.9 | 32 | 32 | 96.7373 | 12043
2237 | 199397 | -68809.4 | 32 | 32 | 137.058 | 29363.3
2238 | 321770 | -613072 | 32 | 32 | 267.609 | 87180.1
2239 | 383642 | -582865 | 32 | 32 | 290.863 | 105900
2240 | 402299 | -486819 | 32 | 31 | 265.009 | 146627
2241 | 400359 | -463147 | 32 | 31 | 264.626 | 172548
2242 | 394399 | -470030 | 32 | 32 | 256.934 | 176245
2243 | 378471 | -401734 | 34 | 34 | 241.626 | 176244
2244 | 355134 | -393120 | 34 | 32 | 238.864 | 176243
2245 | 388982 | -323883 | 36 | 33 | 257.266 | 176241
2246 | 422456 | -300668 | 38 | 34 | 285.323 | 173961
2247 | 424450 | -301428 | 38 | 33 | 286.771 | 158135
2248 | 435189 | -300043 | 40 | 34 | 283.204 | 129057
2249 | 397356 | -322316 | 40 | 34 | 260.321 | 96748.9
2250 | 330659 | -390052 | 40 | 34 | 172.797 | 59850.4
2251 | 183902 | -8215.4 | 34 | 30 | 125.363 | 42783.5
2252 | 163011 | -10983.3 | 31 | 29 | 110.248 | 37958.2
2253 | 155573 | -17628.3 | 30 | 28 | 100.79 | 23246.2
2254 | 165054 | -22496.3 | 30 | 28 | 93.4626 | 12450.2
2255 | 157574 | -30716.2 | 30 | 28 | 93.0836 | 10818.4
2256 | 152695 | -36981.7 | 29 | 27 | 91.7924 | 10821.7
2257 | 150751 | -44365.2 | 28 | 27 | 91.931 | 10824.6
2258 | 148313 | -50641.5 | 28 | 27 | 91.6487 | 10827
2259 | 147011 | -59185.2 | 28 | 27 | 91.6416 | 10829.2
2260 | 148665 | -68221.9 | 27 | 26 | 95.3694 | 12037.5
2261 | 196176 | -53352 | 28 | 26 | 134.635 | 29357.3
2262 | 323185 | -624856 | 28 | 26 | 269.341 | 87173.6
2263 | 385387 | -560911 | 31 | 29 | 284.918 | 105893
2264 | 403659 | -411219 | 34 | 30 | 265.099 | 146622
2265 | 427682 | -332865 | 39 | 32 | 266.25 | 172542
2266 | 423904 | -316191 | 40 | 34 | 258.136 | 176238
2267 | 437504 | -263802 | 44 | 38 | 245.926 | 176236
2268 | 403356 | -227338 | 45 | 35 | 243.082 | 176234
2269 | 449577 | -183810 | 48 | 37 | 264.65 | 176232
2270 | 472324 | -158121 | 49 | 38 | 273.524 | 173952
2271 | 463802 | -122852 | 50 | 38 | 274.561 | 158125
2272 | 463258 | -127948 | 50 | 37 | 270.094 | 129046
2273 | 425580 | -149338 | 49 | 37 | 246.269 | 96737.6
2274 | 340626 | -237503 | 46 | 36 | 174.156 | 59839.3
2275 | 184131 | 0 | 39 | 32 | 116.619 | 42773
2276 | 164885 | -8033.88 | 37 | 32 | 110.695 | 37948.1
2277 | 151370 | 0 | 36 | 31 | 91.7326 | 23234.8
2278 | 140145 | -13665 | 32 | 30 | 91.3009 | 12437.8
2279 | 168819 | -8732.44 | 30 | 29 | 90.1482 | 10805.7
2280 | 161414 | -15607.6 | 30 | 28 | 92.1085 | 10808
2281 | 157741 | -20961.9 | 28 | 27 | 91.6187 | 10810.8
2282 | 154197 | -25762.6 | 29 | 28 | 91.3658 | 10813.4
2283 | 152164 | -29802.5 | 29 | 29 | 91.2004 | 10815.4
2284 | 152990 | -36606.9 | 29 | 28 | 94.9602 | 12023.8
2285 | 200703 | -31631.2 | 30 | 29 | 134.342 | 29343.5
2286 | 324325 | -572585 | 30 | 29 | 266.145 | 87159.8
2287 | 386506 | -512617 | 33 | 32 | 284.581 | 105880
2288 | 404837 | -381194 | 36 | 33 | 264.79 | 146610
2289 | 446741 | -323378 | 42 | 37 | 268.296 | 172533
2290 | 440928 | -269901 | 45 | 39 | 260.149 | 176230
2291 | 417530 | -167999 | 52 | 41 | 247.017 | 176227
2292 | 401043 | -125476 | 55 | 42 | 246.335 | 176226
2293 | 446969 | -74725 | 58 | 45 | 265.291 | 176223
2294 | 477600 | -54001.6 | 59 | 47 | 270.798 | 173943
2295 | 478457 | -32680.8 | 60 | 47 | 270.52 | 158118
2296 | 493567 | -25056.4 | 62 | 48 | 268.137 | 129039
2297 | 440632 | -23895.1 | 61 | 48 | 243.526 | 96730.8
2298 | 337036 | -79089.7 | 57 | 45 | 171.261 | 59832.8
2299 | 186407 | 0 | 55 | 45 | 117.433 | 42766.6
2300 | 166571 | 0 | 53 | 44 | 103.078 | 37941.8
2301 | 153232 | 0 | 52 | 44 | 91.8175 | 23226.5
2302 | 142271 | 0 | 45 | 44 | 83.3263 | 12428.1
2303 | 136975 | 0 | 43 | 43 | 79.6087 | 10794.7
2304 | 135318 | -12610.6 | 42 | 42 | 87.3893 | 10796.5
2305 | 134145 | 0 | 41 | 40 | 78.9986 | 10798.2
2306 | 152588 | -17319.7 | 40 | 39 | 91.1593 | 10800.3
2307 | 149400 | -7296.48 | 39 | 39 | 86.1707 | 10801.7
2308 | 164953 | -17223 | 38 | 37 | 92.9672 | 12010.2
2309 | 209933 | -16778.1 | 37 | 37 | 135.583 | 29330.1
2310 | 326126 | -360881 | 37 | 36 | 239.196 | 87147.2
2311 | 388138 | -372804 | 37 | 36 | 267.784 | 105868
2312 | 409337 | -317266 | 37 | 36 | 266.225 | 146600
2313 | 415671 | -311608 | 37 | 36 | 265.675 | 172523
2314 | 404604 | -317629 | 37 | 35 | 256.334 | 176220
2315 | 406500 | -281549 | 39 | 36 | 242.73 | 176220
2316 | 378149 | -261187 | 40 | 36 | 259.089 | 176219
2317 | 451873 | -203051 | 44 | 37 | 282.395 | 176218
2318 | 485134 | -185998 | 45 | 37 | 291.84 | 173939
2319 | 469942 | -134299 | 48 | 38 | 274.243 | 158114
2320 | 471743 | -142622 | 47 | 36 | 269.774 | 129036
2321 | 432073 | -173462 | 45 | 35 | 245.458 | 96728.1
2322 | 328486 | -248475 | 42 | 33 | 172.266 | 59830.5
2323 | 185133 | 0 | 38 | 31 | 116.571 | 42764.7
2324 | 165752 | -11517.6 | 35 | 29 | 112.143 | 37940.1
2325 | 152227 | 0 | 34 | 28 | 91.7717 | 23225.6
2326 | 141033 | -22744.1 | 34 | 28 | 92.4634 | 12428.9
2327 | 155748 | -12619.7 | 33 | 27 | 87.0723 | 10796.6
2328 | 162266 | -29800.3 | 29 | 25 | 89.9562 | 10799.8
2329 | 157239 | -31572.8 | 28 | 25 | 89.2086 | 10802.8
2330 | 154081 | -43050.3 | 27 | 24 | 89.793 | 10806.7
2331 | 151722 | -48798.9 | 27 | 25 | 89.5509 | 10810.4
2332 | 156804 | -61534.4 | 26 | 24 | 90.1016 | 10813.6
2333 | 147970 | -62596.7 | 25 | 23 | 87.2256 | 10816.8
2334 | 146436 | -79927.3 | 23 | 21 | 84.8446 | 10819.8
2335 | 128171 | -743017 | 26 | 23 | 124.805 | 10822.1
2336 | 130019 | -647174 | 27 | 23 | 112.035 | 10824
2337 | 128247 | -518867 | 30 | 24 | 103.227 | 10823
2338 | 127977 | -446376 | 33 | 26 | 98.6247 | 10820.3
2339 | 135276 | -396736 | 36 | 28 | 95.3654 | 10820.2
2340 | 150629 | -375324 | 38 | 29 | 93.6826 | 10820.1
2341 | 150373 | -371163 | 38 | 29 | 93.2402 | 10820.4
2342 | 123931 | -8935.51 | 39 | 30 | 75.8916 | 10820.7
2343 | 123757 | -10677.6 | 41 | 31 | 75.5654 | 10821.3
2344 | 124742 | -13754.9 | 40 | 31 | 75.8164 | 10822.9
2345 | 123089 | -13206.8 | 40 | 30 | 77.5316 | 10824.7
2346 | 152536 | -22112.9 | 40 | 30 | 89.8064 | 10825.8
2347 | 151991 | -22888.1 | 39 | 30 | 93.0215 | 10827.6
2348 | 146068 | -20182.4 | 38 | 30 | 92.0065 | 10829.5
2349 | 144949 | -22647.8 | 38 | 30 | 91.8906 | 10831.9
2350 | 142511 | -24706.3 | 37 | 30 | 90.7085 | 10833.6
2351 | 141588 | -26184.3 | 37 | 30 | 89.8852 | 10835.4
2352 | 139520 | -28096.2 | 36 | 30 | 85.1732 | 4026.7
2353 | 138648 | -34572.4 | 36 | 29 | 85.2968 | 4028.28
2354 | 137465 | -39210.7 | 37 | 30 | 85.0204 | 4029.96
2355 | 137793 | -54956.9 | 37 | 30 | 86.8732 | 4031.54
2356 | 135916 | -59698.8 | 37 | 30 | 86.4484 | 4033.05
2357 | 135823 | -67473.2 | 37 | 30 | 85.7344 | 4035.16
2358 | 134691 | -73596.1 | 36 | 29 | 83.106 | 4037.09
2359 | 134577 | -65490.4 | 38 | 32 | 80.636 | 4039.02
2360 | 136216 | -56851.4 | 38 | 33 | 81.0029 | 4040.83
2361 | 136676 | -40454.7 | 43 | 35 | 80.8381 | 4042.59
2362 | 142101 | -31042.8 | 47 | 37 | 81.063 | 4044.08
2363 | 140761 | -24042.6 | 48 | 39 | 80.12 | 4045.01
2364 | 129248 | -13586.2 | 51 | 41 | 76.3864 | 4045.17
2365 | 130824 | -11612.7 | 53 | 43 | 76.3548 | 4045.18
2366 | 144416 | -12971.1 | 55 | 45 | 79.7235 | 4044.99
2367 | 119116 | 0 | 56 | 46 | 67.2524 | 4044.46
2368 | 119173 | -10656.3 | 58 | 47 | 73.8754 | 4044.41
2369 | 137351 | -4989.31 | 55 | 46 | 79.2781 | 4044.53
2370 | 119140 | 0 | 54 | 45 | 72.9101 | 4043.85
2371 | 144785 | -16681.5 | 47 | 41 | 89.42 | 4044.2
2372 | 140881 | -14586.5 | 45 | 41 | 89.2141 | 4044.95
2373 | 139017 | -22780.9 | 40 | 38 | 89.3401 | 4045.46
2374 | 136249 | -29086.3 | 40 | 38 | 88.117 | 4047.26
2375 | 134916 | -41311.3 | 37 | 36 | 88.3935 | 4048.63
2376 | 134190 | -45488.7 | 36 | 36 | 91.2333 | 10860.7
2377 | 133517 | -51869.1 | 36 | 36 | 91.7703 | 10862.3
2378 | 132773 | -60674.7 | 36 | 36 | 91.8077 | 10863.2
2379 | 131870 | -73659 | 33 | 33 | 92.0416 | 10864.5
2380 | 134814 | -83719.9 | 33 | 33 | 95.9982 | 12072.2
2381 | 187282 | -72026.9 | 34 | 34 | 136.323 | 29391.5
2382 | 313824 | -630503 | 35 | 34 | 268.791 | 87207.5
2383 | 380228 | -562877 | 37 | 36 | 283.513 | 105927
2384 | 409581 | -409686 | 39 | 37 | 265.626 | 146647
2385 | 439129 | -296793 | 47 | 41 | 268.946 | 172567
2386 | 400104 | -152712 | 57 | 46 | 260.813 | 176262
2387 | 393491 | -142046 | 56 | 45 | 246.526 | 176257
2388 | 397275 | -106306 | 58 | 46 | 245.243 | 176253
2389 | 439079 | -65768.3 | 61 | 48 | 263.882 | 176250
2390 | 454094 | -54208.9 | 60 | 48 | 266.777 | 173969
2391 | 460998 | -48549.9 | 60 | 48 | 268.645 | 158141
2392 | 459200 | -59555.2 | 59 | 48 | 265.489 | 129060
2393 | 417013 | -60609.9 | 59 | 48 | 242.337 | 96750.6
2394 | 310232 | -114952 | 58 | 48 | 172.284 | 59851.6
2395 | 181258 | 0 | 55 | 47 | 116.593 | 42784.6
2396 | 161778 | 0 | 54 | 47 | 102.858 | 37958.9
2397 | 148570 | 0 | 54 | 47 | 91.6046 | 23247.1
2398 | 137735 | 0 | 54 | 47 | 83.12 | 12448.9
2399 | 133143 | -5399.36 | 53 | 47 | 85.805 | 10815.9
2400 | 131722 | 0 | 53 | 47 | 78.4641 | 10817.6
2401 | 133330 | -7018.63 | 53 | 47 | 85.1283 | 10819
2402 | 130407 | 0 | 55 | 48 | 78.4056 | 10820.2
2403 | 130153 | -1027.47 | 55 | 48 | 82.821 | 10821.1
2404 | 133043 | 0 | 55 | 48 | 82.4107 | 12028.1
2405 | 179988 | -1608.45 | 54 | 48 | 125.543 | 29346.8
2406 | 325436 | -154668 | 53 | 48 | 239.984 | 87162.1
2407 | 423385 | -167711 | 53 | 48 | 265.851 | 105880
2408 | 446087 | -119849 | 53 | 49 | 270.24 | 146609
2409 | 455692 | -114791 | 53 | 49 | 272.061 | 172530
2410 | 446909 | -147675 | 50 | 48 | 262.426 | 176226
2411 | 440447 | -155652 | 50 | 49 | 247.91 | 176225
2412 | 412399 | -145295 | 50 | 48 | 245.852 | 176224
2413 | 455652 | -136528 | 50 | 48 | 266.316 | 176223
2414 | 478126 | -121113 | 51 | 49 | 273.607 | 173945
2415 | 467116 | -114006 | 50 | 48 | 273.343 | 158120
2416 | 478393 | -129224 | 49 | 48 | 288.608 | 129041
2417 | 434311 | -150312 | 49 | 48 | 247.124 | 96733.5
2418 | 331375 | -192687 | 50 | 49 | 175.236 | 59835.8
2419 | 185356 | 0 | 50 | 49 | 117.197 | 42769.8
2420 | 165892 | 0 | 51 | 50 | 103.047 | 37944.7
2421 | 152618 | -5582.82 | 52 | 51 | 98.3039 | 23230.7
2422 | 141904 | 0 | 56 | 55 | 83.3094 | 12432.9
2423 | 136718 | 0 | 56 | 54 | 83.7543 | 10799.5
2424 | 135170 | 0 | 55 | 53 | 79.0454 | 10801.5
2425 | 134282 | 0 | 54 | 52 | 79.0046 | 10802.7
2426 | 133572 | 0 | 55 | 52 | 78.9723 | 10803.9
2427 | 132957 | -8072.08 | 55 | 52 | 85.7137 | 10804.8
2428 | 136061 | 0 | 55 | 52 | 82.5474 | 12012.2
2429 | 182696 | -1542.57 | 53 | 51 | 125.669 | 29330.9
2430 | 329788 | -103550 | 54 | 52 | 240.121 | 87146.4
2431 | 448313 | -117047 | 55 | 53 | 272.423 | 105865
2432 | 480644 | -70570.1 | 56 | 54 | 270.634 | 146596
2433 | 507949 | -45889 | 59 | 55 | 272.561 | 172519
2434 | 495267 | -28579.5 | 60 | 56 | 260.893 | 176216
2435 | 485084 | -19693.3 | 62 | 57 | 249.274 | 176214
2436 | 405121 | -73402.6 | 50 | 47 | 239.804 | 176214
2437 | 497739 | -77837.8 | 53 | 51 | 266.422 | 176213
2438 | 491922 | -63833.3 | 55 | 49 | 271.473 | 173935
2439 | 476324 | -55163.4 | 53 | 49 | 269.353 | 158111
2440 | 480306 | -60209.6 | 53 | 49 | 265.645 | 129032
2441 | 426071 | -72727 | 52 | 49 | 242.665 | 96724.7
2442 | 344024 | -142549 | 50 | 47 | 174.121 | 59827.2
2443 | 187189 | 0 | 50 | 47 | 117.146 | 42761.4
2444 | 167510 | 0 | 48 | 46 | 103.121 | 37937.1
2445 | 153971 | -5312.1 | 46 | 45 | 98.3105 | 23221.4
2446 | 142782 | 0 | 46 | 45 | 83.3497 | 12423.3
2447 | 137837 | -11441.2 | 45 | 44 | 87.6679 | 10789.9
2448 | 136240 | 0 | 45 | 44 | 78.975 | 10792.2
2449 | 135347 | -14029.7 | 46 | 45 | 87.1964 | 10794.2
2450 | 134366 | 0 | 46 | 45 | 78.8895 | 10796.1
2451 | 133560 | -14919.5 | 46 | 45 | 87.1523 | 10797.7
2452 | 157146 | -5967.99 | 45 | 45 | 90.1161 | 12005.8
2453 | 210739 | -10387.5 | 45 | 44 | 129.015 | 29325.1
2454 | 327953 | -229698 | 45 | 44 | 239.122 | 87141.3
2455 | 456986 | -269429 | 45 | 44 | 268.168 | 105861
2456 | 472490 | -221317 | 45 | 44 | 272.017 | 146593
2457 | 485432 | -204120 | 46 | 45 | 273.221 | 172516
2458 | 465934 | -193074 | 46 | 45 | 263.102 | 176214
2459 | 450114 | -179971 | 47 | 45 | 248.478 | 176213
2460 | 414751 | -142658 | 48 | 46 | 245.151 | 176213
2461 | 463443 | -121476 | 50 | 47 | 267.028 | 176212
2462 | 484345 | -108594 | 50 | 47 | 269.934 | 173934
2463 | 490442 | -96033.5 | 50 | 49 | 272.532 | 158109
2464 | 468141 | -96748.2 | 50 | 46 | 265.598 | 129030
2465 | 430673 | -105974 | 50 | 46 | 243.798 | 96722.8
2466 | 348626 | -161170 | 49 | 46 | 174.813 | 59825.3
2467 | 187105 | 0 | 48 | 46 | 116.994 | 42759.6
2468 | 167488 | 0 | 48 | 46 | 103.12 | 37935.2
2469 | 154068 | 0 | 48 | 46 | 91.8558 | 23219.2
2470 | 142942 | -6887.92 | 47 | 46 | 90.3209 | 12420.7
2471 | 137906 | 0 | 46 | 45 | 79.6507 | 10787.4
2472 | 136330 | -12348 | 44 | 44 | 86.9514 | 10789.4
2473 | 135154 | 0 | 42 | 42 | 79.0444 | 10791.4
2474 | 155423 | -17596.9 | 40 | 40 | 91.2352 | 10793.2
2475 | 152049 | -8797.93 | 40 | 39 | 86.2918 | 10795.1
2476 | 169173 | -17111.2 | 38 | 38 | 93.1599 | 12003.4
2477 | 213205 | -16248.4 | 36 | 36 | 135.579 | 29323.4
2478 | 326885 | -389032 | 34 | 34 | 238.004 | 87140.5
2479 | 388743 | -406267 | 33 | 33 | 263.023 | 105861
2480 | 407179 | -345854 | 33 | 33 | 264.939 | 146594
2481 | 404947 | -335973 | 33 | 33 | 264.487 | 172518
2482 | 400647 | -357155 | 33 | 33 | 275.308 | 176217
2483 | 385492 | -313509 | 34 | 33 | 260.335 | 176217
2484 | 361293 | -288383 | 36 | 35 | 238.898 | 176216
2485 | 392463 | -249170 | 36 | 34 | 276.473 | 176215
2486 | 425169 | -236468 | 37 | 34 | 285.428 | 173936
2487 | 434436 | -238174 | 38 | 35 | 287.555 | 158112
2488 | 440379 | -254652 | 39 | 35 | 284.176 | 129034
2489 | 397890 | -276120 | 39 | 35 | 260.731 | 96727.3
2490 | 322202 | -346186 | 38 | 34 | 173.089 | 59830.1
2491 | 186909 | 0 | 39 | 35 | 120.962 | 42764.1
2492 | 165832 | -7597.34 | 39 | 35 | 109.455 | 37938.9
2493 | 152412 | -11839.1 | 39 | 35 | 98.9436 | 23224.8
2494 | 141188 | -12398.3 | 39 | 35 | 90.3894 | 12428
2495 | 155935 | -15838.3 | 37 | 34 | 90.1682 | 10795.5
2496 | 162924 | -21905.4 | 35 | 33 | 88.7284 | 10798.5
2497 | 159397 | -25620.8 | 35 | 33 | 88.9306 | 10801
2498 | 162130 | -28673.1 | 33 | 31 | 89.9399 | 10804.6
2499 | 154135 | -30580.2 | 32 | 31 | 88.2066 | 10807.9
2500 | 159616 | -43768.1 | 28 | 28 | 90.4261 | 10810.8
2501 | 149554 | -47782.5 | 27 | 27 | 86.6731 | 10813.3
2502 | 150656 | -51204.6 | 28 | 28 | 84.3599 | 10816.2
2503 | 130991 | -586823 | 34 | 33 | 107.707 | 10818.6
2504 | 184328 | -525564 | 39 | 35 | 104.179 | 10820.5
2505 | 168255 | -390632 | 42 | 37 | 95.6289 | 10819.9
2506 | 184404 | -322175 | 47 | 40 | 91.0642 | 10817.3
2507 | 184963 | -267833 | 52 | 42 | 89.2084 | 10817.3
2508 | 185874 | -229381 | 54 | 42 | 87.8195 | 10817.2
2509 | 188465 | -218271 | 54 | 42 | 88.0843 | 10817.5
2510 | 125432 | 0 | 57 | 42 | 68.8902 | 10817.9
2511 | 125243 | 0 | 55 | 41 | 68.8355 | 10818
2512 | 125184 | 0 | 56 | 41 | 68.8347 | 10818
2513 | 124946 | -5767.95 | 55 | 41 | 77.0051 | 10817.6
2514 | 124740 | 0 | 53 | 41 | 74.5435 | 10817.6
2515 | 124357 | -1652.86 | 46 | 38 | 82.9871 | 10818
2516 | 124033 | 0 | 44 | 38 | 79.3037 | 10818.6
2517 | 123745 | -14520.4 | 40 | 37 | 87.1734 | 10819.5
2518 | 154507 | -8982.5 | 39 | 37 | 88.8285 | 10820.8
2519 | 159011 | -18602.2 | 37 | 36 | 91.7644 | 10822.3
2520 | 147266 | -14128.3 | 37 | 35 | 85.9732 | 4014.26
2521 | 145005 | -20294.2 | 37 | 34 | 85.5997 | 4016.6
2522 | 151244 | -30261.1 | 33 | 31 | 87.539 | 4018.27
2523 | 141167 | -28889.7 | 33 | 31 | 85.8173 | 4020.12
2524 | 151652 | -41528 | 33 | 32 | 88.6516 | 4022.49
2525 | 138339 | -45169.4 | 29 | 28 | 84.8503 | 4024.21
2526 | 137586 | -48089.5 | 32 | 30 | 81.6807 | 4026.77
2527 | 147713 | -45567.3 | 38 | 35 | 81.9018 | 4028.26
2528 | 140134 | -26976.6 | 42 | 37 | 76.8051 | 4030
2529 | 146880 | -26408.3 | 46 | 39 | 80.9695 | 4032.23
2530 | 131409 | -12424.8 | 52 | 41 | 74.2721 | 4032.51
2531 | 136109 | -11229.4 | 56 | 42 | 76.7517 | 4032.94
2532 | 132397 | -944.089 | 58 | 42 | 70.2973 | 4032.54
2533 | 119915 | -9329.07 | 60 | 43 | 73.5823 | 4031.51
2534 | 120052 | 0 | 61 | 44 | 67.5611 | 4030.84
2535 | 120116 | 0 | 61 | 44 | 67.3102 | 4030.08
2536 | 120262 | 0 | 62 | 45 | 67.6048 | 4029.38
2537 | 120405 | 0 | 62 | 46 | 69.3557 | 4028.64
2538 | 120328 | 0 | 59 | 45 | 72.4263 | 4028.12
2539 | 125161 | -6830.33 | 52 | 41 | 82.9104 | 4027.86
2540 | 158715 | -5572.93 | 48 | 40 | 90.4849 | 4027.91
2541 | 147262 | -10977.7 | 48 | 40 | 89.7176 | 4028.25
2542 | 145096 | -13151.2 | 46 | 39 | 88.7434 | 4029.45
2543 | 147676 | -15315.6 | 43 | 39 | 88.0664 | 4031.39
2544 | 145629 | -13298.5 | 40 | 37 | 90.8953 | 10843.1
2545 | 144180 | -15783.2 | 41 | 39 | 90.7923 | 10844.7
2546 | 143409 | -17370.2 | 40 | 38 | 90.7328 | 10844.9
2547 | 141870 | -21027.8 | 38 | 37 | 90.6277 | 10845.8
2548 | 140712 | -26514.2 | 37 | 36 | 94.1601 | 12052.9
2549 | 192339 | -32314.5 | 37 | 36 | 134.863 | 14739
2550 | 315162 | -458853 | 37 | 36 | 256.98 | 40035.7
2551 | 414232 | -411356 | 42 | 40 | 262.611 | 43925.6
2552 | 442342 | -258604 | 48 | 43 | 270.41 | 55592.9
2553 | 424967 | -145029 | 56 | 46 | 271.207 | 86722.9
2554 | 422151 | -89907.5 | 60 | 47 | 263.974 | 88665.1
2555 | 420754 | -67739.2 | 61 | 48 | 246.158 | 88660.4
2556 | 455821 | -50952.8 | 64 | 49 | 246.637 | 88656.8
2557 | 532837 | -30602 | 66 | 50 | 269.385 | 88653.5
2558 | 609296 | -22381.2 | 68 | 51 | 282.194 | 86704.2
2559 | 632738 | -20934 | 67 | 52 | 283.506 | 78917.9
2560 | 638866 | -19641.4 | 68 | 52 | 280.957 | 65293.6
2561 | 534769 | -16074.7 | 66 | 51 | 251.694 | 49724.1
2562 | 377457 | -20463.7 | 66 | 51 | 175.779 | 30263.7
2563 | 182796 | 0 | 60 | 49 | 114.233 | 21506.6
2564 | 162991 | 0 | 59 | 48 | 102.914 | 20534.3
2565 | 150056 | 0 | 60 | 49 | 91.6722 | 12746.8
2566 | 139146 | 0 | 61 | 49 | 83.4774 | 12435.5
2567 | 134427 | 0 | 60 | 48 | 79.2384 | 10801.4
2568 | 133232 | 0 | 58 | 48 | 78.5323 | 10802.4
2569 | 132413 | 0 | 54 | 47 | 78.4949 | 10803.3
2570 | 131594 | 0 | 52 | 46 | 78.4578 | 10803.9
2571 | 130764 | 0 | 48 | 43 | 78.4202 | 10804.6
2572 | 134063 | 0 | 46 | 44 | 82.4566 | 12011.5
2573 | 188962 | -8544.7 | 44 | 42 | 129.212 | 14697.3
2574 | 325794 | -117891 | 45 | 43 | 237.959 | 39994.3
2575 | 444677 | -224034 | 45 | 42 | 263.529 | 43883.3
2576 | 465284 | -178139 | 46 | 41 | 271.554 | 55556.3
2577 | 476379 | -168982 | 47 | 41 | 272.466 | 86691.5
2578 | 446443 | -127914 | 50 | 42 | 262.843 | 88636.9
2579 | 436877 | -84406 | 55 | 45 | 247.845 | 88636.2
2580 | 433317 | -67588.7 | 55 | 44 | 244.68 | 88635.1
2581 | 507170 | -35711.7 | 59 | 45 | 264.925 | 88633.9
2582 | 522881 | -29567.5 | 56 | 44 | 272.214 | 86686.8
2583 | 557385 | -17516.2 | 58 | 45 | 276.324 | 78901.5
2584 | 563097 | -18616 | 59 | 46 | 272.497 | 65278.2
2585 | 468775 | -16555.3 | 57 | 44 | 246.258 | 49709.6
2586 | 334415 | -53446.1 | 54 | 43 | 171.306 | 30249.9
2587 | 186351 | 0 | 49 | 40 | 115.399 | 21493.7
2588 | 166933 | 0 | 47 | 39 | 103.094 | 20522.1
2589 | 153436 | 0 | 45 | 39 | 91.827 | 12733.4
2590 | 142141 | 0 | 43 | 37 | 83.3206 | 12422.8
2591 | 137194 | -9003.49 | 40 | 35 | 87.3218 | 10789.3
2592 | 135515 | 0 | 37 | 33 | 79.0611 | 10790.8
2593 | 134504 | -17279.7 | 35 | 31 | 88.0593 | 10793.1
2594 | 154794 | -7547.86 | 34 | 31 | 86.3992 | 10795.2
2595 | 166375 | -16323.7 | 33 | 30 | 89.4237 | 10797.3
2596 | 165891 | -17710.1 | 32 | 28 | 96.6562 | 12005.9
2597 | 211313 | -14550 | 30 | 27 | 135.359 | 14693.8
2598 | 325980 | -409549 | 30 | 27 | 235.945 | 39992.4
2599 | 388114 | -369868 | 33 | 30 | 259.98 | 43882.5
2600 | 406438 | -275760 | 35 | 31 | 264.91 | 55555.4
2601 | 448210 | -235276 | 41 | 36 | 268.239 | 86689.5
2602 | 454367 | -204067 | 45 | 39 | 261.288 | 88634.7
2603 | 451139 | -159986 | 49 | 42 | 248.984 | 88633.4
2604 | 417726 | -100248 | 53 | 45 | 247.329 | 88632.4
2605 | 490743 | -68478.3 | 56 | 47 | 266.56 | 88631
2606 | 503251 | -33103.6 | 58 | 48 | 270.787 | 86683.6
2607 | 548272 | -19688.6 | 60 | 50 | 275.626 | 78898.3
2608 | 579998 | -17861.8 | 62 | 51 | 275.048 | 65275.1
2609 | 522972 | -15447.8 | 62 | 51 | 250.73 | 49706.5
2610 | 349703 | -18006.2 | 60 | 51 | 171.985 | 30246.9
2611 | 187598 | 0 | 58 | 50 | 115.154 | 21490.6
2612 | 167849 | 0 | 56 | 49 | 103.137 | 20519
2613 | 154503 | 0 | 55 | 49 | 91.8757 | 12729.4
2614 | 143334 | 0 | 53 | 48 | 83.3748 | 12418.2
2615 | 138382 | 0 | 52 | 47 | 79.6723 | 10784.1
2616 | 136930 | 0 | 51 | 47 | 79.0062 | 10785.5
2617 | 135865 | -6935.79 | 50 | 46 | 85.774 | 10786.9
2618 | 135000 | 0 | 50 | 46 | 78.9182 | 10788.3
2619 | 134298 | -9112.37 | 51 | 47 | 86.0914 | 10789.5
2620 | 137160 | 0 | 49 | 47 | 82.5974 | 11997.2
2621 | 183553 | -2155.08 | 49 | 47 | 125.709 | 14683.6
2622 | 329482 | -78914.9 | 52 | 50 | 239.446 | 39980.6
2623 | 452265 | -108471 | 53 | 51 | 274.434 | 43869.5
2624 | 481047 | -81828.7 | 53 | 51 | 270.726 | 55545.7
2625 | 523286 | -54422.2 | 57 | 54 | 273.757 | 86680.5
2626 | 555814 | -22017.7 | 62 | 57 | 267.075 | 88625.8
2627 | 549291 | -14408.7 | 64 | 57 | 253.906 | 88625
2628 | 615335 | -10875 | 67 | 59 | 259.275 | 88624.4
2629 | 814957 | -9213.53 | 73 | 62 | 294.578 | 88623.9
2630 | 880358 | -9087.78 | 73 | 62 | 284.926 | 86677.3
2631 | 874029 | -8630.7 | 70 | 61 | 284.447 | 78892.2
2632 | 851572 | -7802.03 | 72 | 60 | 281.738 | 65269.2
2633 | 699641 | -6983.9 | 69 | 58 | 252.225 | 49700.7
2634 | 447310 | -7823.96 | 61 | 59 | 178.658 | 30241.4
2635 | 189235 | 0 | 60 | 56 | 116.741 | 21485.3
2636 | 169708 | 0 | 58 | 56 | 103.222 | 20513.9
2637 | 156079 | 0 | 56 | 55 | 91.9479 | 12721.7
2638 | 144996 | 0 | 56 | 55 | 83.4504 | 12410.2
2639 | 140054 | 0 | 55 | 55 | 79.7482 | 10775
2640 | 138389 | 0 | 55 | 55 | 79.1916 | 10776
2641 | 137369 | 0 | 55 | 55 | 79.1448 | 10776.4
2642 | 136395 | 0 | 57 | 55 | 79.1005 | 10776.9
2643 | 135647 | 0 | 57 | 55 | 79.0664 | 10777.2
2644 | 138543 | 0 | 57 | 54 | 82.6602 | 11984
2645 | 185220 | 0 | 55 | 53 | 121.21 | 14669.9
2646 | 376149 | -32935.3 | 55 | 53 | 243.202 | 39966.3
2647 | 506179 | -24059 | 57 | 54 | 256.509 | 43854.8
2648 | 588002 | -19998.6 | 61 | 56 | 277.504 | 55537.1
2649 | 635460 | -14842.2 | 62 | 57 | 280.755 | 86672.6
2650 | 738505 | -10392.9 | 67 | 60 | 282.791 | 88618.4
2651 | 688659 | -9015.88 | 67 | 60 | 264.003 | 88617.8
2652 | 638807 | -8599.18 | 65 | 57 | 258.92 | 88617.8
2653 | 697655 | -9228.9 | 64 | 56 | 279.962 | 88617.7
2654 | 598178 | -9970.13 | 58 | 51 | 267.283 | 86671.5
2655 | 581899 | -10838.7 | 57 | 50 | 276.665 | 78886.8
2656 | 555846 | -12881 | 56 | 50 | 272.04 | 65264.2
2657 | 448931 | -15961.9 | 54 | 49 | 245.333 | 49696.3
2658 | 345818 | -49923.7 | 53 | 48 | 173.96 | 30237.3
2659 | 189253 | 0 | 52 | 48 | 117.064 | 21481.7
2660 | 169308 | 0 | 51 | 47 | 103.204 | 20510.8
2661 | 155770 | 0 | 50 | 46 | 91.9337 | 12719.4
2662 | 144566 | 0 | 49 | 45 | 83.4309 | 12408.3
2663 | 139704 | -5256.62 | 48 | 45 | 86.1664 | 10774
2664 | 137610 | 0 | 47 | 44 | 75.1042 | 10775.6
2665 | 136526 | 0 | 46 | 43 | 79.0649 | 10777.1
2666 | 135656 | 0 | 45 | 43 | 75.0145 | 10779.2
2667 | 134669 | -11807.2 | 43 | 42 | 82.6824 | 10780.9
2668 | 133536 | 0 | 40 | 39 | 74.9186 | 10782.8
2669 | 132814 | -16238.9 | 40 | 38 | 82.211 | 10784.5
2670 | 155547 | -7200.33 | 39 | 37 | 78.5891 | 10786.4
2671 | 152451 | -336556 | 38 | 37 | 89.5048 | 10788.4
2672 | 171043 | -356370 | 38 | 37 | 93.5454 | 10790.5
2673 | 170414 | -316571 | 39 | 37 | 90.8025 | 10794.1
2674 | 174068 | -300798 | 40 | 37 | 89.5033 | 10794.8
2675 | 179683 | -288780 | 41 | 38 | 88.5937 | 10796.4
2676 | 140507 | -289731 | 36 | 36 | 88.223 | 10797.6
2677 | 168142 | -285461 | 40 | 37 | 88.2172 | 10798.8
2678 | 132721 | 0 | 40 | 37 | 75.3945 | 10799.9
2679 | 126146 | 0 | 40 | 37 | 70.899 | 10801.1
2680 | 125777 | -18428.9 | 40 | 37 | 78.0397 | 10801.7
2681 | 125380 | -6776.38 | 40 | 37 | 76.3928 | 10803
2682 | 148890 | -14160.9 | 40 | 36 | 86.2768 | 10804.2
2683 | 143599 | -12645.2 | 40 | 35 | 88.8361 | 10805.9
2684 | 155785 | -17846.8 | 40 | 35 | 92.7787 | 10807.5
2685 | 152782 | -19624.6 | 39 | 35 | 92.6201 | 10809.4
2686 | 150925 | -21857.4 | 39 | 35 | 91.9488 | 10811.7
2687 | 149105 | -24588.2 | 37 | 34 | 91.3253 | 10814.4
2688 | 146709 | -27731.3 | 35 | 31 | 86.8172 | 4006.33
2689 | 144950 | -32259.5 | 34 | 30 | 87.3352 | 4008.67
2690 | 143455 | -40008.3 | 34 | 31 | 87.5684 | 4011.14
2691 | 142203 | -47632.7 | 34 | 31 | 87.5741 | 4013.7
2692 | 141186 | -55041.4 | 34 | 31 | 87.4828 | 4016.31
2693 | 140391 | -62527 | 34 | 31 | 86.2109 | 4018.81
2694 | 139658 | -64198.4 | 35 | 32 | 83.4884 | 4021.22
2695 | 139451 | -64689.6 | 35 | 32 | 81.5 | 4023.49
2696 | 138957 | -55318.2 | 36 | 33 | 81.4806 | 4025.7
2697 | 140526 | -49522.4 | 36 | 33 | 82.0368 | 4027.81
2698 | 139542 | -37587.4 | 40 | 35 | 81.201 | 4029.79
2699 | 142919 | -32060.6 | 42 | 37 | 81.3316 | 4031.44
2700 | 140657 | -26339.6 | 43 | 37 | 80.3433 | 4032.95
2701 | 142997 | -23765.8 | 47 | 40 | 80.1099 | 4034.3
2702 | 143303 | -20038 | 50 | 40 | 79.8298 | 4035.38
2703 | 133150 | -11323.7 | 53 | 42 | 76.6467 | 4036.32
2704 | 131408 | -10654.8 | 55 | 42 | 76.8549 | 4036.92
2705 | 119487 | -6270.46 | 55 | 41 | 75.4626 | 4037
2706 | 147642 | -2729.47 | 53 | 41 | 81.6905 | 4037.08
2707 | 144501 | -16385.4 | 49 | 38 | 89.4068 | 4037.62
2708 | 141518 | -16169 | 39 | 33 | 89.3883 | 4037.95
2709 | 138715 | -26541.8 | 38 | 32 | 89.2705 | 4039.3
2710 | 137331 | -37350.5 | 36 | 32 | 89.4765 | 4040.56
2711 | 135790 | -41761.1 | 37 | 32 | 88.4363 | 4042.51
2712 | 142272 | -53352 | 34 | 29 | 93.0665 | 10854.7
2713 | 134771 | -49601.9 | 36 | 30 | 90.7484 | 10856.6
2714 | 143853 | -67723.5 | 33 | 28 | 93.3171 | 10857.7
2715 | 133647 | -63507.6 | 33 | 28 | 90.6102 | 10858.5
2716 | 138562 | -86036.3 | 27 | 24 | 95.5542 | 12066.5
2717 | 183867 | -70400.9 | 26 | 24 | 134.27 | 14752.6
2718 | 314107 | -663051 | 30 | 28 | 249.74 | 40049.4
2719 | 376611 | -539877 | 35 | 31 | 277.636 | 43938.5
2720 | 413627 | -386801 | 38 | 32 | 266.35 | 55600.7
2721 | 455251 | -306068 | 45 | 36 | 269.8 | 86731.5
2722 | 422896 | -221582 | 50 | 38 | 260.485 | 88674.9
2723 | 411094 | -180998 | 52 | 40 | 246.643 | 88670.2
2724 | 388292 | -137625 | 54 | 40 | 244.913 | 88667.2
2725 | 434595 | -88323 | 58 | 41 | 264.651 | 88664
2726 | 468833 | -54579.6 | 60 | 43 | 269.588 | 86714.6
2727 | 477751 | -32419.6 | 61 | 43 | 270.882 | 78926.9
2728 | 473716 | -27342.9 | 61 | 45 | 265.76 | 65301.2
2729 | 436332 | -26151.1 | 61 | 45 | 243.557 | 49730.9
2730 | 325521 | -63942.5 | 61 | 45 | 170.391 | 30270
2731 | 181553 | 0 | 57 | 43 | 114.172 | 21512.7
2732 | 161979 | 0 | 56 | 43 | 102.867 | 20540.1
2733 | 148866 | 0 | 55 | 42 | 91.618 | 12754.7
2734 | 138117 | 0 | 55 | 43 | 83.1373 | 12444.1
2735 | 133373 | 0 | 53 | 42 | 79.4449 | 10810.7
2736 | 132075 | 0 | 53 | 42 | 78.4799 | 10812.3
2737 | 131324 | -6669.81 | 53 | 42 | 85.0823 | 10813.6
2738 | 130592 | 0 | 52 | 41 | 78.4124 | 10814.8
2739 | 130072 | -8133.96 | 52 | 41 | 85.0554 | 10815.7
2740 | 133268 | 0 | 51 | 42 | 82.4207 | 12023.1
2741 | 179994 | -9878.59 | 51 | 42 | 128.951 | 14709.2
2742 | 325439 | -153959 | 52 | 43 | 238.389 | 40006
2743 | 425449 | -169849 | 52 | 43 | 264.491 | 43894.7
2744 | 444729 | -82336.7 | 56 | 46 | 270.573 | 55565.5
2745 | 463664 | -54274.3 | 59 | 47 | 272.188 | 86697.5
2746 | 480080 | -27102.8 | 63 | 50 | 262.525 | 88641.7
2747 | 477656 | -19692.1 | 64 | 51 | 247.934 | 88639.8
2748 | 566658 | -16569.9 | 67 | 53 | 255.728 | 88638.3
2749 | 634043 | -13368.3 | 68 | 53 | 277.824 | 88637.2
2750 | 718830 | -11703.9 | 70 | 55 | 290.953 | 86690
2751 | 809125 | -12518.9 | 73 | 57 | 307.18 | 78904.5
2752 | 805540 | -11874.7 | 74 | 57 | 301.639 | 65281.6
2753 | 742616 | -9793.18 | 74 | 57 | 273.923 | 49712.9
2754 | 504812 | -14863 | 73 | 57 | 174.739 | 30252.6
2755 | 188221 | 0 | 66 | 54 | 113.197 | 21495.8
2756 | 168158 | 0 | 59 | 51 | 101.613 | 20523.9
2757 | 155091 | 0 | 58 | 52 | 91.9023 | 12733.2
2758 | 143827 | 0 | 55 | 51 | 83.3973 | 12421.2
2759 | 138802 | 0 | 52 | 49 | 79.6914 | 10786.4
2760 | 137228 | 0 | 50 | 48 | 79.1388 | 10786.9
2761 | 136218 | 0 | 49 | 47 | 79.0925 | 10787.5
2762 | 135400 | 0 | 48 | 47 | 79.0553 | 10788.1
2763 | 134412 | 0 | 47 | 46 | 79.0106 | 10788.5
2764 | 137189 | 0 | 46 | 45 | 82.5988 | 11995.4
2765 | 183640 | 0 | 45 | 45 | 121.137 | 14681.1
2766 | 328908 | -48406.3 | 47 | 46 | 235.393 | 39977.4
2767 | 473654 | -77280.6 | 51 | 48 | 264.74 | 43865.7
2768 | 515557 | -41105 | 57 | 51 | 271.493 | 55545.1
2769 | 616933 | -15382.9 | 64 | 55 | 281.159 | 86680
2770 | 740250 | -11532.2 | 70 | 58 | 285.927 | 88625.2
2771 | 772347 | -8927.79 | 76 | 60 | 277.367 | 88624.3
2772 | 927057 | -23136.7 | 78 | 62 | 282.282 | 88623.7
2773 | 1008010 | -7221.23 | 79 | 62 | 312.163 | 88624.1
2774 | 1084730 | -6446.93 | 81 | 63 | 323.549 | 86678.2
2775 | 1178750 | -7719.72 | 81 | 64 | 330.269 | 78894.1
2776 | 1163830 | -12156.5 | 81 | 64 | 323.573 | 65271.6
2777 | 1083840 | -16955.4 | 79 | 64 | 294.971 | 49703.3
2778 | 723599 | -11342.8 | 77 | 64 | 187.323 | 30243.5
2779 | 191111 | 0 | 73 | 62 | 115.443 | 21486.4
2780 | 170834 | 0 | 68 | 60 | 102.31 | 20514.1
2781 | 157703 | 0 | 69 | 61 | 92.698 | 12720.2
2782 | 146507 | 0 | 67 | 60 | 83.2709 | 12407.3
2783 | 141454 | 0 | 65 | 59 | 79.479 | 10771.5
2784 | 139919 | 0 | 64 | 59 | 79.0314 | 10771.4
2785 | 139071 | 0 | 65 | 60 | 79.555 | 10771.2
2786 | 138235 | 0 | 63 | 60 | 78.6574 | 10770.9
2787 | 137033 | 0 | 63 | 58 | 79.12 | 10770.5
2788 | 140014 | 0 | 61 | 56 | 82.2514 | 11976.5
2789 | 186640 | 0 | 57 | 54 | 121.016 | 14661.4
2790 | 615549 | -10510.4 | 62 | 56 | 256.32 | 39957
2791 | 709022 | -13724.4 | 64 | 56 | 285.632 | 43845.1
2792 | 759185 | -9847.12 | 68 | 57 | 294.766 | 55532.3
2793 | 791740 | -9181.02 | 66 | 58 | 277.832 | 86668.5
2794 | 753595 | -8129.06 | 62 | 58 | 277.657 | 88614.5
2795 | 784898 | -6821.89 | 67 | 61 | 269.533 | 88614.3
2796 | 956344 | -7460.02 | 75 | 63 | 293.86 | 88614.4
2797 | 1157040 | -4849.29 | 81 | 66 | 322.241 | 88614.7
2798 | 1158660 | -5227.35 | 80 | 66 | 328.227 | 86669.5
2799 | 1196110 | -4887.94 | 80 | 66 | 331.844 | 78885.8
2800 | 1211690 | -4106.4 | 78 | 66 | 327.212 | 65262.9
2801 | 1166590 | -4063.36 | 79 | 66 | 279.631 | 49694.8
2802 | 794890 | -14884.7 | 77 | 65 | 191.423 | 30235.7
2803 | 192352 | 0 | 75 | 64 | 116.121 | 21479.1
2804 | 172048 | 0 | 72 | 63 | 103.102 | 20507.4
2805 | 158555 | 0 | 70 | 62 | 91.9692 | 12712.2
2806 | 147746 | 0 | 69 | 63 | 83.6813 | 12399
2807 | 142635 | 0 | 69 | 63 | 80.2283 | 10762.7
2808 | 141171 | 0 | 70 | 64 | 79.9924 | 10762.5
2809 | 140153 | 0 | 70 | 64 | 79.6704 | 10762.3
2810 | 139332 | 0 | 69 | 64 | 79.3179 | 10762.1
2811 | 138190 | 0 | 65 | 62 | 78.3235 | 10761.8
2812 | 141051 | 0 | 61 | 59 | 81.7888 | 11967.8
2813 | 187513 | 0 | 57 | 56 | 121.057 | 14652.8
2814 | 658443 | -9409.22 | 57 | 57 | 256.104 | 39948.6
2815 | 889864 | -12344.3 | 65 | 61 | 296.576 | 43836.6
2816 | 912983 | -9553.83 | 66 | 62 | 285.61 | 55526.4
2817 | 955862 | -7889.68 | 69 | 61 | 288.852 | 86663.4
2818 | 1018550 | -8285.28 | 70 | 62 | 287.749 | 88609.7
2819 | 902453 | -4645.58 | 73 | 62 | 286.672 | 88611.2
2820 | 945456 | -4339.56 | 76 | 62 | 291.062 | 88611.4
2821 | 1110680 | -4428.48 | 79 | 63 | 316.273 | 88610.9
2822 | 1164470 | -6399.56 | 79 | 63 | 325.686 | 86665.4
2823 | 1228960 | -11385.9 | 81 | 63 | 320.532 | 78882.2
2824 | 1209400 | -20663.6 | 82 | 62 | 325.33 | 65260.5
2825 | 1013730 | -15952.5 | 77 | 60 | 273.7 | 49692.9
2826 | 671341 | -7940.12 | 76 | 60 | 185.79 | 30233.7
2827 | 193162 | 0 | 70 | 60 | 116.054 | 21477
2828 | 173098 | 0 | 71 | 62 | 104.213 | 20504.8
2829 | 159952 | 0 | 70 | 64 | 92.3102 | 12709.2
2830 | 147864 | 0 | 68 | 60 | 83.3766 | 12395.8
2831 | 142475 | 0 | 69 | 56 | 80.4916 | 10759.2
2832 | 141127 | 0 | 64 | 55 | 74.1156 | 10758.9
2833 | 140037 | 0 | 63 | 55 | 75.066 | 10758.6
2834 | 139133 | 0 | 62 | 55 | 74.9879 | 10759
2835 | 138160 | 0 | 61 | 54 | 74.9081 | 10759.3
2836 | 137268 | 0 | 60 | 53 | 74.8332 | 10759.7
2837 | 136526 | 0 | 57 | 52 | 73.8539 | 10760
2838 | 135739 | 0 | 56 | 52 | 70.9649 | 10760.4
2839 | 249385 | -8252.47 | 60 | 55 | 89.3087 | 10760.6
2840 | 264048 | -12061.2 | 64 | 55 | 92.7364 | 10760.9
2841 | 279056 | -16162 | 66 | 55 | 93.554 | 10773.3
2842 | 319537 | -17092.2 | 69 | 57 | 97.3008 | 10774.7
2843 | 360201 | -17235.7 | 73 | 59 | 101.431 | 10776.1
2844 | 388189 | -17098.2 | 76 | 59 | 101.424 | 10776.8
2845 | 424895 | -21070.6 | 76 | 58 | 101.99 | 10777.3
2846 | 131509 | 0 | 76 | 58 | 72.5432 | 10777.9
2847 | 193902 | 0 | 76 | 59 | 82.6793 | 10778.4
2848 | 130722 | 0 | 73 | 57 | 70.5753 | 10772.3
2849 | 130534 | 0 | 72 | 56 | 71.2552 | 10769.5
2850 | 130440 | 0 | 69 | 56 | 74.2144 | 10767.1
2851 | 130027 | 0 | 64 | 55 | 77.1238 | 10765.5
2852 | 129463 | 0 | 60 | 53 | 78.538 | 10764.7
2853 | 129040 | 0 | 56 | 51 | 79.53 | 10764.2
2854 | 128547 | 0 | 54 | 49 | 78.7078 | 10764.3
2855 | 128149 | 0 | 52 | 47 | 77.8897 | 10764.8
2856 | 127640 | 0 | 50 | 45 | 73.3749 | 3955.29
2857 | 127247 | 0 | 49 | 44 | 73.357 | 3956.26
2858 | 126900 | 0 | 46 | 43 | 73.3413 | 3957.56
2859 | 127553 | -5307.6 | 44 | 41 | 79.4533 | 3958.91
2860 | 125935 | 0 | 43 | 41 | 73.2986 | 3960.33
2861 | 125416 | 0 | 40 | 39 | 76.085 | 3961.89
2862 | 125040 | 0 | 42 | 40 | 69.0248 | 3963.69
2863 | 124752 | -1475.95 | 45 | 41 | 71.4532 | 3965.36
2864 | 124539 | 0 | 48 | 43 | 67.1189 | 3967.32
2865 | 124239 | -1530.28 | 51 | 44 | 71.8885 | 3968.64
2866 | 123857 | 0 | 52 | 43 | 67.4425 | 3968.99
2867 | 124069 | 0 | 54 | 46 | 67.4516 | 3968.87
2868 | 123807 | 0 | 56 | 47 | 67.4401 | 3968.47
2869 | 128072 | -5320.75 | 60 | 48 | 73.889 | 3967.9
2870 | 123763 | 0 | 63 | 50 | 68.3191 | 3967.5
2871 | 123730 | 0 | 65 | 51 | 68.1308 | 3967.26
2872 | 123953 | 0 | 65 | 53 | 67.6176 | 3966.87
2873 | 123553 | 0 | 65 | 52 | 69.6003 | 3966.55
2874 | 123661 | 0 | 62 | 51 | 72.3393 | 3966.01
2875 | 123439 | 0 | 58 | 49 | 75.6041 | 3965.7
2876 | 123376 | 0 | 53 | 47 | 77.1398 | 3965.52
2877 | 123297 | 0 | 51 | 47 | 77.1363 | 3965.81
2878 | 123065 | 0 | 49 | 46 | 76.3259 | 3966.47
2879 | 130480 | -7932.14 | 47 | 45 | 82.1734 | 3967.52
2880 | 122915 | 0 | 48 | 45 | 78.4954 | 10778.9
2881 | 123237 | 0 | 47 | 45 | 78.504 | 9951.91
2882 | 125131 | -8363.95 | 47 | 46 | 84.7384 | 9952.26
2883 | 130883 | -3747.64 | 47 | 46 | 83.2744 | 9952.86
2884 | 157123 | -4562.25 | 47 | 45 | 91.7307 | 11057.3
2885 | 182376 | -3992.16 | 46 | 44 | 123.671 | 13514.9
2886 | 332712 | -81147.5 | 45 | 43 | 236.462 | 36658.3
2887 | 440632 | -170281 | 44 | 42 | 265.248 | 40216
2888 | 461172 | -156341 | 44 | 42 | 271.196 | 50900.5
2889 | 474628 | -159570 | 44 | 43 | 272.078 | 79385.8
2890 | 448586 | -116525 | 48 | 44 | 262.491 | 81166.6
2891 | 461282 | -97650.1 | 51 | 46 | 250.183 | 81166.8
2892 | 450456 | -54819.2 | 55 | 47 | 245.203 | 81166.3
2893 | 513948 | -31160.9 | 57 | 47 | 265.745 | 81165.6
2894 | 579988 | -16011.3 | 59 | 47 | 277.142 | 79384.9
2895 | 634666 | -13346.3 | 61 | 46 | 283.132 | 72262.6
2896 | 620262 | -12610.2 | 60 | 46 | 276.777 | 59799.6
2897 | 533379 | -11533.7 | 59 | 46 | 249.357 | 45556.6
2898 | 356243 | -11478.8 | 58 | 45 | 167.298 | 27753.9
2899 | 184017 | 0 | 54 | 45 | 107.588 | 19743.4
2900 | 164183 | 0 | 51 | 43 | 99.7684 | 18855
2901 | 151004 | 0 | 47 | 41 | 91.7156 | 11726.1
2902 | 140165 | 0 | 45 | 41 | 83.2304 | 11441.3
2903 | 135302 | 0 | 44 | 40 | 79.5324 | 9946.07
2904 | 134035 | -7845.88 | 42 | 39 | 82.9976 | 9947.63
2905 | 132945 | 0 | 40 | 38 | 78.5192 | 9948.82
2906 | 132134 | -14676.8 | 39 | 37 | 86.6669 | 9950.46
2907 | 131395 | -4123.26 | 37 | 36 | 82.8776 | 9952.21
2908 | 135739 | -11244.8 | 38 | 37 | 87.368 | 11057.7
2909 | 207537 | -11189.4 | 38 | 37 | 131.166 | 13516.3
2910 | 331320 | -149616 | 39 | 38 | 232.279 | 36660.7
2911 | 442318 | -208887 | 44 | 43 | 262.677 | 40219.2
2912 | 458538 | -123089 | 50 | 47 | 272.359 | 50902.8
2913 | 498778 | -74967 | 55 | 52 | 277.173 | 79387.8
2914 | 488808 | -36268.3 | 58 | 52 | 262.295 | 81167.2
2915 | 474787 | -19095.2 | 60 | 51 | 247.175 | 81166.3
2916 | 546287 | -20870.1 | 63 | 51 | 253.531 | 81165.7
2917 | 616430 | -11733.8 | 64 | 52 | 275.628 | 81165.5
2918 | 698980 | -10949 | 66 | 52 | 287.74 | 79384.7
2919 | 737924 | -10243.5 | 67 | 53 | 278.467 | 72262.5
2920 | 718699 | -9693.95 | 66 | 53 | 281.527 | 59799.4
2921 | 621915 | -8635.93 | 65 | 53 | 252.059 | 45556.4
2922 | 425633 | -8276.62 | 64 | 53 | 170.773 | 27753.6
2923 | 188390 | 0 | 63 | 52 | 108.183 | 19743.1
2924 | 168734 | 0 | 62 | 52 | 99.8063 | 18854.6
2925 | 155329 | 0 | 61 | 52 | 91.6962 | 11724.3
2926 | 144282 | 0 | 61 | 52 | 83.4556 | 11438.8
2927 | 139468 | 0 | 60 | 52 | 79.4667 | 9942.74
2928 | 137923 | 0 | 60 | 52 | 79.1703 | 9943.44
2929 | 137052 | 0 | 60 | 52 | 79.1303 | 9944.01
2930 | 136314 | 0 | 59 | 52 | 79.0967 | 9944.54
2931 | 135366 | 0 | 59 | 51 | 79.0538 | 9945
2932 | 138647 | 0 | 59 | 51 | 81.0647 | 11049.1
2933 | 185489 | 0 | 59 | 51 | 119.222 | 13506.2
2934 | 392415 | -28296.9 | 59 | 51 | 244.524 | 36649.1
2935 | 562491 | -16907.7 | 61 | 53 | 259.504 | 40206.1
2936 | 617544 | -15960.9 | 63 | 54 | 269.321 | 50896
2937 | 689225 | -11690.3 | 65 | 56 | 272.916 | 79380.8
2938 | 729551 | -9486.3 | 66 | 57 | 266.86 | 81161
2939 | 704994 | -8257.26 | 66 | 58 | 251.863 | 81160.7
2940 | 726293 | -7659.32 | 67 | 59 | 252.781 | 81160.7
2941 | 842759 | -8476.31 | 65 | 60 | 274.951 | 81160.8
2942 | 847443 | -11529.4 | 63 | 60 | 281.094 | 79380.4
2943 | 839175 | -13998.1 | 61 | 60 | 282.837 | 72258.5
2944 | 857556 | -14884.6 | 61 | 61 | 281.94 | 59795.6
2945 | 755410 | -12589.9 | 62 | 61 | 256.351 | 45553
2946 | 490991 | -10419.5 | 62 | 61 | 174.051 | 27750.6
2947 | 190772 | 0 | 61 | 61 | 109.637 | 19740.3
2948 | 170743 | 0 | 61 | 61 | 100.115 | 18851.9
2949 | 157119 | 0 | 60 | 60 | 91.7389 | 11721
2950 | 146079 | 0 | 62 | 60 | 84.096 | 11435.5
2951 | 141156 | 0 | 63 | 60 | 80.1714 | 9939.15
2952 | 139539 | 0 | 65 | 60 | 79.8415 | 9939.69
2953 | 138750 | 0 | 64 | 60 | 78.9765 | 9940.01
2954 | 137775 | 0 | 63 | 59 | 78.8949 | 9940.24
2955 | 136962 | 0 | 62 | 58 | 78.8217 | 9940.27
2956 | 140181 | 0 | 62 | 58 | 81.2082 | 11044
2957 | 187161 | 0 | 62 | 58 | 119.4 | 13500.7
2958 | 573040 | -20379.4 | 62 | 58 | 251.809 | 36643.3
2959 | 771878 | -14220.6 | 64 | 60 | 286.327 | 40200.1
2960 | 815399 | -11879.2 | 65 | 61 | 279.488 | 50892.3
2961 | 906347 | -11493.7 | 67 | 62 | 284.796 | 79377.3
2962 | 960079 | -10177 | 68 | 63 | 279.62 | 81158
2963 | 870138 | -6965.12 | 68 | 63 | 261.295 | 81158.4
2964 | 902409 | -6495 | 69 | 64 | 262.739 | 81158.5
2965 | 994172 | -7350.15 | 68 | 64 | 303.717 | 81158.3
2966 | 1038850 | -13586.2 | 66 | 65 | 315.95 | 79378
2967 | 1046060 | -15324.9 | 65 | 65 | 318.46 | 72256.2
2968 | 1005460 | -16102.7 | 64 | 64 | 310.421 | 59793.4
2969 | 887699 | -13694.9 | 64 | 64 | 278.552 | 45550.9
2970 | 562705 | -11746.9 | 63 | 63 | 178.424 | 27748.5
2971 | 191614 | 0 | 63 | 63 | 110.305 | 19738.2
2972 | 171384 | 0 | 62 | 62 | 99.9189 | 18850
2973 | 158071 | 0 | 62 | 62 | 92.1228 | 11718.3
2974 | 146635 | 0 | 60 | 60 | 83.0148 | 11432.6
2975 | 141548 | 0 | 57 | 57 | 79.8163 | 9936.05
2976 | 139806 | 0 | 55 | 55 | 79.256 | 9936.53
2977 | 138688 | 0 | 54 | 53 | 79.2047 | 9936.98
2978 | 137884 | 0 | 52 | 52 | 79.168 | 9937.63
2979 | 136848 | 0 | 51 | 50 | 79.1211 | 9938.4
2980 | 139873 | 0 | 51 | 50 | 81.1205 | 11042.9
2981 | 186196 | 0 | 51 | 49 | 119.255 | 13500.5
2982 | 365793 | -35750.5 | 51 | 49 | 235.839 | 36644
2983 | 459932 | -41492.4 | 52 | 49 | 263.149 | 40201.6
2984 | 518340 | -53159.6 | 54 | 50 | 271.175 | 50892.6
2985 | 543384 | -34435.9 | 55 | 51 | 272.571 | 79377.9
2986 | 561994 | -23398.2 | 57 | 52 | 266.166 | 81158.5
2987 | 556823 | -15853 | 59 | 53 | 251.731 | 81158.4
2988 | 596190 | -12222.1 | 61 | 54 | 253.45 | 81158.4
2989 | 670247 | -14292.8 | 62 | 54 | 273.575 | 81158.7
2990 | 734039 | -15993 | 64 | 54 | 299.064 | 79378.4
2991 | 791375 | -16477.7 | 65 | 54 | 304.367 | 72256.5
2992 | 764958 | -16087.5 | 65 | 53 | 297.402 | 59793.8
2993 | 663943 | -13655.8 | 64 | 52 | 267.405 | 45551.1
2994 | 453723 | -10648.6 | 64 | 51 | 168.292 | 27748.6
2995 | 190628 | 0 | 61 | 48 | 106.626 | 19738.3
2996 | 170904 | 0 | 57 | 46 | 99.8192 | 18850
2997 | 157223 | 0 | 54 | 43 | 92.0003 | 11718.7
2998 | 146230 | 0 | 53 | 43 | 83.5065 | 11433.2
2999 | 141249 | 0 | 51 | 42 | 79.8026 | 9937.22
3000 | 139269 | 0 | 50 | 41 | 75.1795 | 9938.37
3001 | 138207 | 0 | 48 | 40 | 75.1305 | 9939.49
3002 | 137263 | -6335.29 | 47 | 39 | 81.7424 | 9941.35
3003 | 136145 | 0 | 45 | 38 | 75.0369 | 9942.89
3004 | 135376 | -1209.88 | 44 | 38 | 77.8306 | 9944.54
3005 | 134400 | 0 | 42 | 37 | 71.7528 | 9946.26
3006 | 133598 | -13075.2 | 41 | 36 | 77.0294 | 9947.92
3007 | 168423 | -177086 | 44 | 38 | 85.1244 | 9949.77
3008 | 221868 | -216190 | 46 | 40 | 88.6907 | 9951.31
3009 | 210896 | -178341 | 49 | 41 | 89.0332 | 9956.45
3010 | 211787 | -152811 | 52 | 42 | 89.5427 | 9957.75
3011 | 213372 | -125492 | 54 | 43 | 90.1713 | 9959.12
3012 | 210783 | -95255.6 | 57 | 44 | 89.3073 | 9960
3013 | 210148 | -76720.9 | 59 | 45 | 88.1009 | 9960.69
3014 | 129083 | 0 | 60 | 46 | 70.895 | 9961.31
3015 | 128882 | 0 | 62 | 47 | 71.8803 | 9961.97
3016 | 128613 | 0 | 61 | 47 | 70.2461 | 9959.45
3017 | 128368 | 0 | 61 | 46 | 69.0112 | 9958
3018 | 128098 | 0 | 60 | 46 | 68.7141 | 9957.26
3019 | 127906 | 0 | 56 | 45 | 71.8619 | 9956.84
3020 | 127472 | 0 | 52 | 43 | 76.2592 | 9956.88
3021 | 127088 | 0 | 48 | 41 | 79.4417 | 9957.09
3022 | 127873 | -5858.13 | 46 | 40 | 83.1052 | 9957.73
3023 | 126322 | 0 | 44 | 39 | 77.808 | 9958.72
3024 | 125872 | -12310.8 | 42 | 38 | 80.9833 | 3729.43
3025 | 125377 | 0 | 41 | 37 | 73.2726 | 3730.94
3026 | 125130 | -16758.5 | 39 | 37 | 81.7744 | 3732.6
3027 | 124532 | -5403.07 | 38 | 36 | 77.6633 | 3734.42
3028 | 126037 | -12775.1 | 38 | 36 | 76.1297 | 3736.21
3029 | 148314 | -12405.2 | 37 | 36 | 80.5892 | 3738.23
3030 | 144809 | -14034.6 | 37 | 36 | 77.8051 | 3740.29
3031 | 123217 | -12008.7 | 42 | 39 | 73.4591 | 3742.4
3032 | 126302 | -11731.6 | 47 | 42 | 73.4364 | 3744.43
3033 | 122876 | -7380.41 | 52 | 44 | 73.4368 | 3745.68
3034 | 122751 | 0 | 55 | 45 | 67.3924 | 3745.96
3035 | 122815 | -10106.4 | 59 | 47 | 73.999 | 3745.89
3036 | 122764 | 0 | 62 | 48 | 67.9712 | 3745.03
3037 | 122872 | 0 | 63 | 49 | 67.756 | 3744.3
3038 | 122846 | 0 | 64 | 49 | 67.7905 | 3743.61
3039 | 123031 | 0 | 65 | 50 | 67.836 | 3742.86
3040 | 122929 | 0 | 64 | 49 | 67.2762 | 3742.1
3041 | 122952 | 0 | 63 | 48 | 67.2455 | 3741.35
3042 | 123069 | 0 | 62 | 48 | 67.2852 | 3740.74
3043 | 123095 | 0 | 59 | 47 | 69.4037 | 3740.34
3044 | 122872 | 0 | 56 | 45 | 73.9172 | 3740.2
3045 | 122885 | 0 | 53 | 44 | 77.1176 | 3740.27
3046 | 128676 | -7172.09 | 51 | 43 | 83.0479 | 3740.72
3047 | 134114 | -3370.17 | 50 | 43 | 80.4503 | 3741.41
3048 | 128755 | -3394.26 | 48 | 42 | 83.1864 | 9972.82
3049 | 126828 | -3521.98 | 48 | 42 | 83.0968 | 9973.87
3050 | 123984 | -5445.47 | 49 | 42 | 84.6912 | 9974.12
3051 | 124095 | -5263.2 | 49 | 42 | 84.7041 | 9974.87
3052 | 151161 | -6562.49 | 49 | 42 | 91.2156 | 11079.4
3053 | 176137 | -5524.38 | 49 | 42 | 123.358 | 13536.8
3054 | 332230 | -119302 | 49 | 42 | 233.91 | 36680.1
3055 | 427736 | -152504 | 50 | 43 | 263.879 | 40237.5
3056 | 447656 | -113838 | 51 | 44 | 272.219 | 50917.2
3057 | 458701 | -101143 | 52 | 45 | 272.697 | 79399.5
3058 | 441860 | -84026.6 | 53 | 46 | 259.818 | 81178.3
3059 | 445071 | -80352.7 | 54 | 47 | 244.703 | 81177
3060 | 431156 | -64862.3 | 55 | 48 | 242.622 | 81176
3061 | 487019 | -56563.1 | 56 | 48 | 263.207 | 81175.4
3062 | 501569 | -40306 | 56 | 49 | 270.339 | 79394.5
3063 | 500222 | -23737 | 57 | 49 | 271.841 | 72272
3064 | 507994 | -15585.7 | 58 | 50 | 268.178 | 59808.7
3065 | 452573 | -15063.5 | 58 | 50 | 242.803 | 45565.5
3066 | 349995 | -35902.6 | 59 | 50 | 166.501 | 27762.4
3067 | 183859 | 0 | 58 | 50 | 107.098 | 19751.5
3068 | 164285 | 0 | 56 | 50 | 99.7406 | 18862.8
3069 | 151058 | 0 | 55 | 50 | 91.7181 | 11735.5
3070 | 140056 | 0 | 53 | 49 | 83.2256 | 11450.5
3071 | 135359 | 0 | 51 | 48 | 79.5349 | 9955.27
3072 | 133979 | 0 | 49 | 47 | 78.5663 | 9956.53
3073 | 133127 | -7744.75 | 48 | 46 | 85.2027 | 9957.77
3074 | 132527 | 0 | 46 | 46 | 78.4999 | 9958.99
3075 | 131696 | -10812.9 | 45 | 45 | 85.7288 | 9960.23
3076 | 134654 | 0 | 45 | 45 | 80.8837 | 11065.2
3077 | 181221 | -13775.8 | 45 | 45 | 128.139 | 13523.1
3078 | 339187 | -109379 | 45 | 45 | 230.954 | 36667
3079 | 448546 | -159311 | 48 | 47 | 264.553 | 40224.8
3080 | 463029 | -112728 | 50 | 49 | 272.81 | 50907.4
3081 | 496572 | -88202.4 | 53 | 51 | 276.677 | 79391.9
3082 | 485461 | -44950.9 | 57 | 53 | 260.876 | 81171.4
3083 | 490366 | -23145.4 | 61 | 55 | 248.282 | 81170.6
3084 | 547930 | -13767.1 | 65 | 57 | 254.131 | 81170.2
3085 | 579044 | -11673.9 | 62 | 55 | 269.502 | 81169.9
3086 | 573982 | -11762 | 58 | 53 | 274.863 | 79389.1
3087 | 526312 | -12789 | 55 | 51 | 273.154 | 72266.6
3088 | 495797 | -18641.2 | 54 | 49 | 267.675 | 59803.4
3089 | 425436 | -39414.9 | 52 | 48 | 241.285 | 45560.4
3090 | 348668 | -92480.9 | 51 | 46 | 171.468 | 27757.8
3091 | 187134 | 0 | 49 | 44 | 113.435 | 19747.3
3092 | 167441 | 0 | 46 | 41 | 99.885 | 18859.1
3093 | 154016 | 0 | 44 | 39 | 91.8534 | 11731.7
3094 | 142900 | -9161.18 | 42 | 37 | 91.2017 | 11447.5
3095 | 137888 | 0 | 39 | 35 | 79.6499 | 9952.92
3096 | 136220 | -16531.4 | 37 | 33 | 87.9651 | 9955.07
3097 | 135230 | -6077.12 | 36 | 32 | 83.4765 | 9957.28
3098 | 135635 | -13828.9 | 34 | 31 | 86.2922 | 9959.37
3099 | 157401 | -14087.9 | 33 | 30 | 89.7551 | 9961.66
3100 | 156846 | -18567.6 | 33 | 29 | 92.1625 | 11067.6
3101 | 216186 | -26326.2 | 32 | 29 | 134.671 | 13526.6
3102 | 326670 | -399890 | 32 | 28 | 228.814 | 36671.5
3103 | 388950 | -345302 | 35 | 30 | 277.855 | 40231.4
3104 | 407213 | -260216 | 37 | 31 | 283.728 | 50912.6
3105 | 437297 | -238988 | 40 | 32 | 286.089 | 79397
3106 | 453145 | -208831 | 44 | 36 | 279.773 | 81177.3
3107 | 441949 | -154135 | 49 | 38 | 266.988 | 81176.2
3108 | 416554 | -99081.6 | 53 | 40 | 246.972 | 81174.7
3109 | 477001 | -73916.9 | 55 | 42 | 265.708 | 81173.5
3110 | 515934 | -38289.6 | 58 | 43 | 271.407 | 79391.8
3111 | 527040 | -17231 | 60 | 44 | 274.032 | 72269.2
3112 | 521854 | -14478.3 | 59 | 44 | 269.243 | 59805.7
3113 | 464947 | -13610.3 | 58 | 43 | 243.806 | 45562.5
3114 | 352994 | -40661.7 | 57 | 42 | 166.587 | 27759.5
3115 | 188045 | 0 | 54 | 41 | 110.653 | 19748.7
3116 | 168257 | 0 | 52 | 40 | 102.086 | 18860.1
3117 | 154753 | 0 | 49 | 38 | 91.8872 | 11732.8
3118 | 143700 | 0 | 47 | 38 | 83.3914 | 11448.3
3119 | 138716 | -7909.94 | 44 | 37 | 87.018 | 9953.56
3120 | 136967 | 0 | 42 | 35 | 79.0081 | 9955.39
3121 | 135952 | -14354.2 | 41 | 34 | 87.3397 | 9957.22
3122 | 134963 | 0 | 39 | 33 | 78.9166 | 9959.16
3123 | 134041 | -18690.4 | 38 | 31 | 87.9419 | 9960.98
3124 | 136683 | -7958.03 | 37 | 31 | 85.5515 | 11066.6
3125 | 214431 | -15796.1 | 37 | 31 | 131.286 | 13525.2
3126 | 327722 | -305915 | 36 | 30 | 228.428 | 36669.7
3127 | 417285 | -263732 | 41 | 33 | 279.469 | 40228.3
3128 | 467730 | -200719 | 45 | 37 | 290.079 | 50910.2
3129 | 468231 | -141021 | 50 | 39 | 274.788 | 79394
3130 | 447933 | -99850.2 | 53 | 41 | 263.818 | 81173.6
3131 | 461049 | -64736 | 57 | 43 | 249.373 | 81172.2
3132 | 457291 | -30406.6 | 60 | 44 | 244.697 | 81170.9
3133 | 539471 | -16787.4 | 62 | 45 | 268.803 | 81170.4
3134 | 606764 | -12222.7 | 63 | 46 | 280.217 | 79389.4
3135 | 660829 | -10925.8 | 65 | 46 | 296.929 | 72267
3136 | 665510 | -10304.9 | 65 | 47 | 291.862 | 59803.8
3137 | 602971 | -9406.8 | 65 | 47 | 250.316 | 45560.7
3138 | 430015 | -9082.37 | 65 | 46 | 169.838 | 27757.7
3139 | 189631 | 0 | 60 | 46 | 108.502 | 19747
3140 | 169429 | 0 | 54 | 44 | 102.095 | 18858.4
3141 | 155821 | 0 | 49 | 41 | 91.9361 | 11729.3
3142 | 144711 | 0 | 47 | 41 | 83.4374 | 11444.2
3143 | 139706 | 0 | 45 | 40 | 79.7325 | 9948.93
3144 | 138053 | -6235.87 | 43 | 39 | 85.7496 | 9950.58
3145 | 136858 | 0 | 42 | 38 | 79.1217 | 9952.24
3146 | 135847 | -12198.8 | 40 | 36 | 86.943 | 9953.91
3147 | 134846 | 0 | 39 | 35 | 79.0303 | 9955.66
3148 | 137612 | -16023.9 | 39 | 35 | 89.7812 | 11061
3149 | 183762 | -4530.58 | 40 | 36 | 123.659 | 13519.5
3150 | 331848 | -159939 | 40 | 36 | 227.069 | 36663.6
3151 | 452101 | -208456 | 45 | 39 | 282.413 | 40221.9
3152 | 462705 | -132401 | 49 | 42 | 272.335 | 50905
3153 | 477661 | -84365.8 | 54 | 44 | 275.158 | 79389.9
3154 | 463502 | -52799.2 | 56 | 45 | 261.326 | 81169.6
3155 | 467387 | -34443 | 59 | 46 | 246.07 | 81168.4
3156 | 459412 | -17012.8 | 61 | 47 | 245.756 | 81167.8
3157 | 516908 | -14032.3 | 61 | 47 | 266.364 | 81167.6
3158 | 567612 | -11548.1 | 62 | 47 | 275.597 | 79386.9
3159 | 587768 | -10750.2 | 62 | 47 | 276.712 | 72264.8
3160 | 575452 | -10639.3 | 61 | 47 | 271.344 | 59801.7
3161 | 495879 | -10237 | 60 | 47 | 245.264 | 45558.7
3162 | 352848 | -11458.7 | 59 | 47 | 168.24 | 27755.8
3163 | 189578 | 0 | 58 | 47 | 109.686 | 19745.3
3164 | 169712 | 0 | 57 | 47 | 99.9875 | 18856.8
3165 | 156113 | 0 | 56 | 46 | 91.9495 | 11727.9
3166 | 145279 | 0 | 53 | 47 | 83.4631 | 11442.9
3167 | 140100 | 0 | 51 | 47 | 79.7505 | 9947.38
3168 | 138116 | 0 | 48 | 46 | 75.1271 | 9948.57
3169 | 137039 | -5474.69 | 48 | 46 | 79.5063 | 9949.79
3170 | 136063 | 0 | 48 | 46 | 75.0331 | 9951.69
3171 | 135220 | -1208.94 | 48 | 46 | 79.4236 | 9953.34
3172 | 134397 | 0 | 47 | 46 | 73.3574 | 9955.09
3173 | 133436 | -2099.4 | 47 | 45 | 76.127 | 9956.57
3174 | 132819 | 0 | 46 | 45 | 68.8295 | 9958.16
3175 | 158021 | -123416 | 49 | 47 | 84.8216 | 9959.63
3176 | 207691 | -191088 | 53 | 49 | 88.7623 | 9961.02
3177 | 200236 | -144947 | 56 | 51 | 89.3174 | 9964.1
3178 | 199235 | -109917 | 59 | 51 | 88.4614 | 9964.9
3179 | 201320 | -77702.7 | 62 | 52 | 89.0817 | 9965.75
3180 | 212998 | -58699.7 | 65 | 53 | 88.8923 | 9966.11
3181 | 226621 | -52867.8 | 66 | 53 | 89.223 | 9966.27
3182 | 129132 | 0 | 66 | 53 | 71.5263 | 9966.4
3183 | 128889 | 0 | 67 | 53 | 71.9169 | 9966.5
3184 | 128636 | 0 | 66 | 52 | 70.7292 | 9964.18
3185 | 128494 | 0 | 66 | 52 | 71.0787 | 9962.25
3186 | 128320 | 0 | 65 | 52 | 69.944 | 9961.25
3187 | 128053 | 0 | 61 | 51 | 70.6933 | 9960.48
3188 | 127712 | 0 | 58 | 50 | 75.965 | 9960.08
3189 | 127293 | 0 | 54 | 48 | 79.4511 | 9959.95
3190 | 127041 | 0 | 51 | 47 | 78.6395 | 9960.17
3191 | 126644 | 0 | 49 | 46 | 77.8217 | 9960.67
3192 | 126100 | 0 | 46 | 44 | 73.3053 | 3730.79
3193 | 125745 | 0 | 45 | 43 | 73.2891 | 3731.34
3194 | 125440 | -10105.3 | 45 | 43 | 80.5301 | 3732.6
3195 | 124959 | 0 | 44 | 42 | 73.2537 | 3733.99
3196 | 124676 | -13555.4 | 44 | 42 | 79.4857 | 3735.59
3197 | 124320 | 0 | 43 | 42 | 70.0108 | 3737.23
3198 | 123971 | -15352.4 | 43 | 42 | 75.325 | 3738.8
3199 | 123806 | -3495.37 | 49 | 45 | 71.4075 | 3740.49
3200 | 123741 | 0 | 54 | 48 | 67.0777 | 3741.99
3201 | 123431 | -8948.45 | 60 | 49 | 73.8939 | 3743.13
3202 | 123475 | 0 | 62 | 50 | 68.0038 | 3743.42
3203 | 123370 | 0 | 63 | 50 | 67.7767 | 3742.63
3204 | 123332 | 0 | 65 | 50 | 68.1088 | 3741.75
3205 | 123506 | 0 | 66 | 51 | 67.8919 | 3740.26
3206 | 123455 | 0 | 66 | 51 | 67.629 | 3739.43
3207 | 123435 | 0 | 67 | 51 | 67.929 | 3738.46
3208 | 123540 | 0 | 67 | 51 | 67.6695 | 3737.52
3209 | 123555 | 0 | 68 | 51 | 67.9743 | 3736.79
3210 | 123779 | 0 | 68 | 52 | 67.9258 | 3736.05
3211 | 123771 | 0 | 64 | 52 | 68.8821 | 3735.47
3212 | 123581 | 0 | 59 | 51 | 72.9174 | 3734.98
3213 | 123413 | 0 | 55 | 50 | 77.1416 | 3734.7
3214 | 123199 | 0 | 53 | 49 | 76.332 | 3734.73
3215 | 123079 | 0 | 51 | 48 | 75.5265 | 3735.17
3216 | 123202 | 0 | 49 | 47 | 78.5026 | 9966.43
3217 | 123032 | -9975.08 | 47 | 45 | 84.9746 | 9967.31
3218 | 130057 | -3913.07 | 44 | 44 | 83.236 | 9967.48
3219 | 124718 | -4027.24 | 42 | 42 | 83.004 | 9968.25
3220 | 151085 | -6741.51 | 44 | 43 | 91.2222 | 11072.9
3221 | 179168 | -7004.56 | 45 | 44 | 123.443 | 13530.7
3222 | 336473 | -113877 | 47 | 46 | 229.612 | 36674.4
3223 | 423144 | -124222 | 52 | 49 | 264.058 | 40232
3224 | 457959 | -61868.4 | 57 | 51 | 271.719 | 50912.3
3225 | 516050 | -29610.7 | 62 | 52 | 274.181 | 79395.5
3226 | 573719 | -17442.3 | 66 | 53 | 270.436 | 81174.3
3227 | 587295 | -11536.4 | 69 | 54 | 258.99 | 81173.6
3228 | 682585 | -11172.2 | 73 | 54 | 267.856 | 81172.7
3229 | 776261 | -9438.92 | 74 | 54 | 290.135 | 81171.6
3230 | 839105 | -9206.26 | 75 | 54 | 284.184 | 79390.6
3231 | 884506 | -8677.27 | 76 | 54 | 287.856 | 72268.7
3232 | 872449 | -7725.13 | 75 | 53 | 282.989 | 59805.7
3233 | 785418 | -6734.86 | 74 | 53 | 255.486 | 45562.7
3234 | 545998 | -9925 | 73 | 52 | 171.643 | 27759.3
3235 | 186254 | 0 | 68 | 53 | 105.815 | 19747.8
3236 | 165965 | 0 | 62 | 51 | 98.3092 | 18859
3237 | 152766 | 0 | 57 | 50 | 91.2843 | 11728.3
3238 | 141661 | 0 | 55 | 49 | 83.2986 | 11442.3
3239 | 136850 | 0 | 52 | 47 | 79.6026 | 9945.82
3240 | 135465 | 0 | 50 | 46 | 78.6337 | 9946.16
3241 | 134660 | 0 | 49 | 46 | 78.5968 | 9946.43
3242 | 133795 | 0 | 47 | 45 | 78.5576 | 9947.28
3243 | 132970 | 0 | 46 | 44 | 78.5201 | 9948.18
3244 | 135934 | 0 | 46 | 44 | 80.9417 | 11053
3245 | 182473 | -7408.76 | 45 | 44 | 126.008 | 13510.8
3246 | 327613 | -50991.9 | 45 | 44 | 227.978 | 36654.4
3247 | 458881 | -96848.5 | 51 | 48 | 266.718 | 40212.2
3248 | 500175 | -45801.9 | 57 | 51 | 271.322 | 50900.1
3249 | 585971 | -19392.1 | 63 | 54 | 278.107 | 79385
3250 | 675625 | -11136.2 | 68 | 56 | 279.708 | 81165.1
3251 | 676533 | -8839.05 | 72 | 57 | 265.829 | 81164.6
3252 | 787089 | -8450.17 | 77 | 57 | 278.421 | 81164.4
3253 | 874145 | -6871.06 | 77 | 57 | 304.537 | 81163.9
3254 | 922610 | -6981.64 | 77 | 56 | 314.075 | 79383.3
3255 | 932548 | -6680.32 | 77 | 56 | 316.114 | 72262
3256 | 905878 | -5747.32 | 76 | 56 | 309.665 | 59799.4
3257 | 811524 | -4427.02 | 75 | 56 | 281.785 | 45556.4
3258 | 568856 | -3739.63 | 74 | 55 | 192.82 | 27753.4
3259 | 190835 | 0 | 71 | 55 | 108.625 | 19742
3260 | 170607 | 0 | 69 | 55 | 99.904 | 18853.4
3261 | 157094 | 0 | 66 | 54 | 91.457 | 11721.3
3262 | 145898 | 0 | 65 | 53 | 83.4267 | 11434.9
3263 | 141028 | 0 | 64 | 52 | 79.683 | 9937.98
3264 | 139464 | 0 | 63 | 51 | 79.0923 | 9938.09
3265 | 138592 | 0 | 60 | 50 | 78.4379 | 9938.22
3266 | 137616 | 0 | 58 | 49 | 79.1559 | 9938.4
3267 | 136825 | 0 | 55 | 48 | 79.1199 | 9938.57
3268 | 139635 | 0 | 53 | 47 | 81.1099 | 11042.6
3269 | 186128 | 0 | 50 | 46 | 119.19 | 13499.7
3270 | 359326 | -29870.1 | 48 | 45 | 238.372 | 36642.8
3271 | 445006 | -34349.6 | 50 | 46 | 263.025 | 40200.2
3272 | 508494 | -63113.8 | 51 | 46 | 270.051 | 50893
3273 | 521421 | -45081.1 | 53 | 46 | 270.805 | 79378.3
3274 | 507850 | -22775.9 | 56 | 48 | 262.745 | 81159.2
3275 | 495420 | -12282 | 58 | 49 | 248.462 | 81159.1
3276 | 527077 | -9700.83 | 61 | 50 | 249.427 | 81159.3
3277 | 617065 | -9877.04 | 62 | 51 | 285.916 | 81159.7
3278 | 670678 | -11236.7 | 63 | 51 | 296 | 79379.4
3279 | 704453 | -11920.8 | 64 | 51 | 299.657 | 72257.5
3280 | 695323 | -12255.1 | 63 | 51 | 293.133 | 59794.7
3281 | 608125 | -10634.5 | 62 | 50 | 265.501 | 45552
3282 | 405391 | -9162.53 | 61 | 49 | 165.93 | 27749.5
3283 | 190573 | 0 | 59 | 48 | 108.004 | 19739.2
3284 | 170659 | 0 | 58 | 47 | 99.9497 | 18850.8
3285 | 157184 | 0 | 56 | 46 | 91.9984 | 11719.9
3286 | 145896 | 0 | 55 | 44 | 83.4916 | 11434.5
3287 | 140945 | 0 | 53 | 42 | 79.7887 | 9938.5
3288 | 139255 | 0 | 52 | 40 | 79.112 | 9939.5
3289 | 138409 | 0 | 50 | 39 | 79.0729 | 9940.46
3290 | 137420 | 0 | 49 | 38 | 79.0281 | 9941.51
3291 | 136509 | -6464.48 | 47 | 37 | 85.6866 | 9942.57
3292 | 139291 | 0 | 46 | 37 | 81.0943 | 11047.4
3293 | 185512 | -1650.06 | 44 | 37 | 123.613 | 13505.3
3294 | 330498 | -47570.5 | 43 | 36 | 226.688 | 36649.2
3295 | 461896 | -134721 | 46 | 38 | 265.091 | 40207
3296 | 487314 | -94984.1 | 50 | 40 | 273.572 | 50895.7
3297 | 517789 | -70737.8 | 53 | 41 | 275.797 | 79380.8
3298 | 503264 | -34844.2 | 56 | 43 | 261.849 | 81161
3299 | 507728 | -14323.1 | 60 | 44 | 249.701 | 81161.1
3300 | 577172 | -11937.5 | 63 | 45 | 256.033 | 81160.7
3301 | 653702 | -10251.3 | 64 | 46 | 289.121 | 81160.7
3302 | 730312 | -9749.13 | 66 | 47 | 300.78 | 79380.2
3303 | 778784 | -11246.7 | 67 | 48 | 304.805 | 72258.2
3304 | 757175 | -11358.7 | 66 | 48 | 297.614 | 59795.5
3305 | 681088 | -9289.03 | 66 | 48 | 270.801 | 45552.8
3306 | 462153 | -8642.33 | 65 | 47 | 187.513 | 27750
3307 | 190847 | 0 | 62 | 46 | 109.754 | 19739.7
3308 | 170845 | 0 | 59 | 44 | 99.4745 | 18851.3
3309 | 157278 | 0 | 56 | 42 | 92.0028 | 11720.1
3310 | 146286 | 0 | 51 | 41 | 83.5091 | 11434.5
3311 | 141203 | 0 | 47 | 40 | 79.8006 | 9938.43
3312 | 139302 | 0 | 42 | 37 | 79.2332 | 9939.44
3313 | 138194 | 0 | 40 | 37 | 79.1823 | 9940.62
3314 | 137185 | -9051.15 | 39 | 36 | 86.7148 | 9942.03
3315 | 136118 | 0 | 37 | 34 | 79.088 | 9943.65
3316 | 138723 | -15599.7 | 38 | 35 | 89.9444 | 11049.1
3317 | 184741 | -4001.63 | 38 | 36 | 123.48 | 13507.7
3318 | 329854 | -101146 | 39 | 36 | 227.595 | 36652
3319 | 458824 | -167745 | 45 | 41 | 265.59 | 40210.5
3320 | 487836 | -91377.2 | 52 | 44 | 275.737 | 50897.4
3321 | 530466 | -43203.1 | 58 | 47 | 276.323 | 79382.2
3322 | 549437 | -18020.9 | 62 | 48 | 267.441 | 81162.6
3323 | 560995 | -11294.4 | 65 | 49 | 256.093 | 81162.9
3324 | 652880 | -10353.8 | 69 | 49 | 261.939 | 81162.3
3325 | 750132 | -8771.37 | 71 | 50 | 296.315 | 81161.5
3326 | 841890 | -8450.01 | 73 | 51 | 308.682 | 79380.9
3327 | 909499 | -8075.48 | 75 | 52 | 314.775 | 72259
3328 | 896442 | -8872.15 | 74 | 52 | 307.808 | 59796.6
3329 | 844849 | -15541.8 | 74 | 52 | 283.317 | 45553.9
3330 | 611847 | -22043.8 | 73 | 52 | 195.378 | 27750.7
3331 | 192149 | 0 | 68 | 53 | 106.439 | 19740
3332 | 171682 | 0 | 62 | 52 | 98.3886 | 18851.5
3333 | 158048 | 0 | 57 | 51 | 91.5251 | 11719.4
3334 | 146616 | 0 | 54 | 49 | 83.5244 | 11433.3
3335 | 141642 | 0 | 52 | 47 | 79.8204 | 9936.81
3336 | 139735 | 0 | 49 | 45 | 75.2006 | 9937.54
3337 | 138675 | 0 | 47 | 44 | 75.1517 | 9938.39
3338 | 137497 | 0 | 45 | 42 | 75.0983 | 9940.05
3339 | 136626 | 0 | 43 | 41 | 75.0586 | 9941.49
3340 | 135793 | -7919.97 | 44 | 42 | 80.5862 | 9943.09
3341 | 134813 | 0 | 44 | 42 | 71.6986 | 9944.72
3342 | 134207 | -1774.62 | 45 | 44 | 73.2471 | 9946.48
3343 | 183825 | -119847 | 51 | 47 | 86.1526 | 9948.27
3344 | 204389 | -107883 | 58 | 50 | 89.3086 | 9949.54
3345 | 203438 | -50195.1 | 64 | 52 | 90.2058 | 9954.5
3346 | 244755 | -45022.3 | 68 | 53 | 93.1723 | 9955.8
3347 | 296258 | -35827.3 | 73 | 54 | 96.9024 | 9956.57
3348 | 343947 | -29548 | 77 | 54 | 99.7261 | 9956.8
3349 | 367895 | -26225 | 78 | 54 | 100.412 | 9956.78
3350 | 177444 | 0 | 78 | 55 | 82.3655 | 9956.66
3351 | 178326 | 0 | 79 | 55 | 82.036 | 9956.45
3352 | 130326 | 0 | 79 | 55 | 72.4568 | 9952.42
3353 | 130163 | 0 | 78 | 55 | 72.2549 | 9949.46
3354 | 130095 | 0 | 78 | 55 | 72.1731 | 9947.57
3355 | 130050 | 0 | 72 | 54 | 72.8255 | 9945.78
3356 | 129545 | 0 | 66 | 52 | 74.8737 | 9944.52
3357 | 129205 | 0 | 60 | 50 | 78.0242 | 9943.45
3358 | 128844 | 0 | 57 | 49 | 78.7211 | 9942.86
3359 | 128502 | 0 | 54 | 48 | 77.9057 | 9942.83
3360 | 128010 | 0 | 51 | 47 | 73.3916 | 3712.68
3361 | 127511 | 0 | 50 | 46 | 73.369 | 3713.33
3362 | 127090 | 0 | 48 | 45 | 73.35 | 3714.35
3363 | 126648 | 0 | 47 | 44 | 73.33 | 3715.53
3364 | 127749 | -5572.18 | 48 | 45 | 76.2074 | 3716.81
3365 | 126119 | 0 | 49 | 47 | 70.0457 | 3718.15
3366 | 125676 | 0 | 50 | 48 | 67.4227 | 3719.54
3367 | 125538 | 0 | 56 | 51 | 67.0634 | 3720.98
3368 | 128206 | -5499.55 | 61 | 54 | 72.0078 | 3721.92
3369 | 125087 | 0 | 67 | 55 | 69.3421 | 3721.59
3370 | 125162 | 0 | 71 | 56 | 68.9882 | 3720.72
3371 | 155043 | 0 | 75 | 57 | 74.6833 | 3719.47
3372 | 165171 | 0 | 79 | 57 | 74.0718 | 3717.72
3373 | 173010 | 0 | 80 | 57 | 74.4755 | 3715.94
3374 | 179621 | 0 | 81 | 57 | 74.8153 | 3714.43
3375 | 181074 | 0 | 82 | 57 | 74.8945 | 3712.88
3376 | 125542 | 0 | 81 | 57 | 68.1285 | 3711.1
3377 | 167193 | 0 | 80 | 56 | 72.1901 | 3709.37
3378 | 125716 | 0 | 79 | 56 | 68.1266 | 3707.74
3379 | 125662 | 0 | 76 | 55 | 70.3488 | 3706.23
3380 | 125659 | 0 | 72 | 54 | 73.4965 | 3704.96
3381 | 125569 | 0 | 69 | 53 | 76.7555 | 3703.86
3382 | 125524 | 0 | 68 | 53 | 76.4505 | 3703.07
3383 | 125459 | 0 | 66 | 53 | 75.3149 | 3702.63
3384 | 125644 | 0 | 65 | 53 | 78.5218 | 9933
3385 | 125624 | 0 | 65 | 54 | 78.7821 | 9932.88
3386 | 125555 | 0 | 64 | 55 | 78.4841 | 9932.05
3387 | 125263 | 0 | 64 | 55 | 78.7303 | 9931.72
3388 | 129078 | 0 | 63 | 55 | 80.475 | 11035.1
3389 | 234253 | 0 | 61 | 55 | 124.693 | 13491.6
3390 | 682764 | -13828.9 | 60 | 55 | 249.636 | 36633.9
3391 | 765140 | -18263.7 | 63 | 57 | 286.617 | 40190.4
3392 | 819267 | -12062.5 | 66 | 58 | 295.096 | 50886.7
3393 | 876198 | -9974.98 | 69 | 59 | 285.156 | 79372.9
3394 | 922824 | -7431.8 | 72 | 60 | 280.109 | 81154.5
3395 | 908572 | -6414.36 | 74 | 61 | 266.306 | 81154.7
3396 | 998331 | -16625.8 | 77 | 62 | 277.47 | 81155.1
3397 | 1110880 | -5110 | 78 | 63 | 293.99 | 81156.1
3398 | 1157860 | -5474.9 | 80 | 63 | 308.23 | 79376.1
3399 | 1251740 | -5969.75 | 81 | 64 | 314.602 | 72255.2
3400 | 1227380 | -19166.5 | 79 | 63 | 308.174 | 59792.9
3401 | 1112680 | -24687.5 | 78 | 62 | 277.531 | 45550.5
3402 | 739668 | -14557.1 | 76 | 62 | 183.461 | 27747.7
3403 | 187469 | 0 | 75 | 61 | 107.824 | 19736.6
3404 | 167536 | 0 | 74 | 60 | 100.136 | 18847.3
3405 | 154374 | 0 | 73 | 59 | 92.1821 | 11713.9
3406 | 143768 | 0 | 71 | 59 | 83.3029 | 11426.5
3407 | 138813 | 0 | 70 | 58 | 79.8159 | 9928.86
3408 | 137617 | 0 | 68 | 58 | 78.5043 | 9928.19
3409 | 136935 | 0 | 68 | 59 | 79.0057 | 9927.67
3410 | 136330 | 0 | 68 | 60 | 78.9768 | 9927.25
3411 | 135615 | 0 | 68 | 60 | 78.9428 | 9926.9
3412 | 139170 | 0 | 67 | 61 | 81.0916 | 11030.3
3413 | 261274 | 0 | 67 | 61 | 127.031 | 13486.6
3414 | 922362 | -7408.75 | 66 | 61 | 265.259 | 36628.7
3415 | 982053 | -9199.28 | 67 | 62 | 283.875 | 40185
3416 | 1023990 | -9464.12 | 68 | 63 | 292.783 | 50883.9
3417 | 1052070 | -10873 | 69 | 64 | 294.938 | 79370.9
3418 | 1047060 | -9979.73 | 68 | 64 | 284.889 | 81152.2
3419 | 970732 | -7273.79 | 68 | 65 | 267.178 | 81152
3420 | 958118 | -7134.34 | 67 | 65 | 266.282 | 81152.3
3421 | 1100510 | -10491.9 | 68 | 66 | 310.892 | 81152.8
3422 | 1133690 | -13147.1 | 69 | 66 | 322.458 | 79372.7
3423 | 1207060 | -14137.6 | 70 | 67 | 329.837 | 72251.1
3424 | 1188300 | -13711.9 | 70 | 66 | 321.454 | 59788.8
3425 | 1098910 | -10217.9 | 71 | 66 | 272.891 | 45546.4
3426 | 752170 | -6207.46 | 71 | 66 | 182.204 | 27744.1
3427 | 191705 | 0 | 70 | 66 | 108.153 | 19733.7
3428 | 171402 | 0 | 69 | 65 | 100.052 | 18845.5
3429 | 158096 | 0 | 68 | 65 | 92.1259 | 11712.2
3430 | 147110 | 0 | 66 | 65 | 83.2595 | 11425.5
3431 | 142050 | 0 | 65 | 64 | 79.7691 | 9928.17
3432 | 140395 | 0 | 63 | 63 | 78.8764 | 9927.96
3433 | 139531 | 0 | 63 | 63 | 79.3542 | 9927.84
3434 | 138699 | 0 | 63 | 63 | 79.3157 | 9927.8
3435 | 137919 | 0 | 63 | 63 | 79.2796 | 9927.82
3436 | 140929 | 0 | 62 | 62 | 80.9848 | 11031.6
3437 | 250641 | 0 | 62 | 61 | 126.294 | 13488.3
3438 | 732941 | -8909.87 | 61 | 60 | 260.292 | 36630.8
3439 | 798860 | -15311.5 | 60 | 59 | 271.573 | 40187.5
3440 | 783631 | -18014.6 | 60 | 58 | 277.757 | 50884.5
3441 | 767208 | -19449.7 | 59 | 57 | 276.568 | 79370.8
3442 | 751756 | -18247.8 | 59 | 57 | 270.958 | 81151.7
3443 | 695306 | -15391.6 | 60 | 57 | 253.252 | 81152.1
3444 | 664329 | -14006.7 | 60 | 56 | 250.895 | 81152.5
3445 | 743032 | -17481 | 60 | 56 | 271.67 | 81153.3
3446 | 773297 | -20163.5 | 59 | 56 | 298.008 | 79373.3
3447 | 778145 | -21223.2 | 59 | 55 | 299.45 | 72251.7
3448 | 755394 | -21673.2 | 59 | 55 | 294.214 | 59789.3
3449 | 647278 | -20075.2 | 58 | 55 | 248.603 | 45547.1
3450 | 421035 | -18387.3 | 58 | 55 | 168.363 | 27744.7
3451 | 190744 | 0 | 57 | 54 | 107.319 | 19734.6
3452 | 171088 | 0 | 55 | 54 | 99.9898 | 18846.5
3453 | 157429 | 0 | 54 | 53 | 92.0097 | 11715
3454 | 146326 | 0 | 54 | 53 | 83.511 | 11429.6
3455 | 141472 | 0 | 55 | 54 | 79.8127 | 9933.51
3456 | 139812 | 0 | 55 | 54 | 79.1373 | 9934.47
3457 | 138829 | 0 | 55 | 54 | 79.0921 | 9935.33
3458 | 137941 | 0 | 55 | 54 | 79.0517 | 9936.16
3459 | 137138 | 0 | 55 | 54 | 79.0152 | 9936.86
3460 | 140109 | 0 | 55 | 54 | 81.1313 | 11041.3
3461 | 186798 | 0 | 55 | 54 | 119.191 | 13498.5
3462 | 410002 | -32850.3 | 55 | 54 | 244.122 | 36641.6
3463 | 549602 | -21176.2 | 56 | 54 | 258.945 | 40198.6
3464 | 597754 | -26135.4 | 58 | 54 | 278.582 | 50890.3
3465 | 635679 | -21847.3 | 59 | 54 | 277.533 | 79375.5
3466 | 632312 | -19600.2 | 59 | 54 | 268.596 | 81156.3
3467 | 602307 | -16732.3 | 59 | 55 | 251.426 | 81156.2
3468 | 592435 | -15228.8 | 59 | 55 | 250 | 81156.3
3469 | 691487 | -18386.4 | 60 | 56 | 290.516 | 81156.8
3470 | 736633 | -20194.8 | 61 | 56 | 298.809 | 79376.6
3471 | 797307 | -20235.3 | 62 | 57 | 303.805 | 72254.9
3472 | 813775 | -20162.5 | 62 | 58 | 299.543 | 59792.2
3473 | 719285 | -16832.5 | 63 | 58 | 271.973 | 45549.7
3474 | 492964 | -13635.4 | 63 | 59 | 171.589 | 27747.3
3475 | 191052 | 0 | 62 | 58 | 108.697 | 19737
3476 | 171297 | 0 | 60 | 58 | 99.502 | 18848.8
3477 | 157659 | 0 | 59 | 57 | 92.0203 | 11717.2
3478 | 146627 | 0 | 58 | 57 | 83.5246 | 11431.5
3479 | 141547 | 0 | 56 | 56 | 79.8162 | 9935.18
3480 | 139841 | 0 | 55 | 55 | 79.2576 | 9935.75
3481 | 138925 | 0 | 55 | 55 | 79.2153 | 9936.12
3482 | 138180 | 0 | 56 | 56 | 79.1814 | 9936.79
3483 | 137308 | 0 | 56 | 56 | 79.1419 | 9937.42
3484 | 140294 | 0 | 56 | 56 | 81.1397 | 11041.8
3485 | 187206 | 0 | 57 | 57 | 119.112 | 13499
3486 | 462464 | -30151.7 | 57 | 57 | 242.646 | 36642
3487 | 658159 | -17965.8 | 59 | 58 | 263.783 | 40199.1
3488 | 720996 | -20797.1 | 61 | 59 | 273.615 | 50891
3489 | 766450 | -18630.6 | 63 | 59 | 276.607 | 79376.2
3490 | 771620 | -16409.2 | 64 | 59 | 268.467 | 81156.8
3491 | 750971 | -12176.3 | 66 | 60 | 258.132 | 81156.7
3492 | 785488 | -10789.7 | 67 | 60 | 277.753 | 81156.9
3493 | 890122 | -12887.1 | 69 | 60 | 304.143 | 81157.3
3494 | 962499 | -15697.4 | 70 | 61 | 315.435 | 79377
3495 | 1037880 | -16541.4 | 72 | 61 | 322.161 | 72255.1
3496 | 1052340 | -15930.4 | 72 | 62 | 317.115 | 59792.3
3497 | 965929 | -12544.7 | 71 | 62 | 288.205 | 45549.7
3498 | 645797 | -8392.52 | 71 | 62 | 197.432 | 27747.2
3499 | 192108 | 0 | 68 | 61 | 107.009 | 19736.9
3500 | 172041 | 0 | 64 | 60 | 99.0403 | 18848.5
3501 | 158520 | 0 | 61 | 59 | 91.3279 | 11715.8
3502 | 147430 | 0 | 61 | 59 | 83.5999 | 11429.6
3503 | 142458 | 0 | 61 | 59 | 79.8948 | 9932.78
3504 | 140775 | 0 | 61 | 60 | 75.2844 | 9933.22
3505 | 139542 | 0 | 60 | 59 | 74.9365 | 9933.6
3506 | 138544 | 0 | 59 | 58 | 75.1457 | 9934.59
3507 | 137613 | 0 | 58 | 57 | 75.1034 | 9935.15
3508 | 137025 | 0 | 58 | 58 | 73.4765 | 9935.78
3509 | 136191 | 0 | 59 | 58 | 71.7623 | 9936.38
3510 | 135503 | 0 | 59 | 58 | 69.3593 | 9937.03
3511 | 223812 | -21411.1 | 61 | 59 | 89.4982 | 9937.65
3512 | 254903 | -17055.5 | 63 | 60 | 91.6182 | 9938.07
3513 | 293268 | -20853.4 | 65 | 61 | 94.2598 | 9947.94
3514 | 330951 | -19076.6 | 67 | 62 | 97.2106 | 9949.18
3515 | 377808 | -18793.3 | 70 | 63 | 100.465 | 9950.15
3516 | 412580 | -18563.7 | 72 | 64 | 101.396 | 9950.63
3517 | 430042 | -18694.8 | 73 | 64 | 101.033 | 9951.09
3518 | 131652 | 0 | 74 | 65 | 73.528 | 9951.52
3519 | 131334 | 0 | 75 | 65 | 73.1201 | 9951.96
3520 | 130974 | 0 | 75 | 64 | 72.3773 | 9946.67
3521 | 130843 | 0 | 74 | 64 | 71.5921 | 9943.83
3522 | 130623 | 0 | 74 | 64 | 72.2575 | 9941.74
3523 | 130371 | 0 | 71 | 63 | 71.2871 | 9939.95
3524 | 130055 | 0 | 68 | 62 | 75.66 | 9938.74
3525 | 129577 | 0 | 65 | 60 | 78.9473 | 9937.83
3526 | 129444 | 0 | 64 | 60 | 78.6271 | 9937.28
3527 | 129161 | 0 | 63 | 60 | 77.78 | 9937.03
3528 | 128799 | 0 | 62 | 60 | 73.2382 | 3706.49
3529 | 128501 | 0 | 61 | 60 | 73.192 | 3706.57
3530 | 128171 | 0 | 60 | 60 | 73.1452 | 3706.9
3531 | 127717 | 0 | 59 | 59 | 73.3783 | 3707.25
3532 | 127455 | 0 | 59 | 59 | 71.7663 | 3707.67
3533 | 127032 | 0 | 59 | 58 | 70.0731 | 3708.14
3534 | 126832 | 0 | 59 | 58 | 67.4802 | 3708.69
3535 | 126758 | 0 | 63 | 60 | 67.9794 | 3709.25
3536 | 126730 | 0 | 66 | 62 | 68.213 | 3709.71
3537 | 126687 | 0 | 70 | 64 | 69.0158 | 3709.71
3538 | 126609 | 0 | 71 | 65 | 68.2378 | 3709.33
3539 | 126464 | 0 | 72 | 66 | 68.2729 | 3708.04
3540 | 180450 | 0 | 73 | 67 | 74.9745 | 3706.83
3541 | 126202 | 0 | 73 | 67 | 68.4402 | 3705.31
3542 | 126184 | 0 | 72 | 67 | 68.2375 | 3703.79
3543 | 126174 | 0 | 72 | 67 | 69.863 | 3702.55
3544 | 126146 | 0 | 72 | 67 | 69.7409 | 3701.73
3545 | 126128 | 0 | 71 | 67 | 69.4159 | 3700.63
3546 | 125962 | 0 | 71 | 66 | 70.1217 | 3700.01
3547 | 125925 | 0 | 70 | 66 | 70.1851 | 3698.95
3548 | 125966 | 0 | 68 | 67 | 73.6234 | 3698.45
3549 | 125812 | 0 | 67 | 66 | 77.2285 | 3697.96
3550 | 181653 | 0 | 67 | 66 | 83.3254 | 3697.69
3551 | 125582 | 0 | 66 | 66 | 75.6263 | 3697.57
3552 | 125506 | 0 | 66 | 66 | 73.4838 | 3697.59
3553 | 125425 | 0 | 66 | 66 | 73.48 | 3697.7
3554 | 125227 | 0 | 65 | 65 | 73.174 | 3697.7
3555 | 125045 | 0 | 65 | 64 | 73.4265 | 3697.79
3556 | 125035 | 0 | 65 | 65 | 71.8259 | 3697.87
3557 | 125045 | 0 | 66 | 66 | 70.4795 | 3698.01
3558 | 166064 | 0 | 66 | 66 | 74.1569 | 3698.16
3559 | 124804 | 0 | 67 | 66 | 68.0589 | 3698.29
3560 | 124738 | 0 | 68 | 66 | 68.031 | 3698.34
3561 | 124695 | 0 | 69 | 66 | 68.587 | 3698.38
3562 | 124645 | 0 | 69 | 66 | 68.0678 | 3698.14
3563 | 124627 | 0 | 70 | 66 | 68.2792 | 3697.72
3564 | 178524 | 0 | 70 | 65 | 74.6083 | 3697.09
3565 | 124643 | 0 | 72 | 66 | 68.5039 | 3696.24
3566 | 124699 | 0 | 75 | 67 | 69.7578 | 3695.25
3567 | 188620 | 0 | 77 | 67 | 80.4475 | 3694.39
3568 | 124769 | 0 | 77 | 67 | 70.013 | 3693.16
3569 | 124858 | 0 | 77 | 67 | 69.9971 | 3691.7
3570 | 124939 | 0 | 77 | 67 | 69.7836 | 3690.4
3571 | 124595 | 0 | 74 | 64 | 70.0695 | 3689.11
3572 | 193577 | 0 | 70 | 62 | 80.4254 | 3688.11
3573 | 124365 | 0 | 67 | 59 | 76.688 | 3687.23
3574 | 124451 | 0 | 66 | 58 | 76.3297 | 3686.76
3575 | 124437 | 0 | 64 | 57 | 75.2031 | 3686.69
3576 | 124629 | 0 | 63 | 56 | 77.9835 | 9917.29
3577 | 163733 | 0 | 61 | 55 | 83.429 | 9917.47
3578 | 124395 | 0 | 59 | 54 | 77.908 | 9916.93
3579 | 124193 | 0 | 57 | 52 | 78.1227 | 9916.93
3580 | 128144 | 0 | 56 | 53 | 80.5881 | 11020.8
3581 | 234280 | 0 | 56 | 53 | 124.919 | 13477.7
3582 | 701074 | -16270.3 | 55 | 53 | 251.726 | 36620.5
3583 | 758786 | -28090.6 | 58 | 55 | 283.427 | 40177.2
3584 | 806514 | -18353.8 | 62 | 56 | 293.996 | 50877.8
3585 | 856840 | -11969.5 | 65 | 57 | 282.331 | 79365.3
3586 | 858047 | -9173.84 | 67 | 57 | 274.624 | 81148.5
3587 | 810487 | -7192.65 | 68 | 58 | 259.014 | 81150
3588 | 817558 | -7414.22 | 70 | 57 | 259.757 | 81150.3
3589 | 897218 | -6825.3 | 71 | 57 | 281.569 | 81150
3590 | 975288 | -7477.99 | 72 | 58 | 292.189 | 79369.9
3591 | 985731 | -8273.66 | 73 | 57 | 298.272 | 72249.1
3592 | 985057 | -14021 | 72 | 57 | 292.529 | 59787
3593 | 860208 | -13428.2 | 71 | 56 | 261.582 | 45544.6
3594 | 628551 | -21142.1 | 70 | 55 | 176.375 | 27741.8
3595 | 186675 | 0 | 66 | 55 | 106.295 | 19730.8
3596 | 166734 | 0 | 61 | 54 | 97.8849 | 18842.7
3597 | 153281 | 0 | 57 | 52 | 91.5636 | 11709.2
3598 | 142503 | 0 | 56 | 52 | 83.3367 | 11422.7
3599 | 137688 | 0 | 54 | 51 | 79.6407 | 9925.83
3600 | 136326 | 0 | 53 | 51 | 79.0977 | 9926.4
3601 | 135416 | 0 | 51 | 50 | 79.0561 | 9927.02
3602 | 134565 | 0 | 50 | 49 | 79.0174 | 9927.78
3603 | 133721 | 0 | 48 | 47 | 78.9791 | 9928.54
3604 | 136926 | 0 | 48 | 48 | 80.9866 | 11033.1
3605 | 198233 | -4397.37 | 48 | 48 | 126.478 | 13490.8
3606 | 371310 | -23793.9 | 48 | 48 | 228.604 | 36634.3
3607 | 505144 | -37141.8 | 53 | 51 | 264.578 | 40192.1
3608 | 630455 | -21486.1 | 59 | 54 | 279.829 | 50886.1
3609 | 739685 | -14236 | 64 | 56 | 287.267 | 79371.8
3610 | 786974 | -10650.5 | 67 | 57 | 280.968 | 81153.6
3611 | 743363 | -7863.19 | 69 | 57 | 278.376 | 81154.9
3612 | 797704 | -8134.46 | 72 | 57 | 283.378 | 81154.8
3613 | 903932 | -6842.38 | 74 | 58 | 308.044 | 81155
3614 | 994577 | -10070.9 | 75 | 59 | 319.395 | 79374.2
3615 | 1082440 | -11046.9 | 77 | 60 | 325.678 | 72253.2
3616 | 1087960 | -15194.8 | 77 | 60 | 321.271 | 59791
3617 | 1036130 | -18342 | 76 | 61 | 294.721 | 45548.5
3618 | 739863 | -21500 | 76 | 61 | 205.391 | 27745.7
3619 | 191576 | 0 | 73 | 61 | 107.321 | 19734.6
3620 | 171261 | 0 | 70 | 60 | 99.3418 | 18846
3621 | 157877 | 0 | 68 | 59 | 91.846 | 11712.5
3622 | 146912 | 0 | 69 | 59 | 84.1831 | 11425.6
3623 | 142036 | 0 | 70 | 59 | 80.5157 | 9928.21
3624 | 140692 | 0 | 71 | 60 | 79.8961 | 9928.01
3625 | 140059 | 0 | 72 | 60 | 79.9113 | 9103.46
3626 | 139475 | 0 | 73 | 61 | 79.9298 | 9103.11
3627 | 138704 | 0 | 73 | 61 | 79.6141 | 9102.57
3628 | 142106 | 0 | 72 | 61 | 81.4412 | 10103.4
3629 | 270442 | 0 | 71 | 61 | 127.228 | 12331.9
3630 | 1068770 | -5023.01 | 73 | 63 | 264.383 | 33330.4
3631 | 1210630 | -10663.2 | 74 | 65 | 302.671 | 36556.6
3632 | 1026730 | -14405.3 | 68 | 60 | 292.698 | 46268.2
3633 | 968154 | -15913.6 | 68 | 58 | 309.664 | 72118.3
3634 | 953837 | -14353.8 | 69 | 58 | 304.639 | 73735
3635 | 839037 | -11765.4 | 68 | 57 | 283.774 | 73735.7
3636 | 888225 | -16274.5 | 70 | 58 | 288.253 | 73735.7
3637 | 966331 | -13872 | 71 | 58 | 309.881 | 73735.1
3638 | 946928 | -17777.6 | 68 | 56 | 312.907 | 72120
3639 | 973293 | -19181 | 68 | 56 | 316.127 | 65658.5
3640 | 947712 | -19248.8 | 68 | 56 | 310.021 | 54350.3
3641 | 790423 | -16865 | 65 | 54 | 276.553 | 41426.8
3642 | 556197 | -16549.9 | 65 | 54 | 192.669 | 25272.6
3643 | 192744 | 0 | 63 | 53 | 110.061 | 18003.6
3644 | 172638 | 0 | 60 | 51 | 98.7214 | 17197.8
3645 | 159298 | 0 | 57 | 50 | 92.0951 | 10724.3
3646 | 147995 | 0 | 56 | 49 | 83.5872 | 10464.5
3647 | 142907 | 0 | 55 | 47 | 79.8781 | 9106.28
3648 | 141495 | 0 | 54 | 47 | 79.3325 | 9106.84
3649 | 140360 | 0 | 52 | 46 | 79.2807 | 9107.44
3650 | 139347 | 0 | 50 | 45 | 79.2346 | 9108.13
3651 | 138500 | 0 | 48 | 45 | 79.196 | 9108.81
3652 | 140931 | 0 | 47 | 43 | 81.1691 | 10111.1
3653 | 201102 | -3857.95 | 45 | 42 | 126.497 | 12341.2
3654 | 369258 | -22740.1 | 48 | 42 | 226.7 | 33341.4
3655 | 489113 | -50233.8 | 51 | 44 | 263.498 | 36569.3
3656 | 566402 | -47214.1 | 54 | 45 | 289.724 | 46272.9
3657 | 589742 | -30339.3 | 56 | 46 | 288.927 | 72119.9
3658 | 612302 | -22263.7 | 59 | 47 | 282.503 | 73737.3
3659 | 616899 | -15793.9 | 62 | 48 | 269.603 | 73738.1
3660 | 644230 | -13204.6 | 64 | 49 | 271.881 | 73738
3661 | 750876 | -15542 | 66 | 50 | 295.82 | 73737.5
3662 | 851673 | -17645.2 | 69 | 52 | 309.152 | 72121.5
3663 | 879539 | -18676.6 | 69 | 52 | 311.258 | 65659.5
3664 | 884234 | -17701.2 | 70 | 52 | 307.355 | 54351.6
3665 | 816628 | -17448.5 | 70 | 53 | 279.979 | 41428
3666 | 569140 | -16713.8 | 68 | 52 | 193.343 | 25273.7
3667 | 192826 | 0 | 66 | 52 | 110.431 | 18005.2
3668 | 172745 | 0 | 62 | 51 | 98.4841 | 17199.4
3669 | 159278 | 0 | 61 | 51 | 91.8777 | 10726.2
3670 | 148008 | 0 | 55 | 49 | 83.3321 | 10466.3
3671 | 143023 | 0 | 54 | 49 | 79.8833 | 9108.11
3672 | 140946 | 0 | 55 | 48 | 75.2557 | 9108.59
3673 | 139949 | 0 | 55 | 47 | 75.2096 | 9109.24
3674 | 139009 | 0 | 54 | 46 | 75.1668 | 9110.66
3675 | 138235 | 0 | 53 | 46 | 75.1315 | 9111.69
3676 | 137330 | 0 | 52 | 46 | 73.4905 | 9112.67
3677 | 136497 | 0 | 51 | 46 | 71.7296 | 9113.65
3678 | 135628 | 0 | 53 | 46 | 68.6817 | 9114.69
3679 | 196228 | -38496.5 | 57 | 50 | 88.1599 | 9115.76
3680 | 217278 | -40283.2 | 61 | 52 | 88.4923 | 9116.68
3681 | 246489 | -29145.6 | 66 | 54 | 92.353 | 9124.7
3682 | 283426 | -23706 | 69 | 56 | 94.0342 | 9125.85
3683 | 318160 | -20050.5 | 72 | 57 | 95.142 | 9126.73
3684 | 349322 | -19117.9 | 74 | 58 | 95.5732 | 9127.15
3685 | 383894 | -18614 | 76 | 59 | 115.219 | 9127.41
3686 | 185341 | 0 | 79 | 60 | 83.4296 | 9127.73
3687 | 187744 | 0 | 79 | 60 | 83.2444 | 9128.04
3688 | 131629 | 0 | 80 | 61 | 72.5486 | 9122.77
3689 | 131405 | 0 | 80 | 61 | 72.3579 | 9119.48
3690 | 131295 | 0 | 79 | 61 | 72.3177 | 9117.12
3691 | 130996 | 0 | 76 | 60 | 74.5154 | 9115.02
3692 | 130796 | 0 | 72 | 59 | 75.6995 | 9113.4
3693 | 130576 | 0 | 71 | 59 | 79.7393 | 9112.01
3694 | 130402 | 0 | 69 | 59 | 78.5857 | 9111.05
3695 | 130213 | 0 | 69 | 60 | 78.3127 | 9110.47
3696 | 129835 | 0 | 68 | 60 | 73.4948 | 3456.51
3697 | 129541 | 0 | 66 | 60 | 73.143 | 3456.2
3698 | 129200 | 0 | 66 | 60 | 73.6554 | 3456.12
3699 | 128918 | 0 | 66 | 60 | 73.642 | 3456.03
3700 | 128643 | 0 | 66 | 60 | 72.0291 | 3456.04
3701 | 128423 | 0 | 65 | 60 | 70.0221 | 3456.06
3702 | 128356 | 0 | 68 | 62 | 71.0741 | 3456.09
3703 | 128330 | 0 | 70 | 64 | 68.0747 | 3456.06
3704 | 128135 | 0 | 71 | 65 | 67.9527 | 3456.03
3705 | 128162 | 0 | 77 | 68 | 69.3358 | 3455.4
3706 | 194347 | 0 | 82 | 71 | 81.0723 | 3453.76
3707 | 195901 | 0 | 84 | 71 | 82.0939 | 3452
3708 | 203369 | 0 | 79 | 69 | 83.7614 | 3450.08
3709 | 207115 | 0 | 69 | 68 | 78.5927 | 3447.66
3710 | 127234 | 0 | 67 | 65 | 69.6738 | 3446.35
3711 | 126869 | 0 | 65 | 62 | 69.5621 | 3444.26
3712 | 126681 | 0 | 65 | 59 | 70.0904 | 3443.36
3713 | 126898 | 0 | 66 | 60 | 70.6716 | 3443.1
3714 | 126718 | 0 | 66 | 60 | 70.5775 | 3442.99
3715 | 126609 | 0 | 66 | 60 | 71.9465 | 3442.63
3716 | 126354 | 0 | 65 | 59 | 73.8499 | 3442.33
3717 | 126164 | 0 | 64 | 58 | 77.1416 | 3442.21
3718 | 126097 | 0 | 64 | 58 | 76.5979 | 3442.1
3719 | 126172 | 0 | 63 | 59 | 75.5085 | 3442.14
3720 | 126187 | 0 | 60 | 58 | 77.8792 | 9095.81
3721 | 126091 | 0 | 60 | 58 | 78.6332 | 9095.96
3722 | 125895 | 0 | 58 | 57 | 78.6245 | 9095.31
3723 | 153568 | 0 | 58 | 56 | 83.8715 | 9095.27
3724 | 129163 | 0 | 57 | 55 | 80.6556 | 10096.8
3725 | 225258 | 0 | 56 | 54 | 124.744 | 12326.2
3726 | 675674 | -13951.3 | 56 | 54 | 253.431 | 33325.7
3727 | 657389 | -25218.2 | 56 | 53 | 275.236 | 36552.9
3728 | 633070 | -19150.6 | 56 | 52 | 270.317 | 46262.8
3729 | 604866 | -17207.8 | 56 | 49 | 272.624 | 72111.6
3730 | 617540 | -14278.5 | 59 | 50 | 263.743 | 73727.9
3731 | 629079 | -10404.7 | 62 | 52 | 250.881 | 73728.4
3732 | 634305 | -8578.75 | 63 | 53 | 250.311 | 73728.9
3733 | 714062 | -12188.4 | 63 | 53 | 272.176 | 73729.8
3734 | 767627 | -14106.6 | 64 | 54 | 283.912 | 72114.7
3735 | 851778 | -14596.4 | 66 | 56 | 307.945 | 65652.9
3736 | 878274 | -13984 | 67 | 57 | 304.807 | 54344.9
3737 | 778900 | -11562.2 | 66 | 57 | 275.495 | 41421.8
3738 | 518007 | -8802.88 | 65 | 57 | 189.236 | 25268.3
3739 | 186543 | 0 | 64 | 56 | 108.013 | 18000
3740 | 166944 | 0 | 64 | 56 | 99.6899 | 17194.4
3741 | 153991 | 0 | 64 | 57 | 92.0184 | 10720.8
3742 | 143232 | 0 | 63 | 58 | 83.2246 | 10460.7
3743 | 138381 | 0 | 63 | 58 | 79.7827 | 9102.2
3744 | 137178 | 0 | 63 | 59 | 78.8207 | 9102.09
3745 | 136204 | 0 | 63 | 58 | 78.7756 | 9101.98
3746 | 135613 | 0 | 63 | 58 | 78.748 | 9101.84
3747 | 135003 | 0 | 63 | 58 | 78.7198 | 9101.69
3748 | 138340 | 0 | 62 | 58 | 80.8658 | 10103.2
3749 | 245361 | 0 | 62 | 58 | 125.815 | 12332.1
3750 | 697551 | -9629.25 | 62 | 58 | 254.038 | 33331.4
3751 | 798481 | -14302 | 63 | 58 | 292.887 | 36558.3
3752 | 827114 | -16544.6 | 63 | 58 | 304.337 | 46266.6
3753 | 869439 | -17327.9 | 63 | 59 | 306.62 | 72114.6
3754 | 903139 | -14669.6 | 66 | 60 | 302.064 | 73730.8
3755 | 854669 | -11343.7 | 67 | 61 | 285.346 | 73731.2
3756 | 902779 | -10044 | 68 | 62 | 288.398 | 73731.5
3757 | 1040430 | -12930.3 | 70 | 63 | 314.904 | 73732.2
3758 | 1108150 | -15570.2 | 71 | 64 | 326.134 | 72117.2
3759 | 1147970 | -16637.1 | 72 | 64 | 330.262 | 65655.7
3760 | 1132430 | -16063.6 | 72 | 64 | 324.448 | 54347.4
3761 | 1034160 | -13012.4 | 71 | 64 | 294.281 | 41424.2
3762 | 705028 | -9053.5 | 71 | 64 | 204.282 | 25270.1
3763 | 191786 | 0 | 70 | 64 | 115.906 | 18001.8
3764 | 171692 | 0 | 69 | 64 | 102.917 | 17196
3765 | 158090 | 0 | 68 | 63 | 92.1259 | 10721.8
3766 | 147233 | 0 | 68 | 63 | 83.8824 | 10461.4
3767 | 142360 | 0 | 67 | 63 | 79.8627 | 9102.52
3768 | 140810 | 0 | 67 | 63 | 79.5744 | 9102.27
3769 | 139979 | 0 | 66 | 63 | 79.229 | 9102.01
3770 | 139080 | 0 | 66 | 63 | 79.4511 | 9101.8
3771 | 138346 | 0 | 66 | 63 | 79.4163 | 9101.56
3772 | 141600 | 0 | 66 | 63 | 81.4317 | 10102.8
3773 | 260415 | 0 | 66 | 63 | 126.728 | 12331.8
3774 | 966745 | -6869.52 | 67 | 64 | 261.785 | 33330.8
3775 | 1057560 | -16782.2 | 67 | 64 | 312.043 | 36557.4
3776 | 1087030 | -17695.2 | 68 | 65 | 321.524 | 46266.5
3777 | 1192760 | -17357.3 | 73 | 67 | 331.81 | 72115
3778 | 1264440 | -14375 | 76 | 68 | 327.123 | 73731
3779 | 1183110 | -10207 | 79 | 68 | 308.433 | 73731.2
3780 | 1215050 | -9199.56 | 80 | 68 | 310.547 | 73732.6
3781 | 1386090 | -12222.7 | 81 | 69 | 338.782 | 73734.1
3782 | 1341370 | -16440.7 | 80 | 67 | 342.614 | 72118.5
3783 | 1422150 | -17862.6 | 81 | 68 | 348.652 | 65657.1
3784 | 1444980 | -20956 | 81 | 68 | 344.373 | 54349
3785 | 1366140 | -23924.2 | 81 | 68 | 316.249 | 41425.8
3786 | 932529 | -18869.4 | 79 | 67 | 218.498 | 25272.1
3787 | 194114 | 0 | 76 | 66 | 115.128 | 18003.1
3788 | 174009 | 0 | 73 | 66 | 103.404 | 17196.2
3789 | 159667 | 0 | 71 | 62 | 94.7193 | 10721.2
3790 | 148877 | 0 | 69 | 60 | 83.4657 | 10460
3791 | 143794 | 0 | 66 | 58 | 79.3627 | 9100.69
3792 | 142216 | 0 | 60 | 56 | 77.725 | 9100.17
3793 | 141378 | 0 | 60 | 57 | 79.2078 | 9099.84
3794 | 140313 | 0 | 58 | 56 | 79.1596 | 9099.71
3795 | 139345 | 0 | 57 | 55 | 79.1155 | 9099.83
3796 | 142314 | 0 | 57 | 55 | 81.2316 | 10101.6
3797 | 244350 | 0 | 57 | 54 | 125.185 | 12331
3798 | 715508 | -8652.37 | 61 | 56 | 243.818 | 33330.1
3799 | 824280 | -23121.1 | 63 | 56 | 297.926 | 36557.5
3800 | 891001 | -21311.1 | 67 | 57 | 310.072 | 46267.1
3801 | 912336 | -21004.2 | 69 | 57 | 311.059 | 72117.1
3802 | 921017 | -17380.2 | 71 | 57 | 304.103 | 73734.5
3803 | 849688 | -13502.5 | 72 | 57 | 287.044 | 73735.4
3804 | 928268 | -14625.3 | 75 | 59 | 293.816 | 73735.6
3805 | 1013500 | -14814 | 77 | 59 | 315.689 | 73735.2
3806 | 1072430 | -18347.6 | 77 | 59 | 325.411 | 72119.5
3807 | 1115940 | -19903.8 | 78 | 59 | 329.16 | 65657.9
3808 | 1109580 | -18849.5 | 79 | 59 | 323.816 | 54350
3809 | 1031650 | -20184.3 | 79 | 59 | 296.08 | 41426.6
3810 | 689118 | -11081.8 | 75 | 59 | 204.338 | 25272.7
3811 | 194409 | 0 | 72 | 59 | 111.74 | 18003.6
3812 | 174313 | 0 | 67 | 59 | 100.958 | 17197
3813 | 160444 | 0 | 64 | 57 | 93.562 | 10722.4
3814 | 149305 | 0 | 62 | 56 | 84.7245 | 10461.6
3815 | 144402 | 0 | 60 | 56 | 80.7226 | 9102.66
3816 | 142670 | 0 | 60 | 56 | 80.9376 | 9102.18
3817 | 141447 | 0 | 57 | 54 | 80.8455 | 9101.83
3818 | 140702 | 0 | 57 | 55 | 80.7894 | 9101.58
3819 | 139549 | 0 | 57 | 54 | 80.7045 | 9101.82
3820 | 142436 | 0 | 56 | 53 | 82.7794 | 10103.7
3821 | 242392 | 0 | 56 | 53 | 131.639 | 12332.7
3822 | 591411 | -10022.1 | 58 | 53 | 236.389 | 33332.4
3823 | 729687 | -24817.2 | 62 | 54 | 293.173 | 36559.7
3824 | 788337 | -22895.9 | 66 | 54 | 303.863 | 46268
3825 | 877569 | -21401 | 70 | 56 | 309.98 | 72116.4
3826 | 931629 | -17399.3 | 74 | 57 | 306.417 | 73734.5
3827 | 895463 | -12743.6 | 76 | 57 | 291.054 | 73735.5
3828 | 959884 | -17059.2 | 78 | 59 | 294.574 | 73736
3829 | 1046620 | -14414.3 | 79 | 59 | 317.551 | 73735.9
3830 | 1161520 | -18028.9 | 81 | 61 | 330.777 | 72120.1
3831 | 1170840 | -19817.2 | 81 | 60 | 332.584 | 65658.7
3832 | 1177030 | -24129.1 | 82 | 60 | 327.541 | 54350.7
3833 | 1116760 | -23836.4 | 81 | 61 | 300.847 | 41427.3
3834 | 792963 | -22377.1 | 80 | 61 | 209.956 | 25273.4
3835 | 194962 | 0 | 76 | 61 | 114.938 | 18004.3
3836 | 174434 | 0 | 73 | 60 | 103.237 | 17197.3
3837 | 160923 | 0 | 71 | 59 | 94.7538 | 10722.6
3838 | 149752 | 0 | 70 | 58 | 83.8258 | 10461.3
3839 | 144999 | 0 | 70 | 59 | 80.39 | 9102.08
3840 | 143070 | 0 | 69 | 59 | 75.447 | 9101.46
3841 | 142026 | 0 | 68 | 59 | 75.3544 | 9100.94
3842 | 141243 | 0 | 68 | 60 | 75.5862 | 9101.16
3843 | 140288 | 0 | 68 | 60 | 75.5404 | 9101.04
3844 | 139467 | 0 | 68 | 60 | 73.9008 | 9101
3845 | 138823 | 0 | 69 | 61 | 72.4711 | 9100.91
3846 | 138241 | 0 | 68 | 62 | 71.736 | 9100.79
3847 | 457676 | -3709.22 | 65 | 62 | 115.571 | 9100.67
3848 | 402894 | -6146.91 | 64 | 63 | 114.138 | 9100.4
3849 | 371448 | -11428.6 | 64 | 63 | 113.82 | 9116.36
3850 | 414396 | -13130.8 | 67 | 65 | 116.762 | 9118.35
3851 | 445951 | -13848 | 69 | 66 | 118.44 | 9120.2
3852 | 504179 | -14299.6 | 72 | 68 | 122.791 | 9121.38
3853 | 538973 | -14516.3 | 73 | 69 | 124.485 | 9122.18
3854 | 133668 | 0 | 74 | 70 | 74.4251 | 9122.87
3855 | 133438 | 0 | 75 | 71 | 73.7536 | 9123.47
3856 | 133360 | 0 | 78 | 73 | 73.1497 | 9117.07
3857 | 133186 | 0 | 80 | 74 | 72.6417 | 9113.97
3858 | 132604 | 0 | 78 | 71 | 72.5607 | 9111.39
3859 | 132372 | 0 | 77 | 71 | 74.8051 | 9109.54
3860 | 132162 | 0 | 75 | 71 | 79.3722 | 9107.68
3861 | 131939 | 0 | 75 | 71 | 82.5065 | 9106.26
3862 | 131399 | 0 | 74 | 68 | 79.1015 | 9105.14
3863 | 131167 | 0 | 71 | 68 | 77.6235 | 9104.34
3864 | 130929 | 0 | 70 | 69 | 73.6252 | 3450.09
3865 | 130440 | 0 | 70 | 67 | 73.8721 | 3449.38
3866 | 130155 | 0 | 69 | 67 | 73.5497 | 3449.04
3867 | 129782 | 0 | 68 | 66 | 73.4945 | 3448.73
3868 | 129464 | 0 | 66 | 65 | 71.544 | 3448.49
3869 | 129272 | 0 | 67 | 66 | 70.6773 | 3448.28
3870 | 129030 | 0 | 67 | 66 | 67.8313 | 3448.18
3871 | 128891 | 0 | 69 | 67 | 68.2787 | 3448.15
3872 | 128679 | 0 | 70 | 67 | 68.2148 | 3447.79
3873 | 128470 | 0 | 72 | 67 | 69.1435 | 3447.31
3874 | 192148 | 0 | 70 | 67 | 74.6881 | 3446.91
3875 | 128169 | 0 | 71 | 68 | 68.5285 | 3446.09
3876 | 128180 | 0 | 73 | 69 | 68.7896 | 3445.25
3877 | 127055 | 0 | 63 | 60 | 65.3129 | 3444.07
3878 | 127290 | 0 | 61 | 59 | 67.2517 | 3443.06
3879 | 126831 | 0 | 59 | 56 | 67.5326 | 3441.79
3880 | 172295 | 0 | 57 | 55 | 74.1898 | 3441.3
3881 | 126473 | 0 | 56 | 54 | 68.3428 | 3441
3882 | 126377 | 0 | 56 | 54 | 68.5816 | 3441.03
3883 | 126218 | 0 | 55 | 54 | 70.4537 | 3441.61
3884 | 125875 | 0 | 54 | 53 | 73.9128 | 3442.2
3885 | 125501 | 0 | 52 | 51 | 77.2361 | 3442.97
3886 | 125399 | 0 | 52 | 51 | 76.4312 | 3443.81
3887 | 125119 | 0 | 51 | 50 | 75.6187 | 3444.79
3888 | 132542 | -2425.76 | 51 | 50 | 85.1917 | 9099.44
3889 | 124995 | 0 | 50 | 49 | 78.5893 | 9100.57
3890 | 124914 | 0 | 50 | 49 | 78.5801 | 9100.9
3891 | 124750 | 0 | 51 | 49 | 78.5727 | 9101.75
3892 | 128316 | -6248.71 | 51 | 49 | 87.1521 | 10104
3893 | 175561 | 0 | 51 | 50 | 118.218 | 12334.1
3894 | 409534 | -36437.7 | 52 | 50 | 239.989 | 33334.1
3895 | 493833 | -23020.7 | 52 | 50 | 256.468 | 36561.9
3896 | 545191 | -33450.2 | 53 | 51 | 273.531 | 46266.6
3897 | 585891 | -22020 | 55 | 52 | 272.774 | 72114.4
3898 | 606233 | -19779.4 | 57 | 53 | 265.576 | 73730.7
3899 | 615161 | -13521.3 | 60 | 55 | 250.335 | 73731
3900 | 677939 | -10739.1 | 63 | 57 | 253.704 | 73731.4
3901 | 845708 | -12146.2 | 66 | 59 | 281.84 | 73732
3902 | 947057 | -13706.7 | 69 | 60 | 296.277 | 72116.9
3903 | 1076800 | -13905.2 | 72 | 62 | 311.203 | 65654.8
3904 | 1151270 | -12827.9 | 74 | 64 | 324.645 | 54346.6
3905 | 1102200 | -18726.3 | 74 | 64 | 278.604 | 41423.3
3906 | 795474 | -22222.8 | 75 | 64 | 188.228 | 25269.6
3907 | 187355 | 0 | 72 | 64 | 106.312 | 18001.2
3908 | 167080 | 0 | 70 | 62 | 98.6552 | 17195.4
3909 | 154387 | 0 | 65 | 62 | 90.765 | 10721.5
3910 | 143325 | 0 | 63 | 61 | 82.9699 | 10461
3911 | 138748 | 0 | 62 | 61 | 79.504 | 9102.24
3912 | 137255 | 0 | 61 | 60 | 78.4947 | 9102.19
3913 | 136293 | 0 | 59 | 58 | 78.4165 | 9102.09
3914 | 135403 | 0 | 59 | 56 | 78.6305 | 9102.39
3915 | 134720 | 0 | 57 | 54 | 78.5994 | 9102.26
3916 | 137900 | 0 | 55 | 53 | 81.0308 | 10103.9
3917 | 234143 | 0 | 55 | 53 | 124.571 | 12333.5
3918 | 597306 | -11574.2 | 58 | 55 | 243.802 | 33333.1
3919 | 771354 | -17319.3 | 63 | 56 | 271.437 | 36560.5
3920 | 857171 | -16631.3 | 68 | 57 | 283.909 | 46267.9
3921 | 883706 | -16226.3 | 69 | 57 | 289.952 | 72117.4
3922 | 854364 | -14017.1 | 70 | 56 | 298.361 | 73735.1
3923 | 839563 | -9657.41 | 73 | 58 | 286.164 | 73735.6
3924 | 789004 | -9751.15 | 71 | 57 | 281.45 | 73735.4
3925 | 908497 | -12717.6 | 72 | 58 | 307.557 | 73735.2
3926 | 923691 | -16567.1 | 70 | 57 | 313.273 | 72118.5
3927 | 997145 | -17397.2 | 72 | 58 | 320.738 | 65656.4
3928 | 897403 | -17218.7 | 71 | 55 | 308.687 | 54348.6
3929 | 844481 | -13792.8 | 71 | 56 | 282.46 | 41425.5
3930 | 613345 | -13850.8 | 71 | 55 | 197.369 | 25271.1
3931 | 191737 | 0 | 69 | 55 | 111.048 | 18002.8
3932 | 171986 | 0 | 61 | 55 | 96.8086 | 17197
3933 | 158066 | 0 | 58 | 54 | 91.7823 | 10723
3934 | 147044 | 0 | 57 | 54 | 83.5437 | 10462.8
3935 | 142028 | 0 | 56 | 53 | 79.838 | 9104.2
3936 | 140411 | 0 | 55 | 52 | 79.2834 | 9104.24
3937 | 139528 | 0 | 54 | 52 | 79.2427 | 9104.86
3938 | 138500 | 0 | 53 | 51 | 79.1961 | 9105.39
3939 | 137725 | 0 | 53 | 51 | 79.1608 | 9106.03
3940 | 140638 | 0 | 53 | 51 | 81.1554 | 10108.2
3941 | 221190 | 0 | 54 | 52 | 124.493 | 12338.1
3942 | 467321 | -16298.6 | 55 | 53 | 238.514 | 33338
3943 | 604639 | -29747.2 | 56 | 54 | 270.429 | 36565.5
3944 | 650937 | -25013 | 58 | 54 | 276.224 | 46270.8
3945 | 728004 | -22747.9 | 61 | 56 | 297.656 | 72118.1
3946 | 782573 | -19609 | 62 | 58 | 292.11 | 73734.2
3947 | 773026 | -15264.1 | 64 | 60 | 278.902 | 73734.3
3948 | 846151 | -12834.8 | 67 | 62 | 284.132 | 73734.6
3949 | 1030780 | -14801.1 | 70 | 64 | 313.628 | 73735
3950 | 1140470 | -17435.5 | 73 | 65 | 328.112 | 72119.8
3951 | 1207250 | -18081 | 76 | 65 | 334.29 | 65657.6
3952 | 1168000 | -17498.3 | 74 | 64 | 325.739 | 54349.4
3953 | 1057810 | -13806 | 73 | 63 | 295.386 | 41426.1
3954 | 750497 | -10228.2 | 74 | 64 | 206.42 | 25272.2
3955 | 193007 | 0 | 72 | 63 | 111.862 | 18003.7
3956 | 173072 | 0 | 69 | 63 | 98.7085 | 17197.8
3957 | 159539 | 0 | 66 | 62 | 91.5724 | 10723.8
3958 | 148383 | 0 | 64 | 61 | 83.2414 | 10463.4
3959 | 143520 | 0 | 62 | 61 | 79.4656 | 9104.57
3960 | 141945 | 0 | 65 | 62 | 80.2199 | 9104.54
3961 | 140819 | 0 | 61 | 60 | 78.1973 | 9104.59
3962 | 139951 | 0 | 61 | 60 | 79.1795 | 9104.81
3963 | 138880 | 0 | 59 | 58 | 78.8398 | 9104.84
3964 | 142449 | 0 | 62 | 61 | 81.8306 | 10106.5
3965 | 250074 | 0 | 62 | 61 | 126.13 | 12335.8
3966 | 756134 | -9316.56 | 62 | 60 | 251.261 | 33335.3
3967 | 849137 | -21681.8 | 62 | 60 | 281.047 | 36562.2
3968 | 870177 | -21439.8 | 63 | 60 | 306.958 | 46269.4
3969 | 929289 | -21612 | 65 | 61 | 311.459 | 72116.9
3970 | 967983 | -18459.1 | 67 | 62 | 305.52 | 73733
3971 | 917104 | -14650.2 | 68 | 63 | 288.774 | 73733.3
3972 | 1000560 | -12474.8 | 72 | 64 | 296.717 | 73733.6
3973 | 1163950 | -15138.4 | 74 | 65 | 324.267 | 73734.2
3974 | 1259510 | -18434.1 | 76 | 66 | 336.659 | 72119.1
3975 | 1342860 | -19519.8 | 78 | 67 | 342.731 | 65657.6
3976 | 1350820 | -18331.2 | 78 | 67 | 338.147 | 54349.9
3977 | 1240200 | -14743.7 | 76 | 67 | 308.06 | 41426.7
3978 | 833075 | -11607 | 73 | 66 | 210.614 | 25272.9
3979 | 193359 | 0 | 71 | 64 | 112.187 | 18003.7
3980 | 173932 | 0 | 70 | 65 | 99.1748 | 17197.5
3981 | 160257 | 0 | 69 | 65 | 92.2773 | 10723.1
3982 | 149233 | 0 | 70 | 66 | 84.3437 | 10462.6
3983 | 144293 | 0 | 72 | 67 | 80.9983 | 9103.6
3984 | 142799 | 0 | 73 | 68 | 80.2144 | 9103.25
3985 | 141861 | 0 | 74 | 68 | 80.2163 | 9102.82
3986 | 141027 | 0 | 74 | 68 | 79.8946 | 9102.26
3987 | 139822 | 0 | 74 | 65 | 79.8349 | 9101.58
3988 | 142701 | 0 | 73 | 60 | 81.5153 | 10102.3
3989 | 270655 | 0 | 72 | 58 | 126.976 | 12330.7
3990 | 989205 | -4428.8 | 70 | 60 | 257.209 | 33329.1
3991 | 1108160 | -19443.3 | 69 | 62 | 294.165 | 36555.4
3992 | 1116780 | -20787.4 | 70 | 63 | 319.574 | 46267.3
3993 | 1082210 | -21561 | 71 | 61 | 321.215 | 72115.4
3994 | 1014840 | -18681.4 | 72 | 59 | 309.411 | 73732
3995 | 921123 | -15080 | 72 | 59 | 290.491 | 73734.5
3996 | 937110 | -13995.5 | 73 | 59 | 292.347 | 73734.7
3997 | 1054510 | -17339.2 | 75 | 60 | 317.491 | 73734.5
3998 | 1097330 | -20734.4 | 75 | 60 | 325.319 | 72119.2
3999 | 1068190 | -22152.1 | 76 | 58 | 324.57 | 65657.7
4000 | 1093170 | -21264.6 | 76 | 59 | 320.55 | 54349.7
4001 | 970703 | -26074.8 | 75 | 57 | 290.511 | 41426.1
4002 | 709643 | -29942.2 | 73 | 55 | 182.345 | 25272.1
4003 | 194042 | 0 | 71 | 54 | 107.322 | 18002.9
4004 | 174068 | 0 | 65 | 53 | 97.5102 | 17196.9
4005 | 160487 | 0 | 62 | 53 | 91.4563 | 10722.5
4006 | 149172 | 0 | 58 | 52 | 83.1299 | 10461.9
4007 | 144050 | 0 | 56 | 51 | 79.9301 | 9103.21
4008 | 142295 | 0 | 56 | 52 | 75.3168 | 9103.4
4009 | 140839 | 0 | 55 | 50 | 75.2504 | 9103.77
4010 | 140016 | 0 | 52 | 49 | 75.2125 | 9104.93
4011 | 139046 | 0 | 51 | 49 | 75.1685 | 9105.25
4012 | 138000 | 0 | 50 | 48 | 73.5211 | 9105.78
4013 | 137085 | 0 | 50 | 47 | 71.6936 | 9106.84
4014 | 136654 | 0 | 54 | 50 | 68.7065 | 9107.26
4015 | 223587 | -12733.6 | 58 | 51 | 87.4384 | 9107.88
4016 | 240874 | -13492.3 | 61 | 54 | 89.4441 | 9108.22
4017 | 266805 | -16971.9 | 64 | 55 | 100.259 | 9119.9
4018 | 310780 | -17916.1 | 68 | 56 | 110.798 | 9121.28
4019 | 342689 | -17405.4 | 71 | 57 | 112.743 | 9122.89
4020 | 370319 | -17293 | 73 | 58 | 114.426 | 9123.68
4021 | 399942 | -16884 | 75 | 58 | 116.656 | 9124.03
4022 | 188100 | 0 | 75 | 59 | 83.9308 | 9124.56
4023 | 189487 | 0 | 77 | 61 | 83.4326 | 9125.07
4024 | 132005 | 0 | 77 | 61 | 72.5554 | 9118.97
4025 | 176260 | 0 | 78 | 62 | 79.1151 | 9115.75
4026 | 131631 | 0 | 77 | 61 | 72.0541 | 9113.36
4027 | 131638 | 0 | 73 | 61 | 71.6757 | 9111.34
4028 | 131364 | 0 | 71 | 61 | 76.0702 | 9109.79
4029 | 131304 | 0 | 70 | 62 | 79.735 | 9108.51
4030 | 130846 | 0 | 68 | 61 | 78.571 | 9107.67
4031 | 130419 | 0 | 69 | 60 | 78.5919 | 9107.12
4032 | 130218 | 0 | 68 | 60 | 73.515 | 3452.87
4033 | 129976 | 0 | 66 | 60 | 73.1679 | 3452.59
4034 | 129676 | 0 | 64 | 60 | 73.0868 | 3452.42
4035 | 129219 | 0 | 62 | 59 | 73.0014 | 3452.27
4036 | 128860 | 0 | 60 | 58 | 71.3232 | 3452.3
4037 | 128575 | 0 | 60 | 58 | 70.1369 | 3452.13
4038 | 128407 | 0 | 61 | 59 | 68.5605 | 3452.14
4039 | 128327 | 0 | 63 | 61 | 68.6639 | 3452.57
4040 | 128126 | 0 | 63 | 62 | 67.7206 | 3452.9
4041 | 127857 | 0 | 65 | 63 | 68.3208 | 3453.17
4042 | 127987 | 0 | 73 | 67 | 70.3462 | 3453.04
4043 | 178913 | 0 | 76 | 67 | 75.3853 | 3452.78
4044 | 191772 | 0 | 78 | 69 | 80.9301 | 3451.6
4045 | 202172 | 0 | 81 | 71 | 82.5531 | 3449.67
4046 | 203351 | 0 | 81 | 71 | 83.0762 | 3448.08
4047 | 264038 | 0 | 84 | 72 | 93.7049 | 3446.21
4048 | 273741 | 0 | 86 | 74 | 82.702 | 3444.32
4049 | 274988 | 0 | 86 | 75 | 81.8639 | 3442.84
4050 | 274042 | 0 | 85 | 75 | 81.8159 | 3441.02
4051 | 214577 | 0 | 84 | 75 | 78.7738 | 3439.38
4052 | 128390 | 0 | 80 | 75 | 74.3629 | 3438.03
4053 | 128424 | 0 | 79 | 74 | 77.9406 | 3436.8
4054 | 128497 | 0 | 78 | 74 | 77.1443 | 3435.7
4055 | 128285 | 0 | 76 | 72 | 76.3339 | 3434.58
4056 | 128585 | 0 | 76 | 72 | 79.3192 | 9087.27
4057 | 128460 | 0 | 76 | 71 | 79.3133 | 9086.42
4058 | 128392 | 0 | 77 | 71 | 79.3099 | 9084.88
4059 | 128313 | 0 | 77 | 71 | 79.306 | 9083.79
4060 | 132570 | 0 | 77 | 71 | 81.3798 | 10084.2
4061 | 292122 | 0 | 77 | 71 | 129.092 | 12312.3
4062 | 1677950 | -3716.32 | 77 | 71 | 299.473 | 33310.4
4063 | 1680600 | -27947.9 | 79 | 71 | 333.759 | 36536.3
4064 | 1675220 | -19511.4 | 84 | 73 | 338.583 | 46258
4065 | 1729020 | -16787 | 86 | 74 | 339.463 | 72108.3
4066 | 1733930 | -26965.1 | 89 | 73 | 340.484 | 73726.5
4067 | 1630640 | -34532.1 | 88 | 74 | 325.599 | 73727.8
4068 | 1642590 | -34965.4 | 89 | 73 | 327.98 | 73728.7
4069 | 1838300 | -31925.2 | 93 | 75 | 357.48 | 73729
4070 | 1749580 | -32011.6 | 93 | 73 | 356.628 | 72114
4071 | 1804560 | -32181.6 | 93 | 73 | 362.13 | 65652.9
4072 | 1817380 | -31754.7 | 93 | 73 | 359.921 | 54345
4073 | 1790470 | -34686 | 92 | 74 | 340.26 | 41422
4074 | 1360970 | -46147.6 | 91 | 74 | 246.455 | 25268.5
4075 | 191641 | 0 | 89 | 73 | 107.371 | 17999.8
4076 | 171268 | 0 | 84 | 74 | 99.6632 | 17192.8
4077 | 158300 | 0 | 81 | 74 | 92.7633 | 10715.4
4078 | 147494 | 0 | 79 | 73 | 84.2265 | 10452.4
4079 | 142592 | 0 | 78 | 73 | 80.5025 | 9091.88
4080 | 141110 | 0 | 77 | 72 | 79.5218 | 9090.14
4081 | 140360 | 0 | 76 | 72 | 79.4836 | 9088.73
4082 | 139549 | 0 | 76 | 71 | 79.443 | 9087.53
4083 | 138702 | 0 | 74 | 69 | 79.0751 | 9086.41
4084 | 222703 | 0 | 72 | 68 | 89.1253 | 10086.9
4085 | 291146 | 0 | 70 | 65 | 127.709 | 12315
4086 | 1261260 | 0 | 68 | 62 | 268.909 | 33313.4
4087 | 1177100 | -18903.6 | 69 | 60 | 295.689 | 36539.7
4088 | 1203650 | -19118.8 | 72 | 62 | 325.465 | 46260
4089 | 1272000 | -19624.3 | 75 | 64 | 335.599 | 72110.7
4090 | 1344340 | -16426.1 | 77 | 66 | 330.465 | 73728.5
4091 | 1292360 | -11726.5 | 81 | 68 | 314.771 | 73729.8
4092 | 1395810 | -22647.7 | 83 | 69 | 320.657 | 73730.4
4093 | 1546470 | -25419.3 | 84 | 70 | 347.312 | 73730.6
4094 | 1661800 | -28687.1 | 86 | 72 | 361.021 | 72115.3
4095 | 1720850 | -34633.6 | 87 | 72 | 371.499 | 65654
4096 | 1778900 | -34304.3 | 88 | 73 | 372.857 | 54346.2
4097 | 1750720 | -37276.1 | 87 | 74 | 335.53 | 41423
4098 | 1331270 | -49134.7 | 85 | 74 | 241.212 | 25269.4
4099 | 195650 | 0 | 83 | 73 | 118.233 | 18000.6
4100 | 174921 | 0 | 82 | 73 | 100.706 | 17193.5
4101 | 161746 | 0 | 81 | 73 | 92.938 | 10717.1
4102 | 150748 | 0 | 79 | 72 | 84.3905 | 10454.6
4103 | 145690 | 0 | 79 | 72 | 80.6583 | 9094.39
4104 | 144158 | 0 | 79 | 72 | 80.0998 | 9092.74
4105 | 143153 | 0 | 78 | 71 | 80.0489 | 9091.39
4106 | 142224 | 0 | 78 | 70 | 80.0022 | 9090.11
4107 | 141363 | 0 | 77 | 69 | 79.9589 | 9088.85
4108 | 144690 | 0 | 76 | 68 | 81.9875 | 10089.1
4109 | 308239 | 0 | 71 | 69 | 128.622 | 12317.1
4110 | 1554460 | 0 | 71 | 69 | 294.849 | 33315.3
4111 | 1552800 | -22182.4 | 71 | 70 | 321.439 | 36541.2
4112 | 1443980 | -22657.2 | 71 | 70 | 336.792 | 46260.6
4113 | 1436280 | -23188.2 | 72 | 70 | 344.168 | 72110.1
4114 | 1504300 | -19797.5 | 75 | 71 | 342.104 | 73726.4
4115 | 1459590 | -14741.1 | 80 | 73 | 325.199 | 73727
4116 | 1527040 | -17981.3 | 82 | 73 | 330.122 | 73729
4117 | 1747180 | -25313.8 | 85 | 75 | 360.394 | 73730.3
4118 | 1709640 | -31481 | 83 | 74 | 364.74 | 72115.2
4119 | 1764020 | -34959.6 | 81 | 75 | 371.321 | 65653.7
4120 | 1750840 | -25249.9 | 81 | 75 | 362.905 | 54345.9
4121 | 1672150 | -22792.3 | 80 | 75 | 333.458 | 41422.2
4122 | 1154170 | -19412.2 | 78 | 74 | 230.72 | 25268.8
4123 | 195636 | 0 | 74 | 68 | 108.927 | 18000.3
4124 | 175203 | 0 | 73 | 68 | 100.006 | 17193.1
4125 | 161666 | 0 | 71 | 66 | 92.1681 | 10717.6
4126 | 150771 | 0 | 74 | 68 | 85.1873 | 10456.1
4127 | 145293 | 0 | 72 | 65 | 79.943 | 9096.66
4128 | 143827 | 0 | 70 | 64 | 79.1867 | 9095.87
4129 | 142958 | 0 | 70 | 64 | 79.6872 | 9094.79
4130 | 142031 | 0 | 69 | 64 | 79.3285 | 9094.13
4131 | 141203 | 0 | 65 | 64 | 78.3441 | 9093.48
4132 | 143964 | 0 | 64 | 63 | 81.2001 | 10094.4
4133 | 275763 | 0 | 65 | 64 | 127.788 | 12322.9
4134 | 1163730 | -4780.4 | 66 | 65 | 265.386 | 33321.9
4135 | 1213570 | -24064.7 | 67 | 64 | 318.248 | 36548.6
4136 | 1257640 | -23711.9 | 70 | 66 | 332.958 | 46262.2
4137 | 1318630 | -23203.6 | 72 | 67 | 337.064 | 72111.9
4138 | 1369320 | -19663.7 | 75 | 68 | 333.627 | 73729.6
4139 | 1274670 | -15112.2 | 77 | 69 | 314.26 | 73730.9
4140 | 1238870 | -13661.2 | 79 | 68 | 312.726 | 73732.2
4141 | 1420670 | -17377.7 | 79 | 69 | 341.254 | 73732.3
4142 | 1355100 | -20934.2 | 79 | 66 | 343.485 | 72116
4143 | 1362560 | -22416.5 | 81 | 65 | 344.903 | 65654.9
4144 | 1309860 | -21895 | 77 | 64 | 336.216 | 54347.1
4145 | 1273770 | -26800.8 | 78 | 65 | 310.592 | 41423.9
4146 | 881790 | -32883.9 | 76 | 63 | 215.376 | 25270
4147 | 194546 | 0 | 75 | 61 | 115.992 | 18001.1
4148 | 174991 | 0 | 71 | 62 | 101.459 | 17194.5
4149 | 161197 | 0 | 70 | 61 | 94.7755 | 10719.4
4150 | 150181 | 0 | 66 | 60 | 82.8763 | 10458.1
4151 | 145323 | 0 | 65 | 61 | 79.9222 | 9098.84
4152 | 143622 | 0 | 64 | 61 | 79.3226 | 9098.28
4153 | 142412 | 0 | 64 | 60 | 79.5273 | 9097.98
4154 | 141564 | 0 | 63 | 60 | 79.1887 | 9097.81
4155 | 140429 | 0 | 65 | 59 | 80.0021 | 9097.69
4156 | 143636 | 0 | 67 | 59 | 82.1052 | 10099.1
4157 | 260429 | 0 | 67 | 59 | 126.58 | 12328.2
4158 | 923913 | -5866.04 | 66 | 59 | 253.589 | 33327.2
4159 | 1060590 | -23680.5 | 70 | 60 | 313.43 | 36553.8
4160 | 1130820 | -23132 | 73 | 62 | 325.838 | 46265.2
4161 | 1217700 | -22453.8 | 77 | 64 | 331.771 | 72115.8
4162 | 1265960 | -18568.5 | 81 | 65 | 325.893 | 73733.4
4163 | 1141270 | -14041.7 | 82 | 64 | 305.213 | 73734.4
4164 | 1258880 | -19307.4 | 83 | 66 | 312.424 | 73734.7
4165 | 1262170 | -23899.4 | 79 | 64 | 330.396 | 73734.6
4166 | 1315130 | -26734.9 | 79 | 65 | 340.252 | 72119.1
4167 | 1267120 | -24650.4 | 67 | 64 | 332.039 | 65657
4168 | 1378530 | -23403.1 | 74 | 67 | 341.552 | 54349
4169 | 1331200 | -19477.7 | 78 | 69 | 314.784 | 41425.2
4170 | 716356 | -15196.5 | 71 | 60 | 203.763 | 25271.4
4171 | 194908 | 0 | 71 | 61 | 114.01 | 18002.5
4172 | 174544 | 0 | 68 | 60 | 100.976 | 17196
4173 | 161060 | 0 | 65 | 59 | 91.6027 | 10721.4
4174 | 149695 | 0 | 61 | 57 | 82.678 | 10460.7
4175 | 144670 | 0 | 62 | 57 | 80.2937 | 9101.71
4176 | 142898 | 0 | 60 | 57 | 74.8346 | 9101.57
4177 | 141756 | 0 | 60 | 57 | 75.2919 | 9101.69
4178 | 140919 | 0 | 61 | 58 | 75.5474 | 9102.47
4179 | 139650 | 0 | 61 | 56 | 75.2326 | 9102.96
4180 | 138762 | 0 | 58 | 54 | 73.3008 | 9103.44
4181 | 137777 | 0 | 57 | 52 | 71.7887 | 9103.82
4182 | 137108 | 0 | 56 | 51 | 70.0667 | 9104.23
4183 | 238378 | -16210.1 | 57 | 51 | 88.4815 | 9104.78
4184 | 241920 | -18087.3 | 58 | 51 | 92.1093 | 9105.29
4185 | 248035 | -26309.4 | 60 | 53 | 88.4804 | 9118.17
4186 | 247485 | -17540.6 | 62 | 54 | 95.7835 | 9120.14
4187 | 254734 | -17461.8 | 62 | 54 | 95.409 | 9121.44
4188 | 266168 | -18045.7 | 63 | 54 | 98.5887 | 9122.4
4189 | 282212 | -18400.2 | 64 | 55 | 101.909 | 9123.18
4190 | 132485 | 0 | 66 | 56 | 73.138 | 9123.84
4191 | 132066 | 0 | 67 | 56 | 72.4162 | 9124.55
4192 | 131811 | 0 | 68 | 56 | 72.3448 | 9119.22
4193 | 131550 | 0 | 69 | 56 | 72.2598 | 9116.7
4194 | 131356 | 0 | 69 | 56 | 71.684 | 9114.96
4195 | 131306 | 0 | 67 | 57 | 72.9547 | 9113.67
4196 | 130862 | 0 | 63 | 56 | 76.0303 | 9112.77
4197 | 130513 | 0 | 60 | 55 | 79.6791 | 9112.07
4198 | 130190 | 0 | 57 | 54 | 78.782 | 9111.63
4199 | 129791 | 0 | 56 | 53 | 77.964 | 9111.6
4200 | 129472 | 0 | 55 | 53 | 73.4576 | 3458.31
4201 | 128971 | 0 | 55 | 52 | 73.4351 | 3458.8
4202 | 128729 | 0 | 54 | 52 | 73.4239 | 3459.58
4203 | 128342 | 0 | 54 | 52 | 73.4065 | 3460.38
4204 | 128011 | 0 | 54 | 52 | 71.7915 | 3461.21
4205 | 127680 | 0 | 54 | 52 | 70.0321 | 3462.07
4206 | 127449 | 0 | 56 | 53 | 68.7135 | 3462.94
4207 | 127326 | 0 | 59 | 55 | 67.2013 | 3463.77
4208 | 127202 | 0 | 62 | 57 | 67.877 | 3464.57
4209 | 127086 | 0 | 66 | 59 | 68.8791 | 3464.65
4210 | 127082 | 0 | 69 | 61 | 68.7178 | 3464.88
4211 | 126963 | 0 | 71 | 62 | 68.5793 | 3464.02
4212 | 170473 | 0 | 74 | 64 | 80.1689 | 3463.32
4213 | 181122 | 0 | 76 | 64 | 80.8329 | 3462.02
4214 | 187064 | 0 | 78 | 66 | 81.446 | 3460.26
4215 | 192350 | 0 | 79 | 67 | 82.1408 | 3458.78
4216 | 177783 | 0 | 80 | 68 | 78.3159 | 3457.18
4217 | 176052 | 0 | 81 | 68 | 77.975 | 3455.56
4218 | 126858 | 0 | 78 | 66 | 70.6052 | 3454.04
4219 | 127095 | 0 | 76 | 66 | 72.0812 | 3452.54
4220 | 127120 | 0 | 75 | 66 | 74.3108 | 3451.09
4221 | 127117 | 0 | 74 | 66 | 77.5559 | 3449.88
4222 | 126828 | 0 | 74 | 65 | 77.019 | 3449.01
4223 | 127010 | 0 | 73 | 65 | 75.9105 | 3448.35
4224 | 187358 | 0 | 73 | 65 | 86.1246 | 9101.31
4225 | 127174 | 0 | 72 | 65 | 78.8989 | 9100.73
4226 | 126938 | 0 | 71 | 64 | 78.8002 | 9099.36
4227 | 127138 | 0 | 71 | 65 | 79.081 | 9098.55
4228 | 130955 | 0 | 71 | 65 | 81.1283 | 10099.1
4229 | 266075 | 0 | 71 | 65 | 127.196 | 12327.6
4230 | 1294540 | -7769.82 | 72 | 66 | 283.401 | 33326.1
4231 | 1345030 | -15998.2 | 74 | 67 | 315.973 | 36552.3
4232 | 1427730 | -11027.5 | 78 | 70 | 325.958 | 46264.8
4233 | 1536080 | -10540.9 | 82 | 72 | 331.118 | 72116.1
4234 | 1601110 | -9006.9 | 84 | 73 | 324.23 | 73733.6
4235 | 1546750 | -12081.3 | 85 | 75 | 304.799 | 73734.5
4236 | 1725940 | -19314.8 | 89 | 77 | 319.119 | 73734.7
4237 | 1886510 | -31124.9 | 91 | 77 | 357.298 | 73734.7
4238 | 1830170 | -32584.8 | 89 | 76 | 358.112 | 72119.3
4239 | 1824130 | -33167.7 | 87 | 75 | 358.005 | 65657.9
4240 | 1866410 | -33250.9 | 88 | 76 | 358.134 | 54349.8
4241 | 1847850 | -36180.5 | 89 | 77 | 340.517 | 41426.5
4242 | 1363570 | -45534.9 | 88 | 76 | 242.606 | 25272.8
4243 | 191287 | 0 | 86 | 75 | 107.469 | 18003.9
4244 | 170487 | 0 | 80 | 74 | 100.154 | 17196.8
4245 | 157635 | 0 | 79 | 75 | 92.7295 | 10720.7
4246 | 146972 | 0 | 79 | 75 | 84.2001 | 10458.1
4247 | 141475 | 0 | 73 | 70 | 79.7987 | 9097.93
4248 | 140184 | 0 | 73 | 71 | 79.3817 | 9096.53
4249 | 139426 | 0 | 74 | 71 | 79.6697 | 9095.27
4250 | 138629 | 0 | 71 | 70 | 78.3981 | 9094.33
4251 | 137966 | 0 | 71 | 70 | 79.1826 | 9093.58
4252 | 216108 | 0 | 72 | 71 | 89.6524 | 10094.2
4253 | 294426 | 0 | 72 | 71 | 129.262 | 12322.6
4254 | 1467310 | -4584.94 | 73 | 69 | 289.587 | 33321.1
4255 | 1523480 | -15957.3 | 73 | 71 | 320.02 | 36547.4
4256 | 1499610 | -17135.8 | 75 | 72 | 329.859 | 46263.2
4257 | 1565080 | -17859.6 | 78 | 73 | 329.544 | 72112.6
4258 | 1537980 | -15291 | 78 | 72 | 333.898 | 73728.7
4259 | 1455910 | -10739.3 | 82 | 74 | 317.269 | 73729.8
4260 | 1593020 | -16960.1 | 84 | 75 | 325.227 | 73731.2
4261 | 1701490 | -13113.1 | 84 | 75 | 355.63 | 73731.5
4262 | 1785090 | -17194.3 | 86 | 76 | 366.35 | 72116.9
4263 | 1827020 | -32682.7 | 87 | 75 | 370.033 | 65655.7
4264 | 1670150 | -33475.5 | 88 | 71 | 349.39 | 54348
4265 | 1638240 | -36715.9 | 87 | 72 | 324.946 | 41424.7
4266 | 1247200 | -47071.4 | 85 | 72 | 233.283 | 25271.1
4267 | 194975 | 0 | 82 | 71 | 108.326 | 18002.2
4268 | 174546 | 0 | 78 | 72 | 99.7038 | 17195
4269 | 161267 | 0 | 75 | 71 | 92.9138 | 10719.1
4270 | 150237 | 0 | 73 | 70 | 83.7077 | 10456.9
4271 | 145112 | 0 | 71 | 69 | 79.8912 | 9096.97
4272 | 143265 | 0 | 70 | 66 | 79.5499 | 9095.87
4273 | 141687 | 0 | 68 | 62 | 79.1228 | 9095.02
4274 | 141033 | 0 | 66 | 60 | 79.0146 | 9094.35
4275 | 140384 | 0 | 64 | 60 | 78.9108 | 9093.8
4276 | 143466 | 0 | 64 | 60 | 81.4382 | 10094.9
4277 | 274594 | 0 | 64 | 60 | 127.423 | 12323.7
4278 | 1101600 | -4839.19 | 68 | 62 | 264.873 | 33322.8
4279 | 1139290 | -22251.2 | 68 | 62 | 292.818 | 36549.5
4280 | 1167190 | -21580.6 | 73 | 63 | 307.653 | 46263.2
4281 | 1192780 | -22442.4 | 70 | 64 | 303.463 | 72112.4
4282 | 1179090 | -19221.2 | 72 | 63 | 313.592 | 73729.5
4283 | 1141910 | -14609.1 | 75 | 65 | 302.385 | 73730.3
4284 | 1176470 | -15235.7 | 77 | 65 | 303.654 | 73731.9
4285 | 1256390 | -15986.8 | 81 | 64 | 328.627 | 73732.4
4286 | 1301900 | -19645.5 | 81 | 64 | 337.095 | 72117.1
4287 | 1379830 | -21174.6 | 81 | 65 | 343.074 | 65655.8
4288 | 1424190 | -29237.3 | 81 | 66 | 340.346 | 54347.9
4289 | 1347220 | -33700.1 | 81 | 66 | 299.042 | 41424.7
4290 | 992379 | -34769.2 | 80 | 66 | 205.842 | 25270.8
4291 | 195444 | 0 | 78 | 66 | 107.683 | 18001.8
4292 | 175227 | 0 | 76 | 66 | 99.9538 | 17194.9
4293 | 161845 | 0 | 71 | 66 | 91.628 | 10719.7
4294 | 150519 | 0 | 68 | 65 | 83.2349 | 10458.1
4295 | 145483 | 0 | 68 | 65 | 80.3212 | 9098.44
4296 | 143884 | 0 | 68 | 65 | 79.6445 | 9097.52
4297 | 142892 | 0 | 68 | 65 | 79.5965 | 9097.07
4298 | 141994 | 0 | 67 | 65 | 79.2448 | 9096.66
4299 | 141123 | 0 | 67 | 65 | 79.4697 | 9096.28
4300 | 143951 | 0 | 65 | 63 | 80.976 | 10097.4
4301 | 275904 | 0 | 65 | 64 | 127.36 | 12326.2
4302 | 1184250 | -5021.27 | 67 | 66 | 265.21 | 33325.1
4303 | 1218550 | -23184.5 | 70 | 64 | 302.212 | 36551.8
4304 | 1136810 | -23003.8 | 71 | 62 | 303.313 | 46264.3
4305 | 1203370 | -22716.6 | 74 | 64 | 328.602 | 72115
4306 | 1253410 | -19257.9 | 76 | 65 | 325.05 | 73731.9
4307 | 1143720 | -14972.5 | 77 | 65 | 305.141 | 73731.8
4308 | 1156060 | -15384 | 78 | 64 | 305.917 | 73733.1
4309 | 1248940 | -17230.6 | 79 | 64 | 329.378 | 73733.3
4310 | 1307290 | -21066.9 | 79 | 65 | 339.258 | 72118
4311 | 1302420 | -23133.6 | 77 | 64 | 339.762 | 65656.4
4312 | 1235270 | -22637.1 | 75 | 63 | 330.066 | 54348.3
4313 | 1109750 | -19136.8 | 74 | 63 | 299.767 | 41425
4314 | 791152 | -14520.5 | 72 | 64 | 210.579 | 25271.1
4315 | 194770 | 0 | 71 | 62 | 114.67 | 18001.8
4316 | 174323 | 0 | 70 | 60 | 99.9824 | 17195.6
4317 | 160365 | 0 | 68 | 56 | 91.9658 | 10720.9
4318 | 149791 | 0 | 65 | 56 | 83.083 | 10460.1
4319 | 144636 | 0 | 66 | 56 | 80.4608 | 9100.98
4320 | 143137 | 0 | 64 | 56 | 79.0391 | 9100.58
4321 | 142227 | 0 | 63 | 57 | 79.2193 | 9100.38
4322 | 141176 | 0 | 61 | 57 | 78.8422 | 9100.21
4323 | 139889 | 0 | 57 | 54 | 79.0046 | 9100.11
4324 | 142652 | 0 | 54 | 52 | 81.2471 | 10101.6
4325 | 236760 | 0 | 54 | 52 | 125.393 | 12330.9
4326 | 565727 | -9699.37 | 54 | 52 | 241.287 | 33330.5
4327 | 654814 | -31442.6 | 54 | 53 | 270.409 | 36558
4328 | 673680 | -31832.9 | 55 | 53 | 294.624 | 46266.8
4329 | 698034 | -30869.4 | 56 | 54 | 296.191 | 72114.9
4330 | 753459 | -26170.1 | 59 | 56 | 290.309 | 73731.3
4331 | 671402 | -24440.3 | 57 | 55 | 272.194 | 73731.8
4332 | 687075 | -21287.7 | 58 | 56 | 272.809 | 73732.2
4333 | 803536 | -24396.7 | 60 | 57 | 296.552 | 73732.9
4334 | 825812 | -25780.7 | 61 | 56 | 305.514 | 72117.8
4335 | 885368 | -26124.4 | 62 | 57 | 310.6 | 65655.8
4336 | 869102 | -25532.8 | 62 | 57 | 303.845 | 54347.7
4337 | 793447 | -22420.3 | 62 | 58 | 276.627 | 41424.5
4338 | 502099 | -19165.3 | 61 | 57 | 189.109 | 25270.9
4339 | 192808 | 0 | 61 | 58 | 112.062 | 18002.6
4340 | 172609 | 0 | 60 | 57 | 102.176 | 17196.9
4341 | 159247 | 0 | 60 | 57 | 94.5848 | 10723.9
4342 | 148111 | 0 | 60 | 57 | 85.4724 | 10464.5
4343 | 143147 | 0 | 60 | 57 | 81.6079 | 9106.25
4344 | 141285 | 0 | 60 | 57 | 76.9312 | 9106.7
4345 | 140565 | 0 | 60 | 57 | 76.8753 | 8392.41
4346 | 139695 | 0 | 60 | 57 | 76.8099 | 8393.37
4347 | 138770 | 0 | 59 | 56 | 76.7405 | 8393.91
4348 | 138030 | 0 | 59 | 56 | 75.0849 | 8394.49
4349 | 137250 | 0 | 60 | 56 | 73.3041 | 8394.99
4350 | 136578 | 0 | 61 | 56 | 70.5703 | 8395.54
4351 | 257768 | -19009.2 | 64 | 57 | 93.4393 | 8396.09
4352 | 289258 | -13077.3 | 66 | 58 | 104.245 | 8396.43
4353 | 328282 | -15726.3 | 69 | 59 | 111.819 | 8406.72
4354 | 358106 | -16102.4 | 71 | 60 | 113.44 | 8408.27
4355 | 392663 | -16341.3 | 72 | 61 | 115.342 | 8409.52
4356 | 411083 | -16502.7 | 74 | 61 | 117.132 | 8410.11
4357 | 415717 | -16608.8 | 73 | 61 | 116.402 | 8410.4
4358 | 132718 | 0 | 73 | 61 | 73.0594 | 8410.79
4359 | 132508 | 0 | 72 | 61 | 71.8826 | 8411.26
4360 | 132194 | 0 | 72 | 61 | 72.3173 | 8405.33
4361 | 131826 | 0 | 71 | 60 | 71.5736 | 8402.2
4362 | 131628 | 0 | 71 | 60 | 72.3662 | 8400.11
4363 | 131302 | 0 | 69 | 59 | 73.3307 | 8398.39
4364 | 130836 | 0 | 66 | 57 | 77.0287 | 8397.22
4365 | 130591 | 0 | 64 | 56 | 80.108 | 8396.37
4366 | 130356 | 0 | 63 | 56 | 78.6349 | 8395.89
4367 | 129915 | 0 | 62 | 55 | 77.7812 | 8395.72
4368 | 129657 | 0 | 61 | 55 | 74.5346 | 3242.44
4369 | 129165 | 0 | 60 | 54 | 74.431 | 3242.56
4370 | 128837 | 0 | 59 | 53 | 74.8092 | 3242.94
4371 | 128617 | 0 | 58 | 53 | 74.7931 | 3243.32
4372 | 128191 | 0 | 57 | 52 | 73.1626 | 3243.78
4373 | 127851 | 0 | 57 | 51 | 71.4949 | 3244.29
4374 | 127588 | 0 | 56 | 50 | 69.5503 | 3244.87
4375 | 127489 | 0 | 57 | 51 | 67.173 | 3245.53
4376 | 127111 | 0 | 59 | 51 | 68.3754 | 3246.17
4377 | 127099 | 0 | 60 | 52 | 68.789 | 3246.77
4378 | 126798 | 0 | 61 | 52 | 69.5034 | 3246.81
4379 | 126762 | 0 | 62 | 53 | 69.8644 | 3246.64
4380 | 126496 | 0 | 63 | 53 | 69.9567 | 3246.03
4381 | 154266 | 0 | 65 | 54 | 77.1549 | 3245.3
4382 | 126395 | 0 | 67 | 55 | 70.9085 | 3244.34
4383 | 162933 | 0 | 69 | 55 | 78.704 | 3243.82
4384 | 126266 | 0 | 69 | 55 | 70.0961 | 3242.96
4385 | 126267 | 0 | 68 | 55 | 69.4027 | 3242.19
4386 | 126221 | 0 | 68 | 55 | 69.7967 | 3241.36
4387 | 126147 | 0 | 65 | 54 | 70.4045 | 3240.62
4388 | 126247 | 0 | 61 | 54 | 73.2286 | 3240.15
4389 | 125808 | 0 | 58 | 52 | 77.0115 | 3239.82
4390 | 125919 | 0 | 56 | 52 | 76.4546 | 3239.76
4391 | 125771 | 0 | 54 | 52 | 75.6481 | 3240.03
4392 | 150243 | 0 | 52 | 51 | 83.7221 | 8393.84
4393 | 125524 | 0 | 51 | 50 | 78.6262 | 8394.12
4394 | 125466 | 0 | 50 | 50 | 78.605 | 8394.06
4395 | 125171 | 0 | 49 | 49 | 78.5919 | 8394.66
4396 | 128797 | 0 | 50 | 50 | 80.6179 | 9308.17
4397 | 191167 | -6481.01 | 52 | 51 | 126.129 | 11340.9
4398 | 409542 | -26380.5 | 53 | 52 | 229.947 | 30482.8
4399 | 601378 | -23332 | 57 | 55 | 271.792 | 33424.6
4400 | 741258 | -16632.1 | 62 | 57 | 285.661 | 42270.1
4401 | 856483 | -14502.2 | 66 | 59 | 291.703 | 65829.9
4402 | 876602 | -11762.1 | 68 | 59 | 283.508 | 67304.4
4403 | 819105 | -8095.66 | 71 | 59 | 266.902 | 67305.5
4404 | 872729 | -15302.4 | 73 | 59 | 270.731 | 67305.6
4405 | 977999 | -9080.59 | 74 | 60 | 305.817 | 67305.6
4406 | 1080340 | -12027.3 | 76 | 61 | 314.552 | 65832.7
4407 | 1131410 | -13624.7 | 77 | 61 | 324.083 | 59942.4
4408 | 1129870 | -18141.8 | 76 | 61 | 324.373 | 49635.1
4409 | 1046370 | -18800.5 | 76 | 61 | 295.461 | 37855.3
4410 | 734795 | -17002.4 | 75 | 61 | 205.491 | 23130.5
4411 | 188303 | 0 | 71 | 61 | 109.423 | 16504.5
4412 | 168250 | 0 | 68 | 60 | 98.618 | 15769.7
4413 | 155108 | 0 | 64 | 59 | 91.0234 | 9867.49
4414 | 144227 | 0 | 64 | 59 | 83.5706 | 9629.74
4415 | 139498 | 0 | 64 | 59 | 79.8728 | 8391.03
4416 | 137931 | 0 | 64 | 60 | 75.8305 | 3237.65
4417 | 136897 | 0 | 64 | 59 | 75.7472 | 3237.61
4418 | 136258 | 0 | 64 | 59 | 75.6958 | 3238.39
4419 | 135611 | 0 | 64 | 59 | 75.6446 | 3238.67
4420 | 135011 | 0 | 64 | 59 | 73.9971 | 3238.96
4421 | 134399 | 0 | 65 | 59 | 72.8454 | 3239.16
4422 | 134075 | 0 | 65 | 60 | 69.9333 | 3239.35
4423 | 133713 | 0 | 68 | 62 | 68.5563 | 3239.52
4424 | 133267 | 0 | 71 | 63 | 71.057 | 3239.59
4425 | 132917 | 0 | 74 | 64 | 72.099 | 3238.94
4426 | 188663 | 0 | 75 | 65 | 81.8052 | 3237.66
4427 | 195811 | 0 | 77 | 66 | 82.7003 | 3235.71
4428 | 201371 | 0 | 78 | 67 | 83.5618 | 3233.58
4429 | 206493 | 0 | 80 | 67 | 84.386 | 3231.75
4430 | 209735 | 0 | 81 | 68 | 84.9514 | 3229.95
4431 | 261405 | 0 | 83 | 68 | 96.0174 | 3228.39
4432 | 262104 | 0 | 82 | 68 | 96.2855 | 3226.65
4433 | 184381 | 0 | 82 | 67 | 79.3132 | 3224.94
4434 | 267235 | 0 | 81 | 67 | 96.5311 | 3223.29
4435 | 212333 | 0 | 77 | 66 | 87.0171 | 3221.74
4436 | 130743 | 0 | 72 | 66 | 74.7875 | 3220.27
4437 | 130153 | 0 | 68 | 64 | 76.6786 | 3219.08
4438 | 129880 | 0 | 66 | 62 | 76.3214 | 3218.21
4439 | 129636 | 0 | 63 | 60 | 75.1531 | 3217.68
4440 | 129688 | 0 | 61 | 59 | 79.5351 | 8370.88
4441 | 129379 | 0 | 60 | 58 | 79.846 | 8370.89
4442 | 129061 | 0 | 59 | 57 | 80.2291 | 8370.26
4443 | 128863 | 0 | 58 | 57 | 80.2144 | 8370.22
4444 | 132525 | 0 | 59 | 58 | 82.3446 | 9283.15
4445 | 240085 | 0 | 61 | 59 | 133.067 | 11315.2
4446 | 993689 | -11292.4 | 62 | 59 | 265.597 | 30456.6
4447 | 1060290 | -21230.3 | 65 | 61 | 297.773 | 33397.7
4448 | 1089970 | -15608.2 | 68 | 62 | 305.04 | 42255.9
4449 | 1140650 | -16109.8 | 71 | 63 | 308.253 | 65820
4450 | 1148360 | -13118.6 | 74 | 63 | 298.786 | 67294.9
4451 | 1059130 | -9500.5 | 76 | 63 | 278.633 | 67296.2
4452 | 1128030 | -22053.4 | 79 | 63 | 283.343 | 67296.9
4453 | 1199820 | -10402 | 80 | 63 | 302.877 | 67297.1
4454 | 1211660 | -14331.1 | 80 | 62 | 311.664 | 65824.7
4455 | 1264020 | -18057.5 | 81 | 62 | 319.829 | 59935.2
4456 | 1266580 | -27651.4 | 80 | 62 | 331.18 | 49628
4457 | 1184090 | -30741.9 | 80 | 62 | 291.586 | 37848.4
4458 | 837068 | -31670.3 | 79 | 61 | 194.53 | 23124
4459 | 190290 | 0 | 75 | 61 | 107.319 | 16498.4
4460 | 170333 | 0 | 70 | 61 | 97.7303 | 15762.9
4461 | 156808 | 0 | 66 | 59 | 91.1791 | 9859.13
4462 | 146022 | 0 | 64 | 59 | 83.1314 | 9620.43
4463 | 141238 | 0 | 62 | 59 | 79.361 | 8381.15
4464 | 139644 | 0 | 60 | 58 | 78.6206 | 8380.67
4465 | 138677 | 0 | 59 | 57 | 79.0852 | 8380.05
4466 | 137814 | 0 | 58 | 56 | 79.0459 | 8379.89
4467 | 137038 | 0 | 57 | 55 | 79.0106 | 8379.94
4468 | 140440 | 0 | 58 | 57 | 81.146 | 9293.02
4469 | 246619 | 0 | 59 | 58 | 125.621 | 11325.2
4470 | 810449 | -8875.61 | 60 | 59 | 248.206 | 30466.6
4471 | 990411 | -22323.2 | 64 | 61 | 309.989 | 33407.9
4472 | 1089910 | -20447.2 | 69 | 63 | 322.894 | 42261
4473 | 1158930 | -19373.7 | 73 | 64 | 327.949 | 65824
4474 | 1253140 | -15731.3 | 76 | 66 | 325.626 | 67299.1
4475 | 1190570 | -11269.3 | 80 | 67 | 308.216 | 67300.4
4476 | 1344310 | -21379.5 | 83 | 69 | 317.37 | 67301
4477 | 1392180 | -12183.3 | 83 | 68 | 339.08 | 67301
4478 | 1441460 | -18156.7 | 84 | 68 | 348.393 | 65828.4
4479 | 1496340 | -24520.7 | 84 | 68 | 352.825 | 59938.7
4480 | 1487850 | -27441.2 | 83 | 68 | 346.846 | 49631.4
4481 | 1384220 | -24056 | 81 | 68 | 317.544 | 37851.7
4482 | 977945 | -19193.2 | 80 | 68 | 221.785 | 23127.3
4483 | 194098 | 0 | 78 | 67 | 116.056 | 16501.5
4484 | 173870 | 0 | 76 | 66 | 105.625 | 15765.7
4485 | 160501 | 0 | 74 | 65 | 95.299 | 9862.06
4486 | 149424 | 0 | 72 | 64 | 83.6226 | 9623.15
4487 | 144385 | 0 | 70 | 63 | 79.814 | 8383.55
4488 | 142751 | 0 | 68 | 62 | 79.1735 | 8382.55
4489 | 141861 | 0 | 68 | 62 | 79.666 | 8381.8
4490 | 141046 | 0 | 67 | 62 | 79.3188 | 8381.21
4491 | 140231 | 0 | 67 | 62 | 79.5463 | 8380.74
4492 | 143644 | 0 | 66 | 63 | 81.2633 | 9293.18
4493 | 273273 | 0 | 66 | 63 | 127.691 | 11324.7
4494 | 1109420 | -5842.01 | 65 | 64 | 294.232 | 30465.4
4495 | 1170820 | -24342.4 | 66 | 64 | 319.839 | 33406.1
4496 | 1127620 | -24491.6 | 66 | 64 | 323.64 | 42261.4
4497 | 1152380 | -24643.3 | 67 | 65 | 326.287 | 65823.5
4498 | 1257720 | -21212.7 | 70 | 67 | 324.7 | 67296.7
4499 | 1181640 | -16161.7 | 74 | 68 | 309.373 | 67297.1
4500 | 1326830 | -15875.2 | 77 | 70 | 317.929 | 67298.9
4501 | 1443960 | -17157.8 | 79 | 70 | 342.764 | 67299.7
4502 | 1533920 | -20853.5 | 81 | 71 | 354.382 | 65827.9
4503 | 1583560 | -21917.6 | 83 | 71 | 359.099 | 59938.2
4504 | 1592390 | -23104.4 | 83 | 71 | 353.995 | 49630.9
4505 | 1495510 | -30571.7 | 82 | 70 | 325.354 | 37851.3
4506 | 1075750 | -32568.1 | 82 | 69 | 230.203 | 23127
4507 | 195407 | 0 | 79 | 69 | 116.368 | 16501.2
4508 | 174970 | 0 | 77 | 69 | 104.903 | 15765.6
4509 | 161623 | 0 | 74 | 68 | 96.3656 | 9861.89
4510 | 150640 | 0 | 73 | 68 | 86.7572 | 9622.93
4511 | 145617 | 0 | 72 | 68 | 82.6734 | 8383.28
4512 | 143787 | 0 | 71 | 68 | 77.8548 | 8382.33
4513 | 142797 | 0 | 70 | 68 | 77.6551 | 8381.54
4514 | 141801 | 0 | 70 | 67 | 78.0673 | 8381.54
4515 | 140885 | 0 | 69 | 66 | 77.3839 | 8381.24
4516 | 140193 | 0 | 69 | 67 | 76.2114 | 8381.03
4517 | 139341 | 0 | 70 | 66 | 75.0849 | 8380.78
4518 | 138732 | 0 | 70 | 67 | 71.9045 | 8380.54
4519 | 709195 | -2834.54 | 73 | 68 | 133.491 | 8380.3
4520 | 684455 | -3473.35 | 77 | 69 | 133.429 | 8379.93
4521 | 697755 | -8438.64 | 80 | 70 | 133.974 | 8398.9
4522 | 740073 | -10525.9 | 82 | 71 | 136.767 | 8401.93
4523 | 789927 | -16871.4 | 84 | 72 | 139.86 | 8403.73
4524 | 850766 | -26983.5 | 86 | 73 | 144.187 | 8404.72
4525 | 869593 | -33218 | 87 | 73 | 148.083 | 8405.36
4526 | 217229 | 0 | 88 | 73 | 90.0325 | 8405.7
4527 | 224707 | 0 | 89 | 73 | 89.4133 | 8406.2
4528 | 228430 | 0 | 87 | 73 | 89.772 | 8397.53
4529 | 227060 | 0 | 84 | 73 | 89.4066 | 8392.46
4530 | 134055 | 0 | 82 | 73 | 74.568 | 8388.69
4531 | 133687 | 0 | 79 | 71 | 75.7027 | 8385.62
4532 | 133267 | 0 | 75 | 69 | 79.5118 | 8383.4
4533 | 132825 | 0 | 72 | 67 | 81.0642 | 8381.73
4534 | 132450 | 0 | 71 | 66 | 80.8631 | 8380.42
4535 | 132157 | 0 | 69 | 66 | 79.4002 | 8379.53
4536 | 131646 | 0 | 68 | 65 | 73.583 | 3225.57
4537 | 131194 | 0 | 67 | 64 | 73.5242 | 3225.01
4538 | 130828 | 0 | 66 | 63 | 73.4704 | 3224.75
4539 | 130523 | 0 | 65 | 62 | 73.4203 | 3224.49
4540 | 129991 | 0 | 64 | 60 | 71.7607 | 3224.37
4541 | 129635 | 0 | 64 | 59 | 70.3484 | 3224.32
4542 | 129315 | 0 | 63 | 58 | 68.4024 | 3224.37
4543 | 129214 | 0 | 65 | 59 | 67.9231 | 3224.52
4544 | 128887 | 0 | 67 | 59 | 68.0911 | 3224.65
4545 | 128668 | 0 | 69 | 59 | 68.524 | 3224.31
4546 | 181453 | 0 | 71 | 60 | 75.1837 | 3223.19
4547 | 193609 | 0 | 73 | 61 | 75.9635 | 3221.68
4548 | 195892 | 0 | 75 | 61 | 76.2318 | 3219.93
4549 | 200961 | 0 | 75 | 61 | 75.9526 | 3218.24
4550 | 201103 | 0 | 76 | 61 | 82.003 | 3216.61
4551 | 257877 | 0 | 76 | 61 | 94.1717 | 3215.16
4552 | 252144 | 0 | 75 | 60 | 93.7529 | 3213.72
4553 | 179558 | 0 | 75 | 60 | 78.1138 | 3212.37
4554 | 175725 | 0 | 74 | 59 | 76.2249 | 3211.09
4555 | 127941 | 0 | 69 | 59 | 68.6551 | 3210.06
4556 | 127660 | 0 | 65 | 58 | 72.8155 | 3209.09
4557 | 127442 | 0 | 60 | 56 | 76.0621 | 3208.36
4558 | 127185 | 0 | 60 | 55 | 76.5121 | 3208.06
4559 | 127163 | 0 | 59 | 55 | 75.7109 | 3208.16
4560 | 127146 | 0 | 59 | 54 | 78.6809 | 8361.89
4561 | 127156 | 0 | 58 | 54 | 78.6813 | 8362.32
4562 | 126850 | 0 | 56 | 53 | 78.6677 | 8361.99
4563 | 126707 | 0 | 55 | 53 | 78.6611 | 8362.14
4564 | 156157 | 0 | 55 | 53 | 85.8535 | 9275.23
4565 | 177379 | 0 | 55 | 53 | 118.522 | 11307.5
4566 | 794581 | -21098.7 | 55 | 53 | 261.56 | 30449.2
4567 | 836623 | -23927 | 57 | 54 | 274.167 | 33390.8
4568 | 855725 | -21098 | 60 | 55 | 285.992 | 42251
4569 | 869860 | -19631.4 | 62 | 55 | 288.095 | 65815.1
4570 | 913359 | -17650.6 | 65 | 57 | 300.306 | 67290.4
4571 | 863497 | -13243.3 | 67 | 58 | 283.732 | 67291.9
4572 | 960833 | -18896.9 | 70 | 60 | 271.399 | 67292.5
4573 | 1074850 | -13984.6 | 72 | 61 | 298.037 | 67292.8
4574 | 1162880 | -16851.4 | 74 | 62 | 327.92 | 65820.4
4575 | 1211390 | -17746.8 | 76 | 62 | 332.708 | 59930.9
4576 | 1227630 | -27129.4 | 76 | 62 | 315.114 | 49624
4577 | 1189210 | -33192.2 | 75 | 63 | 284.226 | 37844.5
4578 | 847679 | -36192.9 | 75 | 62 | 194.243 | 23120.3
4579 | 188744 | 0 | 72 | 62 | 106.614 | 16494.7
4580 | 168948 | 0 | 68 | 62 | 97.8615 | 15759.9
4581 | 155677 | 0 | 65 | 61 | 91.3501 | 9856.23
4582 | 144585 | 0 | 63 | 59 | 83.028 | 9617.83
4583 | 139879 | 0 | 61 | 58 | 79.2645 | 8378.68
4584 | 138266 | 0 | 59 | 56 | 78.5063 | 8378.39
4585 | 137515 | 0 | 58 | 55 | 78.7263 | 8378.3
4586 | 136895 | 0 | 56 | 55 | 78.698 | 8378.4
4587 | 136063 | 0 | 55 | 54 | 78.6604 | 8378.62
4588 | 139317 | 0 | 56 | 55 | 81.0951 | 9291.81
4589 | 234139 | 0 | 58 | 55 | 125.226 | 11324.1
4590 | 706812 | -9821.57 | 59 | 56 | 243.294 | 30465.7
4591 | 875241 | -23562.4 | 63 | 58 | 286.448 | 33407.2
4592 | 1008260 | -21661.6 | 67 | 61 | 317.527 | 42259.8
4593 | 1079520 | -20412.1 | 71 | 62 | 322.799 | 65821.9
4594 | 1168980 | -16795.9 | 74 | 64 | 320.315 | 67297.1
4595 | 1117690 | -12458.8 | 77 | 65 | 304.165 | 67298.7
4596 | 1257220 | -21608.7 | 80 | 67 | 312.114 | 67299.3
4597 | 1377670 | -13211.4 | 81 | 68 | 338.257 | 67299.7
4598 | 1466870 | -17204.5 | 83 | 69 | 350.001 | 65827.2
4599 | 1565510 | -21702.8 | 84 | 70 | 357.154 | 59937.4
4600 | 1591250 | -30890.8 | 83 | 70 | 353.097 | 49630.2
4601 | 1519840 | -36757.7 | 83 | 70 | 331.24 | 37850.6
4602 | 1119170 | -36837.5 | 82 | 70 | 234.754 | 23126.2
4603 | 193872 | 0 | 80 | 69 | 115.371 | 16500.4
4604 | 173442 | 0 | 77 | 68 | 104.88 | 15764.7
4605 | 160254 | 0 | 75 | 68 | 92.8624 | 9860.81
4606 | 149346 | 0 | 74 | 68 | 83.9889 | 9621.77
4607 | 144300 | 0 | 74 | 67 | 80.5398 | 8382.03
4608 | 142786 | 0 | 73 | 67 | 79.658 | 8380.96
4609 | 141776 | 0 | 72 | 66 | 79.5636 | 8380.07
4610 | 140710 | 0 | 71 | 64 | 79.4683 | 8379.23
4611 | 140122 | 0 | 70 | 63 | 79.3971 | 8378.41
4612 | 143469 | 0 | 70 | 63 | 81.6926 | 9290.56
4613 | 280513 | 0 | 70 | 63 | 128.415 | 11321.8
4614 | 1216710 | -4727.52 | 70 | 64 | 299.163 | 30462.3
4615 | 1232160 | -23386.6 | 69 | 64 | 323.249 | 33402.8
4616 | 1207910 | -23809.2 | 69 | 65 | 329.479 | 42260.1
4617 | 1224970 | -24611.4 | 68 | 66 | 330.52 | 65822.4
4618 | 1218320 | -22117.5 | 68 | 66 | 321.381 | 67295.7
4619 | 1100140 | -18310.3 | 69 | 66 | 301.249 | 67296.2
4620 | 1114000 | -17290.9 | 69 | 66 | 301.485 | 67296.6
4621 | 1302890 | -20417.5 | 71 | 68 | 331.406 | 67297.4
4622 | 1388350 | -23560.5 | 74 | 69 | 345.06 | 65825.6
4623 | 1461230 | -24261.9 | 76 | 70 | 350.952 | 59936.5
4624 | 1471010 | -22767.1 | 77 | 70 | 345.914 | 49629.5
4625 | 1441020 | -18640.1 | 77 | 71 | 320.782 | 37849.9
4626 | 1043160 | -16194.1 | 78 | 71 | 225.421 | 23125.7
4627 | 195291 | 0 | 76 | 70 | 115.278 | 16500.1
4628 | 174649 | 0 | 74 | 69 | 104.594 | 15764.9
4629 | 161264 | 0 | 72 | 68 | 92.1965 | 9861.42
4630 | 150273 | 0 | 72 | 68 | 84.2166 | 9622.87
4631 | 145250 | 0 | 71 | 68 | 80.171 | 8383.38
4632 | 143677 | 0 | 71 | 68 | 79.7678 | 8382.58
4633 | 142757 | 0 | 70 | 68 | 79.4057 | 8381.87
4634 | 141899 | 0 | 70 | 68 | 79.6358 | 8381.25
4635 | 141107 | 0 | 69 | 68 | 79.284 | 8380.6
4636 | 144351 | 0 | 69 | 67 | 81.6908 | 9292.88
4637 | 282671 | 0 | 68 | 67 | 128.067 | 11324.2
4638 | 1249850 | -4971.83 | 68 | 67 | 294.782 | 30464.8
4639 | 1368520 | -24200.6 | 72 | 68 | 332.771 | 33405.3
4640 | 1378360 | -23824.2 | 75 | 69 | 342.956 | 42260.8
4641 | 1430000 | -23232.5 | 79 | 69 | 344.662 | 65823
4642 | 1537730 | -19158.3 | 82 | 71 | 343.331 | 67297.2
4643 | 1440710 | -14425.5 | 85 | 72 | 324.64 | 67299.9
4644 | 1620230 | -25738.3 | 88 | 74 | 336.2 | 67300.9
4645 | 1796420 | -33810.7 | 89 | 75 | 370.983 | 67301.1
4646 | 1859760 | -33595.6 | 91 | 76 | 381.334 | 65828.6
4647 | 1960500 | -33614.6 | 92 | 77 | 390.842 | 59939
4648 | 1931360 | -33069.2 | 91 | 76 | 385.366 | 49631.9
4649 | 1759350 | -36041.4 | 89 | 74 | 337.838 | 37852.2
4650 | 1352460 | -47837.5 | 88 | 74 | 244.155 | 23127.8
4651 | 197398 | 0 | 85 | 74 | 117.711 | 16502
4652 | 176387 | 0 | 83 | 73 | 105.086 | 15766.2
4653 | 163171 | 0 | 80 | 73 | 97.2994 | 9861.38
4654 | 152230 | 0 | 80 | 73 | 87.8251 | 9621.6
4655 | 146993 | 0 | 80 | 72 | 83.7975 | 8381.33
4656 | 145410 | 0 | 80 | 72 | 83.1513 | 8379.77
4657 | 144468 | 0 | 80 | 72 | 83.0549 | 8378.4
4658 | 143610 | 0 | 79 | 72 | 82.9683 | 8377.08
4659 | 142710 | 0 | 79 | 71 | 82.8782 | 8375.75
4660 | 146291 | 0 | 77 | 71 | 85.0973 | 9287.31
4661 | 314769 | 0 | 76 | 71 | 150.749 | 11317.9
4662 | 1666380 | 0 | 74 | 71 | 321.291 | 30457.8
4663 | 1700130 | -26868.2 | 76 | 72 | 358.792 | 33397.7
4664 | 1601460 | -25823.6 | 79 | 72 | 358.777 | 42259.6
4665 | 1650030 | -25451.2 | 81 | 73 | 361.584 | 65822
4666 | 1601500 | -22421.2 | 78 | 72 | 350.314 | 67295.5
4667 | 1456730 | -24681.7 | 76 | 72 | 326.619 | 67296.6
4668 | 1408170 | -18180.7 | 73 | 71 | 321.979 | 67297.4
4669 | 1518050 | -21855 | 75 | 71 | 348.825 | 67298.3
4670 | 1559030 | -26116.2 | 76 | 72 | 357.099 | 65826.2
4671 | 1597060 | -27172.9 | 78 | 72 | 360.006 | 59936.8
4672 | 1647010 | -25768 | 79 | 73 | 356.998 | 49629.4
4673 | 1591970 | -21209.7 | 79 | 74 | 330.826 | 37849.9
4674 | 1199860 | -18598.4 | 80 | 75 | 234.874 | 23125.8
4675 | 197740 | 0 | 80 | 75 | 116.482 | 16500.1
4676 | 176667 | 0 | 80 | 75 | 105.501 | 15764.6
4677 | 163399 | 0 | 80 | 75 | 96.3336 | 9860.73
4678 | 152439 | 0 | 80 | 75 | 84.4757 | 9621.65
4679 | 147155 | 0 | 79 | 74 | 80.7322 | 8381.67
4680 | 145323 | 0 | 79 | 74 | 76.1062 | 8380.26
4681 | 144256 | 0 | 78 | 73 | 76.052 | 8378.9
4682 | 143396 | 0 | 76 | 73 | 76.0086 | 8378.3
4683 | 142493 | 0 | 75 | 72 | 75.9633 | 8377.36
4684 | 141727 | 0 | 75 | 72 | 74.3247 | 8376.53
4685 | 140995 | 0 | 75 | 72 | 72.6367 | 8375.77
4686 | 140293 | 0 | 75 | 72 | 72.6457 | 8375.09
4687 | 993830 | 0 | 77 | 73 | 149.813 | 8374.42
4688 | 907610 | -18043.3 | 79 | 73 | 146.029 | 8373.67
4689 | 846999 | -9773.08 | 81 | 74 | 142.997 | 8396.44
4690 | 915392 | -27390.5 | 83 | 75 | 147.973 | 8399.73
4691 | 944970 | -32248.6 | 84 | 76 | 152.117 | 8401.38
4692 | 1005400 | -46295.2 | 86 | 76 | 144.06 | 8402.32
4693 | 991061 | -49528.9 | 87 | 76 | 145.28 | 8403.11
4694 | 223962 | 0 | 87 | 76 | 91.2711 | 8404.01
4695 | 229845 | 0 | 88 | 76 | 89.8957 | 8404.46
4696 | 292479 | 0 | 87 | 76 | 104.321 | 8395.31
4697 | 295720 | 0 | 87 | 76 | 104.801 | 8390.04
4698 | 296304 | 0 | 86 | 76 | 104.596 | 8386.16
4699 | 235125 | 0 | 83 | 76 | 92.3817 | 8383.01
4700 | 134386 | 0 | 81 | 75 | 78.7208 | 8380.6
4701 | 134125 | 0 | 78 | 74 | 80.3593 | 8378.54
4702 | 133787 | 0 | 78 | 73 | 79.5425 | 8376.96
4703 | 133536 | 0 | 77 | 73 | 78.7299 | 8375.56
4704 | 133193 | 0 | 77 | 73 | 74.2209 | 3221.17
4705 | 132794 | 0 | 77 | 72 | 74.201 | 3220.11
4706 | 132513 | 0 | 76 | 72 | 74.1869 | 3219.33
4707 | 132235 | 0 | 76 | 72 | 74.173 | 3218.5
4708 | 131971 | 0 | 76 | 72 | 72.5598 | 3217.69
4709 | 131716 | 0 | 77 | 72 | 70.9286 | 3216.91
4710 | 131582 | 0 | 77 | 73 | 68.2313 | 3216.14
4711 | 131357 | 0 | 79 | 73 | 67.9204 | 3215.38
4712 | 286744 | 0 | 81 | 74 | 82.4489 | 3214.5
4713 | 294506 | 0 | 83 | 74 | 83.3461 | 3213.06
4714 | 302582 | 0 | 86 | 75 | 83.784 | 3211.45
4715 | 313801 | 0 | 88 | 76 | 84.3695 | 3211.57
4716 | 323897 | 0 | 91 | 76 | 84.4398 | 3210.08
4717 | 328573 | 0 | 85 | 75 | 84.6801 | 3209
4718 | 313573 | 0 | 80 | 73 | 103.351 | 3207.07
4719 | 130047 | 0 | 74 | 71 | 70.908 | 3203.13
4720 | 235805 | 0 | 75 | 71 | 88.1143 | 3201.11
4721 | 197808 | 0 | 77 | 73 | 79.4378 | 3199.17
4722 | 130162 | 0 | 78 | 74 | 68.7703 | 3198.41
4723 | 129925 | 0 | 76 | 73 | 70.6181 | 3197.36
4724 | 231949 | 0 | 75 | 72 | 83.8496 | 3196.25
4725 | 129533 | 0 | 73 | 72 | 77.4429 | 3195.21
4726 | 129342 | 0 | 73 | 71 | 77.1006 | 3194.4
4727 | 129254 | 0 | 73 | 71 | 76.2962 | 3193.92
4728 | 129563 | 0 | 73 | 72 | 79.2818 | 8346.68
4729 | 129390 | 0 | 72 | 71 | 78.9581 | 8346.23
4730 | 129273 | 0 | 72 | 71 | 79.226 | 8344.92
4731 | 129065 | 0 | 71 | 70 | 78.903 | 8344.05
4732 | 133402 | 0 | 71 | 71 | 81.2467 | 9256.12
4733 | 286723 | 0 | 72 | 70 | 129.234 | 11287.3
4734 | 1790970 | 0 | 72 | 71 | 309.567 | 30427.8
4735 | 1755390 | -26830.2 | 73 | 71 | 333.331 | 33368.2
4736 | 1611620 | -29158.7 | 73 | 71 | 334.888 | 42242
4737 | 1570770 | -20774.1 | 74 | 71 | 326.693 | 65805.7
4738 | 1613700 | -18342.8 | 75 | 72 | 319.229 | 67279.7
4739 | 1452820 | -14704.8 | 77 | 72 | 295.356 | 67281
4740 | 1533820 | -13783.8 | 78 | 73 | 310.488 | 67283.1
4741 | 1649290 | -17123.3 | 78 | 73 | 343.252 | 67284.7
4742 | 1697190 | -20740 | 79 | 74 | 356.056 | 65813.7
4743 | 1732900 | -22084.1 | 79 | 74 | 362.227 | 59924.9
4744 | 1747960 | -20914.6 | 80 | 74 | 360.158 | 49618.2
4745 | 1656840 | -19567.6 | 80 | 74 | 330.887 | 37838.8
4746 | 1251230 | -25284.9 | 81 | 74 | 226.924 | 23115.4
4747 | 191646 | 0 | 79 | 74 | 108.263 | 16490.5
4748 | 170859 | 0 | 77 | 73 | 100.306 | 15755.3
4749 | 157879 | 0 | 75 | 73 | 92.742 | 9849.64
4750 | 147167 | 0 | 75 | 73 | 84.2099 | 9610.08
4751 | 142264 | 0 | 74 | 73 | 80.1588 | 8369.93
4752 | 140899 | 0 | 74 | 73 | 79.4637 | 8368.61
4753 | 140048 | 0 | 74 | 72 | 79.421 | 8367.51
4754 | 139285 | 0 | 74 | 71 | 79.3829 | 8366.56
4755 | 138678 | 0 | 74 | 71 | 79.3526 | 8365.65
4756 | 142439 | 0 | 74 | 71 | 81.8262 | 9277.64
4757 | 296324 | 0 | 73 | 70 | 129.31 | 11308.7
4758 | 1604070 | 0 | 73 | 70 | 297.836 | 30448.9
4759 | 1642070 | -24170.7 | 75 | 71 | 347.312 | 33389.1
4760 | 1620710 | -23760.7 | 77 | 72 | 356.647 | 42252.2
4761 | 1671970 | -23468.6 | 79 | 73 | 360.061 | 65815.2
4762 | 1690530 | -19840.1 | 81 | 73 | 353.243 | 67291.3
4763 | 1542240 | -17922.7 | 83 | 73 | 330.612 | 67293
4764 | 1667720 | -27998.9 | 85 | 74 | 339.843 | 67294.2
4765 | 1792850 | -33033.6 | 86 | 74 | 368.736 | 67294.8
4766 | 1793270 | -33129.3 | 86 | 74 | 373.773 | 65822.6
4767 | 1798200 | -33432.8 | 87 | 73 | 376.378 | 59933.2
4768 | 1800350 | -33394.7 | 86 | 73 | 372.648 | 49626.2
4769 | 1672730 | -36699.1 | 84 | 72 | 334.343 | 37846.8
4770 | 1248050 | -42511.3 | 83 | 72 | 230.243 | 23122.6
4771 | 195351 | 0 | 81 | 70 | 116.2 | 16496.9
4772 | 174777 | 0 | 78 | 69 | 105.267 | 15761.4
4773 | 161297 | 0 | 76 | 67 | 93.0313 | 9856.2
4774 | 150264 | 0 | 73 | 66 | 83.709 | 9616.63
4775 | 145199 | 0 | 71 | 65 | 79.8953 | 8376.53
4776 | 143665 | 0 | 68 | 64 | 78.95 | 8375.27
4777 | 142734 | 0 | 67 | 64 | 79.3988 | 8374.36
4778 | 141632 | 0 | 66 | 63 | 79.307 | 8373.69
4779 | 141010 | 0 | 65 | 63 | 79.2384 | 8373.2
4780 | 144037 | 0 | 65 | 63 | 81.5056 | 9285.73
4781 | 274502 | 0 | 66 | 63 | 128.038 | 11317.3
4782 | 1166400 | -4962.68 | 66 | 63 | 267.144 | 30458.2
4783 | 1281090 | -28176.5 | 69 | 64 | 327.078 | 33399
4784 | 1283790 | -26667.7 | 72 | 65 | 334.92 | 42257.5
4785 | 1300490 | -25774.1 | 75 | 65 | 337.383 | 65821.7
4786 | 1306350 | -21845.9 | 77 | 65 | 328.655 | 67296.7
4787 | 1196510 | -17369.1 | 78 | 65 | 309.157 | 67298
4788 | 1213670 | -25544.3 | 80 | 64 | 310.014 | 67298.6
4789 | 1295260 | -18981.8 | 81 | 64 | 333.141 | 67298.7
4790 | 1330250 | -23384 | 81 | 64 | 341.52 | 65826.1
4791 | 1374810 | -24879.7 | 82 | 64 | 345.262 | 59936.7
4792 | 1366960 | -28407.9 | 82 | 64 | 339.52 | 49629.5
4793 | 1295980 | -35853 | 81 | 64 | 315.69 | 37849.8
4794 | 957911 | -37980.5 | 81 | 64 | 215.202 | 23125.4
4795 | 196080 | 0 | 77 | 65 | 116.052 | 16499.6
4796 | 175542 | 0 | 72 | 64 | 102.784 | 15763.9
4797 | 162031 | 0 | 68 | 63 | 93.6614 | 9860
4798 | 150764 | 0 | 66 | 62 | 85.1179 | 9621.06
4799 | 145669 | 0 | 64 | 61 | 81.0587 | 8381.6
4800 | 143954 | 0 | 62 | 60 | 80.1666 | 8380.98
4801 | 143003 | 0 | 61 | 60 | 80.4284 | 8380.64
4802 | 141833 | 0 | 61 | 59 | 80.7593 | 8380.41
4803 | 141069 | 0 | 60 | 59 | 80.2088 | 8380.22
4804 | 144001 | 0 | 60 | 59 | 82.8149 | 9292.69
4805 | 259989 | 0 | 60 | 59 | 134.034 | 11324.6
4806 | 905181 | -7446.92 | 60 | 59 | 278.728 | 30465.8
4807 | 1077340 | -29421.1 | 65 | 62 | 314.908 | 33406.9
4808 | 1148630 | -27358.3 | 70 | 64 | 327.809 | 42261.5
4809 | 1234880 | -25829.2 | 75 | 65 | 334.87 | 65822.8
4810 | 1282440 | -21729.2 | 77 | 66 | 327.95 | 67297.2
4811 | 1215990 | -17006.8 | 78 | 67 | 310.81 | 67299.6
4812 | 1284510 | -15546.5 | 80 | 68 | 315.434 | 67300
4813 | 1397380 | -19179.7 | 80 | 68 | 340.262 | 67300.4
4814 | 1437660 | -23408.9 | 81 | 68 | 349.045 | 65828
4815 | 1477020 | -24942.9 | 81 | 68 | 352.545 | 59938
4816 | 1511460 | -24648.4 | 81 | 69 | 348.462 | 49630.9
4817 | 1402840 | -19731.6 | 80 | 69 | 318.527 | 37851.3
4818 | 1045910 | -19444.6 | 80 | 70 | 225.452 | 23127
4819 | 195940 | 0 | 78 | 69 | 116.302 | 16501
4820 | 175375 | 0 | 77 | 68 | 105.42 | 15765.5
4821 | 161947 | 0 | 75 | 67 | 97.0572 | 9861.87
4822 | 150899 | 0 | 75 | 67 | 84.9829 | 9622.98
4823 | 145949 | 0 | 74 | 67 | 80.7945 | 8383.31
4824 | 144315 | 0 | 74 | 67 | 80.552 | 8382.28
4825 | 143208 | 0 | 73 | 66 | 80.0934 | 8381.37
4826 | 142476 | 0 | 73 | 66 | 80.3829 | 8380.56
4827 | 141517 | 0 | 72 | 65 | 79.9402 | 8379.74
4828 | 144950 | 0 | 72 | 65 | 82.3341 | 9291.85
4829 | 286132 | 0 | 72 | 65 | 132.428 | 11323
4830 | 1274870 | -3722.53 | 72 | 65 | 300.966 | 30463.4
4831 | 1431210 | -26793.6 | 75 | 67 | 340.409 | 33403.8
4832 | 1469930 | -26031.2 | 79 | 69 | 347.619 | 42261
4833 | 1569820 | -25313 | 82 | 71 | 353.631 | 65825.2
4834 | 1635820 | -21066.5 | 85 | 72 | 350.449 | 67299.9
4835 | 1573290 | -21256.2 | 87 | 74 | 332.352 | 67300.9
4836 | 1719410 | -34522.3 | 90 | 75 | 336.656 | 67301.6
4837 | 1836570 | -33075.2 | 90 | 75 | 374.535 | 67301.6
4838 | 1837290 | -33184.6 | 90 | 75 | 379.537 | 65829.2
4839 | 1839980 | -33119.2 | 90 | 75 | 381.772 | 59939.7
4840 | 1841250 | -33669.9 | 83 | 75 | 373.801 | 49632.4
4841 | 1583300 | -37933.4 | 77 | 72 | 334.599 | 37852.5
4842 | 967068 | -17587.9 | 70 | 69 | 217.318 | 23128
4843 | 196678 | 0 | 70 | 69 | 113.843 | 16501.9
4844 | 176152 | 0 | 71 | 69 | 100.458 | 15766.1
4845 | 162638 | 0 | 71 | 68 | 92.7676 | 9862.61
4846 | 151404 | 0 | 70 | 67 | 83.9031 | 9624.4
4847 | 146274 | 0 | 70 | 67 | 80.449 | 8385.06
4848 | 144257 | 0 | 69 | 66 | 75.5029 | 8384.32
4849 | 142946 | 0 | 67 | 64 | 75.091 | 8383.67
4850 | 142068 | 0 | 65 | 63 | 74.9735 | 8383.76
4851 | 140965 | 0 | 63 | 61 | 74.8499 | 8383.56
4852 | 140300 | 0 | 63 | 61 | 73.7373 | 8383.5
4853 | 139368 | 0 | 62 | 60 | 71.7803 | 8383.53
4854 | 138463 | 0 | 62 | 59 | 71.1968 | 8383.68
4855 | 449269 | -4601.37 | 65 | 60 | 114.646 | 8383.87
4856 | 440774 | -6194.64 | 69 | 61 | 117.782 | 8384.02
4857 | 448786 | -10743.1 | 72 | 61 | 118.977 | 8400.27
4858 | 486085 | -11997.8 | 74 | 62 | 121.201 | 8403.11
4859 | 526237 | -16450.1 | 76 | 63 | 123.668 | 8405
4860 | 548175 | -21988.9 | 78 | 63 | 124.976 | 8405.95
4861 | 556307 | -21810.4 | 79 | 63 | 125.507 | 8406.51
4862 | 199326 | 0 | 81 | 63 | 85.8846 | 8406.79
4863 | 202886 | 0 | 82 | 63 | 85.4191 | 8407.3
4864 | 251045 | 0 | 80 | 62 | 95.2157 | 8399.85
4865 | 133255 | 0 | 78 | 61 | 72.7314 | 8395.53
4866 | 133019 | 0 | 76 | 60 | 72.4383 | 8392.38
4867 | 133279 | 0 | 74 | 62 | 74.1775 | 8389.88
4868 | 133037 | 0 | 71 | 63 | 76.0696 | 8388.07
4869 | 132849 | 0 | 69 | 64 | 79.5023 | 8386.65
4870 | 132304 | 0 | 67 | 63 | 78.6041 | 8385.59
4871 | 131906 | 0 | 65 | 62 | 77.7156 | 8384.74
4872 | 131543 | 0 | 63 | 62 | 73.1398 | 3230.66
4873 | 130984 | 0 | 63 | 61 | 73.6306 | 3230.02
4874 | 130742 | 0 | 62 | 61 | 73.3269 | 3229.64
4875 | 130376 | 0 | 62 | 61 | 73.5671 | 3229.28
4876 | 130039 | 0 | 62 | 61 | 71.9516 | 3228.9
4877 | 129866 | 0 | 62 | 62 | 70.3352 | 3228.56
4878 | 129404 | 0 | 62 | 62 | 68.5587 | 3228.17
4879 | 129113 | 0 | 62 | 62 | 67.3777 | 3227.86
4880 | 128841 | 0 | 62 | 62 | 67.7036 | 3227.98
4881 | 128427 | 0 | 62 | 61 | 68.5014 | 3228.17
4882 | 128612 | 0 | 64 | 63 | 68.6588 | 3228.09
4883 | 128422 | 0 | 66 | 65 | 70.2219 | 3228
4884 | 128320 | 0 | 68 | 67 | 70.7843 | 3227.98
4885 | 185859 | 0 | 69 | 67 | 80.5944 | 3227.41
4886 | 127924 | 0 | 69 | 67 | 70.2759 | 3226.75
4887 | 127862 | 0 | 70 | 67 | 70.8202 | 3225.77
4888 | 127813 | 0 | 70 | 67 | 70.3316 | 3224.86
4889 | 127763 | 0 | 69 | 67 | 69.5653 | 3223.73
4890 | 127718 | 0 | 69 | 67 | 70.3297 | 3222.73
4891 | 195913 | 0 | 69 | 67 | 77.7319 | 3221.85
4892 | 127534 | 0 | 68 | 67 | 74.0839 | 3221.14
4893 | 127495 | 0 | 68 | 67 | 77.61 | 3220.71
4894 | 127527 | 0 | 69 | 68 | 77.1188 | 3220.31
4895 | 127437 | 0 | 69 | 68 | 76.0459 | 3219.93
4896 | 190778 | 0 | 70 | 68 | 86.3875 | 8372.87
4897 | 127580 | 0 | 70 | 68 | 79.1133 | 8372.44
4898 | 127559 | 0 | 70 | 68 | 79.0617 | 8371.19
4899 | 127517 | 0 | 70 | 68 | 79.0597 | 8370.45
4900 | 198063 | 0 | 69 | 68 | 87.9902 | 9282.45
4901 | 277838 | 0 | 69 | 68 | 128.278 | 11313.6
4902 | 1427350 | -7852.05 | 68 | 68 | 295.271 | 30454
4903 | 1420890 | -26075.9 | 69 | 68 | 319.863 | 33394.5
4904 | 1324460 | -19150.5 | 69 | 68 | 316.158 | 42254.5
4905 | 1363010 | -17737.6 | 70 | 69 | 318.788 | 65817.2
4906 | 1437300 | -15790.9 | 72 | 70 | 312.509 | 67290.8
4907 | 1352720 | -12204.9 | 74 | 71 | 294.745 | 67291.4
4908 | 1452710 | -19279 | 76 | 72 | 319.281 | 67294.1
4909 | 1523070 | -13709.3 | 78 | 71 | 339.807 | 67295.1
4910 | 1512210 | -17223.6 | 79 | 70 | 348.072 | 65823
4911 | 1528430 | -18640.1 | 81 | 69 | 351.331 | 59933.9
4912 | 1580550 | -24902.6 | 81 | 70 | 348.764 | 49626.9
4913 | 1564410 | -24268.1 | 81 | 72 | 325.183 | 37847.6
4914 | 1176760 | -21455.8 | 81 | 73 | 230.68 | 23123.4
4915 | 190575 | 0 | 78 | 72 | 107.527 | 16497.7
4916 | 170066 | 0 | 76 | 71 | 100.396 | 15762.1
4917 | 156983 | 0 | 73 | 70 | 92.0329 | 9858
4918 | 146129 | 0 | 72 | 69 | 83.7362 | 9618.97
4919 | 141129 | 0 | 70 | 67 | 79.657 | 8379.26
4920 | 139653 | 0 | 69 | 66 | 78.9088 | 8378.28
4921 | 138912 | 0 | 68 | 66 | 78.8324 | 8377.53
4922 | 138105 | 0 | 68 | 65 | 79.0616 | 8376.95
4923 | 137372 | 0 | 67 | 64 | 78.7199 | 8376.46
4924 | 198608 | 0 | 66 | 64 | 87.849 | 9288.89
4925 | 274705 | 0 | 66 | 64 | 127.845 | 11320.4
4926 | 1118700 | -6672.64 | 65 | 63 | 267.382 | 30461.1
4927 | 1194860 | -22866.4 | 67 | 63 | 321.995 | 33402
4928 | 1203300 | -22431 | 69 | 64 | 328.618 | 42259
4929 | 1219190 | -22506.3 | 71 | 64 | 330.27 | 65823.1
4930 | 1225880 | -19392 | 73 | 64 | 323.556 | 67298
4931 | 1125750 | -14860.5 | 76 | 64 | 305.854 | 67299.2
4932 | 1189660 | -27517.2 | 78 | 64 | 308.561 | 67299.7
4933 | 1262650 | -15984.2 | 79 | 64 | 331.177 | 67299.7
4934 | 1331380 | -20101.3 | 79 | 65 | 341.858 | 65827.3
4935 | 1410450 | -21922.2 | 80 | 66 | 347.909 | 59937.8
4936 | 1454860 | -27294 | 80 | 67 | 345.29 | 49630.5
4937 | 1421060 | -33337 | 80 | 68 | 320.23 | 37850.8
4938 | 1059070 | -37459.6 | 80 | 68 | 229.792 | 23126.3
4939 | 194441 | 0 | 77 | 68 | 116.251 | 16500.4
4940 | 174078 | 0 | 74 | 68 | 104.531 | 15764.9
4941 | 160788 | 0 | 71 | 67 | 94.6049 | 9861.43
4942 | 149760 | 0 | 70 | 66 | 86.4431 | 9622.6
4943 | 144722 | 0 | 68 | 65 | 81.7982 | 8382.98
4944 | 143078 | 0 | 67 | 64 | 81.5528 | 8381.97
4945 | 142288 | 0 | 66 | 64 | 81.3862 | 8381.06
4946 | 141347 | 0 | 66 | 64 | 81.7809 | 8380.29
4947 | 140395 | 0 | 65 | 63 | 81.136 | 8379.53
4948 | 143811 | 0 | 66 | 64 | 84.3434 | 9291.72
4949 | 277468 | 0 | 67 | 64 | 141.39 | 11323.3
4950 | 1187530 | -5418.55 | 68 | 65 | 294.25 | 30464.1
4951 | 1260100 | -24794.2 | 69 | 65 | 327.309 | 33404.9
4952 | 1267740 | -24252 | 71 | 66 | 334.587 | 42260.8
4953 | 1259900 | -24251 | 72 | 66 | 334.978 | 65823.2
4954 | 1281230 | -21038.5 | 73 | 67 | 329.278 | 67297.6
4955 | 1189930 | -17303.7 | 73 | 68 | 309.046 | 67297.6
4956 | 1253090 | -16050.3 | 74 | 69 | 313.102 | 67297.5
4957 | 1423950 | -19382.9 | 76 | 70 | 341.37 | 67298.2
4958 | 1496680 | -22829.2 | 79 | 71 | 352.189 | 65826.4
4959 | 1573790 | -23870.1 | 81 | 72 | 358.502 | 59937.4
4960 | 1587040 | -22419.9 | 81 | 72 | 353.744 | 49630.4
4961 | 1539570 | -19455.1 | 81 | 73 | 327.414 | 37850.7
4962 | 1110330 | -16546.8 | 81 | 73 | 229.797 | 23126.5
4963 | 196151 | 0 | 77 | 72 | 117.898 | 16500.9
4964 | 175304 | 0 | 74 | 71 | 105.091 | 15765.3
4965 | 161800 | 0 | 70 | 69 | 94.089 | 9861.6
4966 | 150911 | 0 | 71 | 70 | 87.9044 | 9622.81
4967 | 145926 | 0 | 72 | 71 | 84.06 | 8383.34
4968 | 144429 | 0 | 73 | 72 | 83.4477 | 8382.58
4969 | 143369 | 0 | 72 | 71 | 82.111 | 8381.9
4970 | 142394 | 0 | 72 | 70 | 82.5521 | 8381.2
4971 | 141607 | 0 | 71 | 70 | 81.8326 | 8380.41
4972 | 144947 | 0 | 71 | 69 | 84.6484 | 9292.56
4973 | 293372 | 0 | 70 | 69 | 144.178 | 11323.8
4974 | 1372470 | -4169.85 | 70 | 69 | 306.642 | 30464.2
4975 | 1461280 | -25344.2 | 72 | 69 | 340.687 | 33404.5
4976 | 1425110 | -24883.6 | 75 | 69 | 346.081 | 42260.9
4977 | 1430970 | -24563 | 77 | 69 | 345.377 | 65824.5
4978 | 1438370 | -21056.6 | 78 | 69 | 337.599 | 67299.4
4979 | 1246390 | -17042.5 | 78 | 67 | 312.994 | 67299.9
4980 | 1275690 | -24784.1 | 79 | 66 | 313.484 | 67300.5
4981 | 1356600 | -19302.2 | 79 | 66 | 336.007 | 67300.9
4982 | 1382240 | -23812.3 | 78 | 66 | 344.199 | 65828.6
4983 | 1404440 | -25467.8 | 78 | 66 | 346.513 | 59939.1
4984 | 1357800 | -24738.7 | 77 | 65 | 338.102 | 49631.9
4985 | 1211770 | -20951.1 | 76 | 64 | 306.967 | 37852
4986 | 850312 | -23098.8 | 75 | 63 | 213.248 | 23127.5
4987 | 195214 | 0 | 71 | 62 | 111.541 | 16501.5
4988 | 174718 | 0 | 68 | 60 | 102.249 | 15766.1
4989 | 161215 | 0 | 64 | 58 | 92.6883 | 9863
4990 | 150023 | 0 | 62 | 57 | 83.2416 | 9624.8
4991 | 144933 | 0 | 61 | 56 | 79.7513 | 8385.84
4992 | 143278 | 0 | 59 | 55 | 79.1586 | 8385.66
4993 | 142314 | 0 | 58 | 55 | 79.3695 | 8385.72
4994 | 141199 | 0 | 56 | 54 | 79.3188 | 8385.88
4995 | 140375 | 0 | 55 | 54 | 79.2811 | 8386.1
4996 | 143325 | 0 | 56 | 55 | 81.2776 | 9299.25
4997 | 239290 | 0 | 56 | 55 | 125.675 | 11331.5
4998 | 691108 | -9682.63 | 57 | 56 | 263.475 | 30473.1
4999 | 831375 | -30887 | 60 | 57 | 298.298 | 33414.5
5000 | 906488 | -28112.7 | 64 | 58 | 309.463 | 42265
5001 | 964440 | -27361.8 | 67 | 59 | 313.099 | 65827.1
5002 | 976576 | -23204.8 | 69 | 59 | 305.96 | 67302
5003 | 908390 | -18137.2 | 72 | 59 | 290.77 | 67303.1
5004 | 949890 | -22019.4 | 74 | 59 | 293.672 | 67303.3
5005 | 1035910 | -19836.4 | 74 | 59 | 315.881 | 67303.1
5006 | 1114560 | -23293.8 | 75 | 60 | 327.77 | 65830.4
5007 | 1148010 | -24760.1 | 75 | 60 | 330.75 | 59940.7
5008 | 1135540 | -23820.3 | 75 | 60 | 324.616 | 49633.4
5009 | 1035040 | -20360.2 | 74 | 60 | 295.023 | 37853.5
5010 | 739447 | -21386.6 | 74 | 60 | 206.124 | 23128.8
5011 | 194758 | 0 | 69 | 60 | 110.531 | 16502.7
5012 | 174192 | 0 | 65 | 58 | 101.293 | 15767.9
5013 | 160698 | 0 | 60 | 56 | 90.8763 | 9865.32
5014 | 149596 | 0 | 58 | 56 | 83.6601 | 9627.52
5015 | 144451 | 0 | 57 | 55 | 79.9484 | 8388.9
5016 | 142489 | 0 | 55 | 54 | 75.3258 | 8389.07
5017 | 141335 | 0 | 53 | 53 | 75.2727 | 8389.39
5018 | 140103 | 0 | 52 | 51 | 75.2168 | 8390.48
5019 | 139262 | 0 | 50 | 50 | 75.1782 | 8391.34
5020 | 138493 | 0 | 51 | 51 | 73.5433 | 8392.34
5021 | 137684 | 0 | 53 | 52 | 71.9066 | 8393.33
5022 | 136962 | 0 | 54 | 53 | 70.9747 | 8394.37
5023 | 220450 | -26046.2 | 59 | 56 | 90.5998 | 8395.39
5024 | 260764 | -19306 | 63 | 59 | 97.1274 | 8396.16
5025 | 328570 | -19174.5 | 68 | 61 | 112.009 | 8406.73
5026 | 371811 | -16812.5 | 70 | 62 | 113.769 | 8408.05
5027 | 422601 | -16424.6 | 73 | 63 | 117.686 | 8409.23
5028 | 451918 | -16842.1 | 75 | 63 | 119.729 | 8409.85
5029 | 483497 | -16527.8 | 75 | 64 | 121.086 | 8410.21
5030 | 193898 | 0 | 76 | 65 | 84.9578 | 8410.6
5031 | 133020 | 0 | 76 | 66 | 73.2149 | 8411
5032 | 132750 | 0 | 76 | 66 | 72.8419 | 8404.96
5033 | 132563 | 0 | 75 | 66 | 73.3925 | 8401.55
5034 | 132412 | 0 | 75 | 67 | 74.3367 | 8399.41
5035 | 131843 | 0 | 74 | 66 | 75.3897 | 8397.3
5036 | 131597 | 0 | 73 | 65 | 78.4093 | 8396.07
5037 | 131535 | 0 | 72 | 65 | 79.8256 | 8395.01
5038 | 131052 | 0 | 71 | 64 | 78.9625 | 8394.17
5039 | 130888 | 0 | 71 | 64 | 78.4264 | 8393.46
5040 | 130576 | 0 | 70 | 64 | 75.2297 | 3239.52
5041 | 130293 | 0 | 70 | 64 | 75.671 | 3238.98
5042 | 130078 | 0 | 69 | 64 | 75.1016 | 3238.65
5043 | 129592 | 0 | 69 | 63 | 75.5183 | 3238.29
5044 | 129466 | 0 | 69 | 63 | 73.9075 | 3237.99
5045 | 129259 | 0 | 68 | 63 | 71.7519 | 3237.71
5046 | 128857 | 0 | 68 | 62 | 70.339 | 3237.49
5047 | 128849 | 0 | 70 | 63 | 68.1246 | 3237.25
5048 | 128711 | 0 | 73 | 64 | 68.6221 | 3237.06
5049 | 188228 | 0 | 75 | 65 | 75.7857 | 3236.47
5050 | 194741 | 0 | 77 | 66 | 80.8545 | 3234.92
5051 | 202305 | 0 | 78 | 67 | 82.7162 | 3233.08
5052 | 209450 | 0 | 80 | 68 | 84.6422 | 3230.87
5053 | 213562 | 0 | 81 | 69 | 85.3482 | 3228.66
5054 | 217434 | 0 | 81 | 70 | 85.9962 | 3226.61
5055 | 280131 | 0 | 82 | 71 | 99.7563 | 3224.73
5056 | 271792 | 0 | 81 | 70 | 98.0448 | 3222.78
5057 | 216291 | 0 | 80 | 71 | 85.7403 | 3220.97
5058 | 128167 | 0 | 79 | 70 | 71.3655 | 3219.26
5059 | 128242 | 0 | 78 | 70 | 72.7727 | 3217.73
5060 | 128243 | 0 | 78 | 70 | 74.6863 | 3216.37
5061 | 128115 | 0 | 77 | 69 | 77.9254 | 3215.21
5062 | 128089 | 0 | 76 | 69 | 77.124 | 3214.25
5063 | 128030 | 0 | 76 | 69 | 76.3211 | 3213.38
5064 | 128300 | 0 | 75 | 69 | 79.305 | 8365.86
5065 | 127963 | 0 | 72 | 66 | 78.3441 | 8365.08
5066 | 127567 | 0 | 68 | 63 | 77.9237 | 8363.52
5067 | 127404 | 0 | 65 | 60 | 78.0833 | 8362.46
5068 | 186825 | 0 | 65 | 60 | 87.4988 | 9274.49
5069 | 262308 | 0 | 65 | 61 | 127.197 | 11305.9
5070 | 1183500 | -7043.51 | 65 | 61 | 274.881 | 30446.7
5071 | 1185430 | -31259 | 67 | 61 | 302.16 | 33387.7
5072 | 1152940 | -21899.9 | 68 | 62 | 303.801 | 42252.4
5073 | 1160090 | -17531.4 | 70 | 62 | 304.377 | 65815.1
5074 | 1153090 | -15848.4 | 70 | 62 | 295.792 | 67290.1
5075 | 1032410 | -12862.8 | 69 | 62 | 291.537 | 67292.1
5076 | 996116 | -12447.5 | 69 | 61 | 291.962 | 67293
5077 | 1063850 | -16095.9 | 69 | 61 | 314.545 | 67293.3
5078 | 1081600 | -19373.3 | 68 | 61 | 321.573 | 65821.1
5079 | 1073380 | -20833.3 | 68 | 60 | 322.595 | 59931.1
5080 | 1069380 | -20711.3 | 67 | 60 | 316.393 | 49624
5081 | 951186 | -17501.9 | 67 | 60 | 288.044 | 37844.6
5082 | 619543 | -14181 | 66 | 59 | 195.756 | 23120.6
5083 | 188139 | 0 | 64 | 59 | 111.6 | 16494.8
5084 | 168420 | 0 | 62 | 59 | 99.2803 | 15760.8
5085 | 155219 | 0 | 60 | 59 | 91.3959 | 9857.74
5086 | 144237 | 0 | 60 | 59 | 83.4157 | 9620.28
5087 | 139471 | 0 | 59 | 59 | 79.7216 | 8381.62
5088 | 137999 | 0 | 60 | 59 | 78.7488 | 8381.67
5089 | 137693 | 0 | 61 | 61 | 79.0266 | 7929.03
5090 | 137045 | 0 | 62 | 62 | 79.0352 | 7929.26
5091 | 136261 | 0 | 62 | 62 | 78.7411 | 7929.39
5092 | 139486 | 0 | 63 | 62 | 83.0742 | 8786.21
5093 | 249271 | 0 | 63 | 63 | 129.581 | 10693.2
5094 | 964161 | -8333 | 64 | 64 | 270.789 | 28657.2
5095 | 1130150 | -21423.1 | 66 | 66 | 300.882 | 31417.1
5096 | 1281730 | -20492.8 | 70 | 69 | 334.282 | 39725.8
5097 | 1383970 | -19120.8 | 77 | 70 | 343.867 | 61838.1
5098 | 1507210 | -15580.4 | 80 | 72 | 340.082 | 63224.1
5099 | 1388280 | -12542.9 | 83 | 72 | 320.03 | 63225.6
5100 | 1436810 | -22418.1 | 86 | 71 | 322.663 | 63226.4
5101 | 1596740 | -13611.4 | 89 | 72 | 350.794 | 63226.4
5102 | 1654370 | -24397.2 | 90 | 72 | 360.001 | 61844.3
5103 | 1763190 | -33597.5 | 89 | 73 | 373.385 | 56317.1
5104 | 1717790 | -33853.1 | 87 | 72 | 367.632 | 46643.8
5105 | 1738120 | -38182.7 | 88 | 74 | 338.622 | 35588.6
5106 | 1259460 | -38747.5 | 86 | 73 | 236.464 | 21769.5
5107 | 195006 | 0 | 83 | 72 | 121.76 | 15551.2
5108 | 174431 | 0 | 78 | 72 | 103.832 | 14860.6
5109 | 161161 | 0 | 77 | 71 | 92.9084 | 9318.39
5110 | 150195 | 0 | 73 | 70 | 83.7056 | 9093.37
5111 | 145085 | 0 | 71 | 69 | 79.8898 | 7929.54
5112 | 143549 | 0 | 70 | 69 | 79.5634 | 7928.3
5113 | 142628 | 0 | 71 | 69 | 80.1095 | 7927.4
5114 | 141695 | 0 | 69 | 68 | 79.1622 | 7926.67
5115 | 140790 | 0 | 68 | 67 | 79.3469 | 7926.04
5116 | 143970 | 0 | 67 | 66 | 82.9193 | 8782.18
5117 | 281899 | 0 | 68 | 65 | 131.867 | 10688.6
5118 | 1272390 | -4935.78 | 69 | 66 | 278.287 | 28652.2
5119 | 1385920 | -24532.3 | 73 | 67 | 337.437 | 31411.7
5120 | 1392930 | -23834.6 | 76 | 68 | 343.545 | 39725.4
5121 | 1458200 | -23228.6 | 79 | 69 | 347.291 | 61840.4
5122 | 1556300 | -19438.7 | 81 | 71 | 345.729 | 63224.9
5123 | 1460280 | -14945 | 83 | 72 | 326.97 | 63226.1
5124 | 1514850 | -31111.3 | 84 | 71 | 330.362 | 63226.7
5125 | 1667120 | -27923.2 | 87 | 72 | 356.91 | 63226.7
5126 | 1698640 | -32172.2 | 89 | 72 | 367.204 | 61844.9
5127 | 1754570 | -34379.4 | 90 | 72 | 375.351 | 56317.7
5128 | 1751420 | -33624.8 | 89 | 72 | 372.376 | 46644.5
5129 | 1676180 | -36584.3 | 88 | 72 | 336.283 | 35589.2
5130 | 1214910 | -43444.3 | 83 | 71 | 235.559 | 21770.2
5131 | 196671 | 0 | 83 | 71 | 122.792 | 15551.8
5132 | 176117 | 0 | 81 | 71 | 109.337 | 14861.1
5133 | 162983 | 0 | 80 | 72 | 97.3607 | 9318.7
5134 | 151909 | 0 | 79 | 71 | 88.1064 | 9093.67
5135 | 146824 | 0 | 79 | 71 | 84.08 | 7929.55
5136 | 145356 | 0 | 79 | 72 | 83.3225 | 7927.97
5137 | 144421 | 0 | 79 | 72 | 83.2243 | 7926.62
5138 | 143687 | 0 | 78 | 73 | 83.148 | 7925.35
5139 | 142901 | 0 | 79 | 73 | 83.0671 | 7923.99
5140 | 235463 | 0 | 78 | 74 | 102.942 | 8779.41
5141 | 313768 | 0 | 78 | 74 | 154.502 | 10685.1
5142 | 1863040 | 0 | 79 | 75 | 346.447 | 28647.9
5143 | 1860770 | -26122.9 | 80 | 75 | 372.107 | 31406.7
5144 | 1759590 | -25630.9 | 81 | 75 | 369.245 | 39725.1
5145 | 1831910 | -25288.6 | 83 | 76 | 372.83 | 61838.6
5146 | 1932350 | -27075.6 | 87 | 77 | 371.611 | 63222.2
5147 | 1809640 | -34671.1 | 89 | 78 | 357.886 | 63224.4
5148 | 1910270 | -34532.9 | 92 | 78 | 355.02 | 63225.5
5149 | 1994660 | -31071.6 | 92 | 78 | 387.148 | 63225.7
5150 | 2028890 | -31195.2 | 92 | 78 | 393.872 | 61844.3
5151 | 2074510 | -31420.9 | 94 | 78 | 400.315 | 56316.8
5152 | 1979480 | -31084.8 | 91 | 77 | 391.352 | 46643.7
5153 | 1877810 | -34472.4 | 87 | 77 | 353.996 | 35588.6
5154 | 1439210 | -47290.5 | 80 | 78 | 258.382 | 21769.3
5155 | 198986 | 0 | 82 | 77 | 123.793 | 15550.9
5156 | 177566 | 0 | 80 | 76 | 109.665 | 14860.3
5157 | 164124 | 0 | 78 | 75 | 97.515 | 9317.62
5158 | 153116 | 0 | 79 | 75 | 88.2376 | 9092.76
5159 | 147894 | 0 | 79 | 75 | 84.1932 | 7928.59
5160 | 146412 | 0 | 78 | 76 | 83.5519 | 7927.09
5161 | 145351 | 0 | 77 | 75 | 83.4402 | 7925.72
5162 | 144472 | 0 | 77 | 75 | 83.3485 | 7924.4
5163 | 143673 | 0 | 77 | 75 | 83.2656 | 7923.12
5164 | 147519 | 0 | 77 | 75 | 87.1242 | 8778.7
5165 | 321627 | 0 | 77 | 75 | 154.847 | 10684.4
5166 | 1908950 | 0 | 77 | 76 | 348.083 | 28647.3
5167 | 1915050 | -25770.5 | 79 | 76 | 377.148 | 31406.1
5168 | 1887900 | -27400.9 | 82 | 77 | 376.642 | 39724.5
5169 | 1985490 | -26615.6 | 84 | 79 | 382.819 | 61838.3
5170 | 2021280 | -22426.2 | 87 | 79 | 377.47 | 63223.5
5171 | 1935970 | -33198.7 | 91 | 80 | 367.341 | 63224.6
5172 | 1945350 | -33630.8 | 89 | 79 | 367.753 | 63225.4
5173 | 2097060 | -31070.6 | 90 | 80 | 392.467 | 63226
5174 | 2134090 | -31167 | 93 | 81 | 401.678 | 61844.1
5175 | 2157490 | -30932.8 | 94 | 80 | 405.789 | 56316.5
5176 | 2250700 | -30169.8 | 96 | 81 | 397.759 | 46643.2
5177 | 2004290 | -33380.4 | 89 | 79 | 360.529 | 35588.1
5178 | 1055160 | -47531.6 | 73 | 67 | 226.924 | 21769.4
5179 | 197191 | 0 | 69 | 66 | 121.583 | 15550.9
5180 | 176984 | 0 | 70 | 67 | 109.254 | 14860
5181 | 163628 | 0 | 71 | 68 | 97.1624 | 9317.59
5182 | 152448 | 0 | 71 | 68 | 87.0567 | 9093.61
5183 | 147143 | 0 | 70 | 67 | 82.4415 | 7930.25
5184 | 145082 | 0 | 69 | 66 | 77.6154 | 7929.35
5185 | 143923 | 0 | 67 | 65 | 76.85 | 7928.53
5186 | 142883 | 0 | 65 | 64 | 76.5902 | 7928.49
5187 | 141997 | 0 | 65 | 64 | 77.4164 | 7928.21
5188 | 141224 | 0 | 65 | 65 | 77.353 | 7928.08
5189 | 140408 | 0 | 66 | 65 | 77.855 | 7927.97
5190 | 139820 | 0 | 67 | 67 | 75.4517 | 7927.62
5191 | 680309 | -2876.44 | 71 | 68 | 132.588 | 7927.33
5192 | 686920 | -5442.71 | 75 | 70 | 134.038 | 7927.23
5193 | 663896 | -8413.91 | 76 | 70 | 131.771 | 7945.48
5194 | 689304 | -9513.58 | 79 | 71 | 133.603 | 7948.78
5195 | 728917 | -10251 | 81 | 72 | 136.088 | 7950.46
5196 | 720950 | -20238.2 | 82 | 70 | 135.686 | 7951.05
5197 | 748434 | -26253.7 | 83 | 69 | 137.743 | 7951.96
5198 | 209220 | 0 | 83 | 68 | 88.3293 | 7952.61
5199 | 215743 | 0 | 84 | 68 | 87.8662 | 7953.19
5200 | 269985 | 0 | 83 | 67 | 100.878 | 7944.92
5201 | 268002 | 0 | 82 | 67 | 103.848 | 7940.3
5202 | 184345 | 0 | 81 | 65 | 87.9021 | 7936.92
5203 | 133875 | 0 | 78 | 65 | 81.0797 | 7934.19
5204 | 133607 | 0 | 76 | 65 | 82.9734 | 7932.24
5205 | 133099 | 0 | 73 | 63 | 81.7542 | 7930.5
5206 | 132821 | 0 | 70 | 62 | 79.8051 | 7929.24
5207 | 132594 | 0 | 68 | 62 | 79.2659 | 7928.27
5208 | 132101 | 0 | 70 | 62 | 74.4952 | 3091.12
5209 | 131703 | 0 | 69 | 61 | 73.6237 | 3090.61
5210 | 131441 | 0 | 68 | 61 | 73.5731 | 3090.44
5211 | 131156 | 0 | 67 | 61 | 73.5223 | 3090.11
5212 | 130723 | 0 | 65 | 60 | 73.1687 | 3089.83
5213 | 130427 | 0 | 60 | 59 | 72.2377 | 3089.61
5214 | 129553 | 0 | 57 | 55 | 72.0099 | 3089.54
5215 | 129358 | 0 | 57 | 54 | 68.1254 | 3089.6
5216 | 128850 | 0 | 57 | 52 | 67.6717 | 3089.94
5217 | 128680 | 0 | 57 | 51 | 68.1871 | 3090.51
5218 | 128509 | 0 | 57 | 51 | 68.1287 | 3090.86
5219 | 128328 | 0 | 59 | 52 | 67.6444 | 3091.31
5220 | 157030 | 0 | 65 | 54 | 74.486 | 3091.49
5221 | 176619 | 0 | 65 | 54 | 74.0893 | 3091.63
5222 | 176056 | 0 | 68 | 55 | 75.0593 | 3090.64
5223 | 177403 | 0 | 67 | 54 | 73.9784 | 3089.88
5224 | 127618 | 0 | 67 | 55 | 69.1014 | 3088.77
5225 | 127354 | 0 | 66 | 54 | 72.4138 | 3088.05
5226 | 127489 | 0 | 66 | 55 | 75.306 | 3087.35
5227 | 127233 | 0 | 64 | 54 | 75.4386 | 3086.7
5228 | 127188 | 0 | 59 | 53 | 76.2276 | 3086.36
5229 | 126886 | 0 | 57 | 52 | 77.2986 | 3086.28
5230 | 126937 | 0 | 57 | 53 | 76.5006 | 3086.41
5231 | 126799 | 0 | 57 | 54 | 75.6945 | 3086.88
5232 | 127042 | 0 | 57 | 55 | 78.676 | 7923.97
5233 | 154068 | 0 | 57 | 55 | 83.8948 | 7924.55
5234 | 126598 | 0 | 57 | 55 | 78.6768 | 7924.33
5235 | 126374 | 0 | 56 | 54 | 78.6461 | 7924.42
5236 | 129801 | 0 | 54 | 52 | 82.2635 | 8781.18
5237 | 232678 | 0 | 53 | 52 | 128.594 | 10688.2
5238 | 702537 | -13316.5 | 54 | 53 | 255.463 | 28652.3
5239 | 789448 | -25023.1 | 58 | 55 | 281.487 | 31412.4
5240 | 826049 | -22691.7 | 61 | 55 | 286.842 | 39722.3
5241 | 910671 | -22040.5 | 64 | 57 | 292.225 | 61836.7
5242 | 940487 | -18808.9 | 66 | 58 | 285.145 | 63221.5
5243 | 825284 | -14630.1 | 69 | 56 | 265.775 | 63222.8
5244 | 931590 | -26477.9 | 71 | 58 | 273.077 | 63223.2
5245 | 964486 | -15286.3 | 72 | 57 | 309.545 | 63223.2
5246 | 1057370 | -18153.2 | 74 | 58 | 323.098 | 61841.5
5247 | 1124980 | -20049.9 | 74 | 59 | 327.685 | 56314.3
5248 | 1079580 | -20406.5 | 74 | 58 | 320.728 | 46641.2
5249 | 1002240 | -26822.2 | 74 | 58 | 294.51 | 35585.9
5250 | 698822 | -27097.2 | 72 | 57 | 207.465 | 21766.9
5251 | 188514 | 0 | 68 | 57 | 112.284 | 15548.4
5252 | 168441 | 0 | 65 | 56 | 102.401 | 14858.7
5253 | 155466 | 0 | 61 | 56 | 90.9316 | 9317.98
5254 | 144247 | 0 | 57 | 54 | 83.1611 | 9094.59
5255 | 139517 | 0 | 55 | 53 | 79.7237 | 7931.92
5256 | 138246 | 0 | 55 | 54 | 78.7598 | 7931.64
5257 | 137371 | 0 | 55 | 54 | 78.7198 | 7931.56
5258 | 136688 | 0 | 57 | 55 | 78.6886 | 7931.53
5259 | 136040 | 0 | 56 | 55 | 78.6592 | 7932.06
5260 | 139053 | 0 | 57 | 55 | 82.6833 | 8788.61
5261 | 244006 | 0 | 58 | 54 | 129.127 | 10695.6
5262 | 686645 | -10801.7 | 58 | 55 | 255.127 | 28660
5263 | 753765 | -26164.3 | 59 | 55 | 285.642 | 31419.7
5264 | 817972 | -24836.2 | 62 | 57 | 304.974 | 39728.1
5265 | 954548 | -23044.1 | 68 | 59 | 315.814 | 61840.2
5266 | 1040860 | -19281 | 71 | 61 | 311.359 | 63223.1
5267 | 1001060 | -14586.7 | 74 | 62 | 297.598 | 63225.9
5268 | 1115280 | -28430.3 | 77 | 63 | 303.54 | 63226.7
5269 | 1185880 | -14837.5 | 78 | 63 | 325.967 | 63226.9
5270 | 1242070 | -19162.7 | 79 | 63 | 335.67 | 61845.2
5271 | 1272310 | -20806.7 | 80 | 63 | 338.704 | 56317.9
5272 | 1276480 | -22713 | 80 | 63 | 334.769 | 46644.6
5273 | 1212360 | -32128.9 | 79 | 63 | 310.934 | 35589.1
5274 | 885219 | -26184.7 | 78 | 64 | 222.253 | 21770.2
5275 | 193225 | 0 | 74 | 63 | 120.781 | 15551.5
5276 | 173102 | 0 | 69 | 62 | 104.27 | 14861.3
5277 | 159701 | 0 | 65 | 61 | 91.2757 | 9320.37
5278 | 148522 | 0 | 63 | 60 | 83.2099 | 9096.52
5279 | 143649 | 0 | 62 | 60 | 79.7292 | 7933.37
5280 | 142090 | 0 | 61 | 60 | 79.1402 | 7932.78
5281 | 141115 | 0 | 61 | 60 | 79.3517 | 7932.29
5282 | 139890 | 0 | 58 | 57 | 79.0046 | 7932.42
5283 | 139217 | 0 | 57 | 57 | 79.2284 | 7932.43
5284 | 142298 | 0 | 59 | 58 | 82.8308 | 8789.3
5285 | 257577 | 0 | 59 | 58 | 129.763 | 10696.5
5286 | 792277 | -9157.02 | 59 | 58 | 257.104 | 28660.4
5287 | 943973 | -27138.4 | 62 | 60 | 288.277 | 31420.2
5288 | 1009700 | -25506 | 66 | 61 | 316.704 | 39729
5289 | 1092670 | -23657.7 | 72 | 62 | 324.902 | 61841.7
5290 | 1225270 | -19497.4 | 76 | 65 | 323.996 | 63226.6
5291 | 1176370 | -14328.7 | 80 | 66 | 307.238 | 63228
5292 | 1202660 | -31640.9 | 83 | 64 | 308.371 | 63228.6
5293 | 1248040 | -14920.3 | 85 | 63 | 329.913 | 63228.6
5294 | 1327250 | -19563.5 | 85 | 64 | 340.987 | 61846.8
5295 | 1409210 | -24301.6 | 84 | 65 | 347.237 | 56319.6
5296 | 1393880 | -26827 | 84 | 65 | 341.965 | 46646.2
5297 | 1284380 | -33946.2 | 84 | 64 | 319.377 | 35590.7
5298 | 928962 | -29293.8 | 83 | 64 | 227.166 | 21771.7
5299 | 195431 | 0 | 78 | 64 | 122.253 | 15553.1
5300 | 175302 | 0 | 71 | 64 | 102.816 | 14862.5
5301 | 161588 | 0 | 68 | 63 | 91.7551 | 9321.18
5302 | 150397 | 0 | 65 | 62 | 83.1118 | 9096.75
5303 | 145100 | 0 | 63 | 60 | 79.5747 | 7933.56
5304 | 143590 | 0 | 62 | 60 | 79.1264 | 7932.98
5305 | 142553 | 0 | 62 | 60 | 79.3366 | 7932.71
5306 | 141653 | 0 | 61 | 60 | 79.0008 | 7932.62
5307 | 140738 | 0 | 61 | 60 | 79.2155 | 7932.56
5308 | 143608 | 0 | 60 | 59 | 82.6353 | 8789.28
5309 | 254505 | 0 | 58 | 57 | 129.621 | 10696.3
5310 | 817993 | -8428.13 | 59 | 58 | 255.561 | 28660.4
5311 | 996917 | -28625.8 | 64 | 61 | 292.141 | 31420.4
5312 | 1092110 | -26853.9 | 68 | 63 | 309.177 | 39729.3
5313 | 1175940 | -25007.6 | 74 | 64 | 330.389 | 61841.7
5314 | 1279220 | -20719.1 | 78 | 66 | 326.696 | 63226.8
5315 | 1258010 | -15682.8 | 80 | 68 | 312.273 | 63228.2
5316 | 1392070 | -31535.5 | 84 | 69 | 320.393 | 63228.8
5317 | 1442080 | -16022.6 | 86 | 68 | 340.934 | 63228.8
5318 | 1576600 | -27440 | 86 | 70 | 355.044 | 61847
5319 | 1585350 | -30660.6 | 86 | 69 | 357.437 | 56319.7
5320 | 1551560 | -33490.3 | 88 | 68 | 356.396 | 46646.4
5321 | 1398470 | -29873.2 | 85 | 67 | 325.89 | 35591
5322 | 1016450 | -32616.5 | 82 | 67 | 223.375 | 21772.1
5323 | 195783 | 0 | 77 | 65 | 121.477 | 15553.5
5324 | 175740 | 0 | 73 | 65 | 103.562 | 14862.8
5325 | 162111 | 0 | 69 | 64 | 91.554 | 9321.25
5326 | 150813 | 0 | 68 | 63 | 83.7853 | 9096.8
5327 | 145782 | 0 | 67 | 62 | 80.0252 | 7933.51
5328 | 144103 | 0 | 64 | 61 | 78.8238 | 7932.8
5329 | 142949 | 0 | 63 | 60 | 79.2529 | 7932.34
5330 | 142276 | 0 | 62 | 61 | 79.1843 | 7931.58
5331 | 141022 | 0 | 60 | 59 | 78.8016 | 7931.47
5332 | 144250 | 0 | 61 | 60 | 83.2146 | 8788.06
5333 | 262427 | 0 | 63 | 61 | 130.761 | 10695
5334 | 995629 | -7293.54 | 63 | 62 | 263.139 | 28659.1
5335 | 1209540 | -27467.1 | 72 | 65 | 310.673 | 31419
5336 | 1206330 | -26514.8 | 72 | 65 | 318.309 | 39728.7
5337 | 1280100 | -25767.3 | 74 | 66 | 334.805 | 61841.3
5338 | 1372220 | -21249.6 | 79 | 68 | 332.908 | 63225.6
5339 | 1311240 | -16253.7 | 83 | 69 | 316.253 | 63227.5
5340 | 1383970 | -33385.9 | 87 | 68 | 323.58 | 63227.9
5341 | 1411130 | -22467.4 | 84 | 67 | 339.927 | 63228.3
5342 | 1413750 | -28765.8 | 84 | 66 | 346.256 | 61846.7
5343 | 1456430 | -25400.9 | 83 | 66 | 350.14 | 56319.1
5344 | 1487730 | -29390.8 | 85 | 67 | 347.823 | 46645.8
5345 | 1421100 | -34835.3 | 85 | 67 | 330.109 | 35590.5
5346 | 1004950 | -31493.8 | 83 | 66 | 233.307 | 21771.4
5347 | 196400 | 0 | 79 | 66 | 123.067 | 15553
5348 | 176133 | 0 | 75 | 66 | 109.545 | 14862.3
5349 | 162464 | 0 | 71 | 65 | 93.7875 | 9320.76
5350 | 151376 | 0 | 68 | 65 | 83.2756 | 9096.19
5351 | 145381 | 0 | 66 | 60 | 79.7016 | 7932.73
5352 | 144593 | 0 | 65 | 63 | 75.3539 | 7931.65
5353 | 143284 | 0 | 64 | 63 | 75.2542 | 7930.83
5354 | 142214 | 0 | 64 | 63 | 75.4656 | 7931.27
5355 | 141133 | 0 | 63 | 62 | 75.1166 | 7931.29
5356 | 140310 | 0 | 61 | 61 | 74.7503 | 7931.42
5357 | 139367 | 0 | 61 | 60 | 75.2194 | 7931.15
5358 | 138649 | 0 | 61 | 60 | 72.1178 | 7931.41
5359 | 498418 | -4746.37 | 65 | 63 | 120.778 | 7931.25
5360 | 500522 | -6181.77 | 69 | 65 | 121.359 | 7931.54
5361 | 542389 | -10750.9 | 74 | 66 | 125.724 | 7948.08
5362 | 590104 | -11596 | 78 | 68 | 127.609 | 7950.61
5363 | 676794 | -18906.4 | 82 | 69 | 132.336 | 7952.54
5364 | 702767 | -20774.8 | 84 | 69 | 134.045 | 7953
5365 | 722807 | -28438.4 | 84 | 68 | 135.88 | 7953.94
5366 | 208680 | 0 | 86 | 68 | 87.6437 | 7954.38
5367 | 214740 | 0 | 85 | 67 | 87.1208 | 7954.97
5368 | 218336 | 0 | 86 | 69 | 88.5685 | 7946.99
5369 | 215353 | 0 | 81 | 67 | 91.5567 | 7942.08
5370 | 133420 | 0 | 78 | 65 | 80.5396 | 7938.67
5371 | 133393 | 0 | 75 | 65 | 79.6776 | 7935.9
5372 | 133160 | 0 | 74 | 65 | 79.9884 | 7933.97
5373 | 132998 | 0 | 70 | 65 | 79.0096 | 7932.54
5374 | 132692 | 0 | 68 | 67 | 78.6582 | 7931.54
5375 | 132124 | 0 | 67 | 66 | 78.0601 | 7930.74
5376 | 131585 | 0 | 66 | 65 | 73.506 | 3093.68
5377 | 131067 | 0 | 67 | 64 | 74.049 | 3092.94
5378 | 131128 | 0 | 67 | 66 | 73.7857 | 3092.89
5379 | 130700 | 0 | 68 | 66 | 74.0721 | 3092.75
5380 | 130388 | 0 | 69 | 66 | 74.0984 | 3092.63
5381 | 130127 | 0 | 69 | 66 | 73.8167 | 3092.49
5382 | 129791 | 0 | 68 | 65 | 72.2517 | 3092.24
5383 | 129589 | 0 | 68 | 65 | 68.8552 | 3092
5384 | 128933 | 0 | 67 | 62 | 68.1392 | 3091.68
5385 | 129590 | 0 | 66 | 65 | 68.4594 | 3091.41
5386 | 129022 | 0 | 67 | 66 | 68.7826 | 3090.99
5387 | 128850 | 0 | 68 | 66 | 68.6569 | 3090.6
5388 | 188743 | 0 | 69 | 66 | 75.6514 | 3090.07
5389 | 128520 | 0 | 72 | 67 | 72.0747 | 3089.56
5390 | 194095 | 0 | 75 | 68 | 84.5678 | 3088.82
5391 | 257584 | 0 | 78 | 68 | 94.5338 | 3088.24
5392 | 253872 | 0 | 78 | 68 | 95.1481 | 3086.76
5393 | 183838 | 0 | 79 | 69 | 83.0183 | 3085.34
5394 | 128168 | 0 | 77 | 68 | 77.3409 | 3083.78
5395 | 128197 | 0 | 75 | 68 | 76.5921 | 3082.47
5396 | 128229 | 0 | 72 | 68 | 76.986 | 3081.23
5397 | 128142 | 0 | 72 | 67 | 77.8 | 3080.25
5398 | 127836 | 0 | 71 | 65 | 76.6729 | 3079.58
5399 | 127870 | 0 | 70 | 64 | 75.836 | 3079.17
5400 | 188504 | 0 | 69 | 64 | 85.6634 | 7915.25
5401 | 127959 | 0 | 66 | 63 | 78.1876 | 7914.91
5402 | 127890 | 0 | 66 | 63 | 78.9243 | 7913.79
5403 | 127829 | 0 | 65 | 63 | 78.6235 | 7913.27
5404 | 131596 | 0 | 65 | 63 | 82.5226 | 8769.5
5405 | 263156 | 0 | 64 | 63 | 130.039 | 10676.1
5406 | 1253880 | -7408.88 | 64 | 63 | 287.819 | 28639.9
5407 | 1269120 | -28994.9 | 65 | 64 | 307.023 | 31399.6
5408 | 1194910 | -19920.2 | 67 | 64 | 306.891 | 39717.6
5409 | 1251160 | -20231.5 | 68 | 65 | 309.619 | 61831.5
5410 | 1267970 | -17597.4 | 71 | 65 | 302.071 | 63215.3
5411 | 1202030 | -13425.4 | 75 | 66 | 286.223 | 63216.9
5412 | 1227240 | -18111.9 | 73 | 66 | 284.193 | 63218.7
5413 | 1317670 | -16639.5 | 70 | 67 | 304.53 | 63219.5
5414 | 1406140 | -19139.3 | 75 | 68 | 323.186 | 61837.7
5415 | 1432050 | -20557.9 | 77 | 67 | 325.63 | 56310.3
5416 | 1492680 | -25427 | 77 | 68 | 325.999 | 46637.5
5417 | 1363070 | -20805.6 | 77 | 68 | 295.96 | 35582.6
5418 | 911330 | -11438.4 | 74 | 67 | 199.188 | 21764
5419 | 189412 | 0 | 68 | 66 | 113.44 | 15545.7
5420 | 169418 | 0 | 67 | 66 | 103.272 | 14855.7
5421 | 156138 | 0 | 65 | 64 | 91.635 | 9314.12
5422 | 145286 | 0 | 65 | 64 | 83.6611 | 9090.41
5423 | 140311 | 0 | 65 | 63 | 79.9505 | 7927.48
5424 | 139022 | 0 | 63 | 62 | 78.388 | 7927.14
5425 | 137972 | 0 | 63 | 60 | 78.8573 | 7926.92
5426 | 137456 | 0 | 63 | 60 | 78.8331 | 7926.73
5427 | 136818 | 0 | 63 | 60 | 78.8036 | 7926.57
5428 | 140120 | 0 | 62 | 60 | 82.5475 | 8783.2
5429 | 253468 | 0 | 61 | 60 | 129.37 | 10690.1
5430 | 881897 | -8069.89 | 61 | 59 | 263.548 | 28654
5431 | 947628 | -26389.9 | 61 | 59 | 293.288 | 31413.9
5432 | 920996 | -25785.6 | 61 | 59 | 289.319 | 39724.5
5433 | 931742 | -26226.9 | 62 | 59 | 309.475 | 61837.4
5434 | 943034 | -23930.3 | 62 | 60 | 302.311 | 63220.3
5435 | 833065 | -20520.3 | 62 | 59 | 282.397 | 63221
5436 | 899707 | -18190.7 | 65 | 61 | 288.146 | 63221.5
5437 | 1009710 | -21526.9 | 67 | 61 | 312.043 | 63222.1
5438 | 1045330 | -24343.5 | 67 | 61 | 320.205 | 61840.7
5439 | 1158610 | -24723.2 | 70 | 62 | 330.455 | 56313.7
5440 | 1201110 | -23514.7 | 71 | 63 | 328.631 | 46640.4
5441 | 1099120 | -19539.8 | 71 | 63 | 302.788 | 35585.1
5442 | 732906 | -14573.8 | 70 | 62 | 211.047 | 21766.2
5443 | 192383 | 0 | 66 | 61 | 116.738 | 15548.1
5444 | 172346 | 0 | 63 | 60 | 102.696 | 14859.2
5445 | 158963 | 0 | 60 | 59 | 91.311 | 9318.47
5446 | 147970 | 0 | 59 | 59 | 83.5859 | 9095.48
5447 | 142901 | 0 | 58 | 58 | 79.8778 | 7932.97
5448 | 141121 | 0 | 56 | 56 | 79.3158 | 7933.14
5449 | 140178 | 0 | 55 | 55 | 79.2723 | 7933.03
5450 | 139471 | 0 | 56 | 56 | 79.24 | 7933.08
5451 | 138771 | 0 | 57 | 57 | 79.2082 | 7933.09
5452 | 141889 | 0 | 58 | 58 | 82.8121 | 8789.85
5453 | 261077 | 0 | 57 | 57 | 129.927 | 10696.7
5454 | 692223 | -10262 | 56 | 56 | 253.928 | 28660.6
5455 | 785824 | -28493.6 | 57 | 57 | 282.096 | 31420.3
5456 | 821755 | -28235.7 | 58 | 58 | 302.616 | 39728.5
5457 | 973032 | -25568.2 | 64 | 61 | 314.137 | 61840.8
5458 | 1067320 | -20892.3 | 68 | 63 | 311.67 | 63223.6
5459 | 959131 | -16473.9 | 71 | 62 | 293.707 | 63225
5460 | 929188 | -16482.3 | 75 | 59 | 293.703 | 63225.8
5461 | 1080010 | -17243.2 | 77 | 60 | 318.949 | 63226.1
5462 | 1198820 | -20785.3 | 77 | 62 | 332.444 | 61844.4
5463 | 1207980 | -22162.9 | 78 | 62 | 334.209 | 56317.7
5464 | 1200110 | -21249.1 | 78 | 62 | 329.708 | 46644.6
5465 | 1114010 | -17151.4 | 78 | 62 | 305.43 | 35588.9
5466 | 788175 | -15767.9 | 76 | 62 | 216.314 | 21769.9
5467 | 194088 | 0 | 71 | 61 | 118.294 | 15551.4
5468 | 174230 | 0 | 68 | 62 | 102.996 | 14861.5
5469 | 160143 | 0 | 62 | 58 | 90.6679 | 9320.59
5470 | 149286 | 0 | 60 | 58 | 83.1347 | 9097.09
5471 | 144146 | 0 | 58 | 57 | 79.9345 | 7934.05
5472 | 142471 | 0 | 57 | 56 | 79.2582 | 7933.73
5473 | 141370 | 0 | 56 | 55 | 79.2077 | 7933.4
5474 | 140527 | 0 | 55 | 55 | 79.1692 | 7933.2
5475 | 139623 | 0 | 55 | 55 | 79.1281 | 7932.97
5476 | 142273 | 0 | 53 | 53 | 82.8299 | 8789.54
5477 | 261079 | 0 | 53 | 53 | 129.927 | 10696.4
5478 | 623343 | -10712.7 | 53 | 53 | 248.504 | 28660.3
5479 | 745925 | -29143.4 | 56 | 55 | 275.189 | 31420.2
5480 | 860544 | -27447.2 | 62 | 58 | 306.091 | 39729.4
5481 | 1042540 | -24470.1 | 68 | 62 | 320.066 | 61841.9
5482 | 1146320 | -20278.6 | 73 | 64 | 318.857 | 63225.6
5483 | 1113790 | -14404.8 | 79 | 65 | 304.11 | 63227.4
5484 | 1131870 | -28526.2 | 78 | 63 | 304.188 | 63228.1
5485 | 1198850 | -15183.1 | 81 | 63 | 326.427 | 63228.1
5486 | 1216800 | -19287.8 | 83 | 62 | 333.939 | 61846.6
5487 | 1177750 | -21674.4 | 79 | 60 | 332.809 | 56319.1
5488 | 1217950 | -20622.5 | 81 | 61 | 330.891 | 46645.7
5489 | 1108230 | -17327.3 | 79 | 61 | 305.033 | 35590.1
5490 | 798737 | -14364 | 77 | 62 | 217.707 | 21771.3
5491 | 194816 | 0 | 73 | 61 | 120.35 | 15552.6
5492 | 174567 | 0 | 69 | 60 | 105.494 | 14862.3
5493 | 161075 | 0 | 65 | 59 | 91.3443 | 9321.39
5494 | 149993 | 0 | 63 | 59 | 83.2778 | 9097.67
5495 | 144860 | 0 | 60 | 58 | 79.2027 | 7934.73
5496 | 143215 | 0 | 59 | 58 | 79.4109 | 7934.48
5497 | 142022 | 0 | 58 | 57 | 79.3564 | 7934.46
5498 | 140986 | 0 | 57 | 56 | 79.3091 | 7934.66
5499 | 140279 | 0 | 58 | 57 | 79.2767 | 7934.93
5500 | 143030 | 0 | 57 | 56 | 82.8643 | 8791.96
5501 | 242157 | 0 | 56 | 55 | 129.044 | 10699.3
5502 | 652754 | -9946.54 | 57 | 55 | 249.314 | 28663.7
5503 | 797945 | -29504.4 | 61 | 57 | 298.472 | 31423.9
5504 | 908964 | -27314.6 | 65 | 59 | 310.702 | 39731
5505 | 1027670 | -25172 | 72 | 61 | 321.642 | 61842.6
5506 | 1068640 | -20908.4 | 75 | 61 | 314.882 | 63227
5507 | 1056890 | -15668.2 | 77 | 63 | 300.297 | 63228.5
5508 | 1137800 | -30673.9 | 80 | 63 | 304.517 | 63229.1
5509 | 1229420 | -16457.7 | 82 | 63 | 328.525 | 63229
5510 | 1280060 | -20776.5 | 83 | 63 | 337.844 | 61847.4
5511 | 1325770 | -22544.3 | 83 | 63 | 341.888 | 56320.3
5512 | 1273710 | -22086.4 | 83 | 62 | 334.665 | 46646.9
5513 | 1182500 | -25138.1 | 81 | 62 | 309.121 | 35591.5
5514 | 808456 | -22859.1 | 79 | 61 | 218.124 | 21772.4
5515 | 195138 | 0 | 75 | 60 | 123.376 | 15553.7
5516 | 174915 | 0 | 69 | 59 | 104.584 | 14863
5517 | 161500 | 0 | 66 | 59 | 91.9145 | 9322.18
5518 | 150343 | 0 | 64 | 59 | 83.3326 | 9098.21
5519 | 145272 | 0 | 63 | 59 | 79.8419 | 7935.31
5520 | 143391 | 0 | 61 | 59 | 74.8914 | 7935
5521 | 142091 | 0 | 61 | 58 | 75.3443 | 7934.87
5522 | 141270 | 0 | 63 | 59 | 75.9035 | 7935.5
5523 | 140315 | 0 | 65 | 59 | 75.9442 | 7935.85
5524 | 139535 | 0 | 65 | 59 | 75.38 | 7936.19
5525 | 138822 | 0 | 63 | 59 | 74.7509 | 7936.41
5526 | 138021 | 0 | 63 | 59 | 74.3006 | 7936.51
5527 | 389753 | -9033.67 | 66 | 60 | 100.018 | 7936.55
5528 | 387916 | -7572.48 | 69 | 61 | 114.659 | 7936.63
5529 | 467786 | -11634.4 | 73 | 64 | 120.838 | 7950.84
5530 | 500930 | -12577.3 | 76 | 65 | 122.402 | 7952.53
5531 | 548175 | -12853.8 | 78 | 67 | 124.652 | 7954.31
5532 | 558326 | -12959.6 | 78 | 67 | 125.692 | 7954.75
5533 | 585837 | -13154.5 | 79 | 68 | 127.072 | 7955.42
5534 | 134108 | 0 | 77 | 68 | 73.9106 | 7956
5535 | 133796 | 0 | 69 | 68 | 70.1424 | 7956.54
5536 | 133596 | 0 | 70 | 69 | 74.9844 | 7949.69
5537 | 133303 | 0 | 70 | 69 | 78.3241 | 7946.22
5538 | 132978 | 0 | 70 | 69 | 81.3399 | 7944.41
5539 | 132664 | 0 | 69 | 69 | 81.0698 | 7943.08
5540 | 132320 | 0 | 70 | 69 | 81.0443 | 7942.18
5541 | 131911 | 0 | 69 | 68 | 79.7256 | 7941.44
5542 | 131710 | 0 | 69 | 69 | 79.1844 | 7940.9
5543 | 131332 | 0 | 69 | 68 | 78.3664 | 7940.37
5544 | 130963 | 0 | 69 | 68 | 73.8569 | 3103.45
5545 | 130678 | 0 | 69 | 68 | 73.8431 | 3103.01
5546 | 130417 | 0 | 69 | 68 | 73.8306 | 3102.72
5547 | 130066 | 0 | 69 | 67 | 73.8139 | 3102.33
5548 | 129757 | 0 | 67 | 66 | 73.1923 | 3102.07
5549 | 129530 | 0 | 67 | 66 | 73.7104 | 3101.79
5550 | 129318 | 0 | 67 | 66 | 71.1617 | 3101.54
5551 | 129002 | 0 | 68 | 65 | 68.5854 | 3101.42
5552 | 128886 | 0 | 71 | 66 | 68.5484 | 3101.27
5553 | 186840 | 0 | 71 | 67 | 74.8878 | 3101.11
5554 | 192346 | 0 | 73 | 67 | 75.9048 | 3099.65
5555 | 199209 | 0 | 76 | 68 | 76.4 | 3097.82
5556 | 204408 | 0 | 78 | 68 | 76.0884 | 3095.88
5557 | 207433 | 0 | 78 | 68 | 83.2527 | 3093.97
5558 | 211171 | 0 | 79 | 68 | 84.9809 | 3092
5559 | 206386 | 0 | 80 | 66 | 84.2445 | 3090.3
5560 | 272610 | 0 | 80 | 67 | 99.2052 | 3088.61
5561 | 261841 | 0 | 79 | 66 | 100.509 | 3086.85
5562 | 127982 | 0 | 77 | 65 | 77.47 | 3085.34
5563 | 128135 | 0 | 73 | 65 | 76.3114 | 3083.82
5564 | 128005 | 0 | 69 | 64 | 76.6052 | 3082.75
5565 | 127832 | 0 | 66 | 63 | 76.7641 | 3081.79
5566 | 127771 | 0 | 65 | 63 | 76.45 | 3081.24
5567 | 127487 | 0 | 63 | 62 | 75.3118 | 3080.95
5568 | 127609 | 0 | 62 | 61 | 78.5122 | 7917.27
5569 | 127473 | 0 | 61 | 60 | 78.4739 | 7916.88
5570 | 127392 | 0 | 60 | 60 | 78.4385 | 7915.85
5571 | 127196 | 0 | 61 | 60 | 78.972 | 7915.65
5572 | 186410 | 0 | 61 | 60 | 88.8722 | 8772.28
5573 | 264770 | 0 | 61 | 60 | 130.209 | 10678.8
5574 | 1123870 | -9320.47 | 62 | 61 | 281.805 | 28642.5
5575 | 1105080 | -29575.2 | 62 | 61 | 298.081 | 31402.1
5576 | 1047460 | -21869.5 | 64 | 61 | 298.195 | 39719.4
5577 | 1177120 | -17966.3 | 70 | 64 | 308.538 | 61833.2
5578 | 1253100 | -17008.8 | 73 | 65 | 303.893 | 63216.1
5579 | 1233370 | -11094.9 | 76 | 68 | 289.669 | 63218.8
5580 | 1338640 | -19394 | 80 | 69 | 313.087 | 63220.3
5581 | 1475320 | -11710.5 | 83 | 70 | 339.534 | 63220.5
5582 | 1599490 | -16271.8 | 86 | 71 | 354.861 | 61839.1
5583 | 1629710 | -25329.2 | 86 | 70 | 359.718 | 56312.1
5584 | 1733310 | -33244.5 | 89 | 72 | 350.58 | 46639.5
5585 | 1639550 | -31251.7 | 87 | 72 | 325.367 | 35584.6
5586 | 1180820 | -37116.3 | 84 | 71 | 229.461 | 21765.9
5587 | 190367 | 0 | 81 | 71 | 117.116 | 15547.7
5588 | 169476 | 0 | 80 | 67 | 103.982 | 14857.2
5589 | 157274 | 0 | 78 | 70 | 92.7107 | 9314.51
5590 | 146455 | 0 | 77 | 71 | 84.1742 | 9089.47
5591 | 141660 | 0 | 77 | 72 | 80.4557 | 7925.5
5592 | 140328 | 0 | 76 | 72 | 79.4825 | 7924.06
5593 | 139291 | 0 | 72 | 69 | 78.4692 | 7922.91
5594 | 138198 | 0 | 65 | 64 | 77.1214 | 7921.83
5595 | 137676 | 0 | 66 | 65 | 79.2245 | 7920.84
5596 | 141058 | 0 | 65 | 65 | 82.7027 | 8776.82
5597 | 281637 | 0 | 65 | 64 | 131.301 | 10683.4
5598 | 1240020 | -5983.7 | 65 | 64 | 277.836 | 28647.1
5599 | 1324020 | -23307.9 | 68 | 66 | 329.753 | 31406.5
5600 | 1331670 | -22729.5 | 72 | 67 | 338.793 | 39722.5
5601 | 1441170 | -22229.7 | 75 | 69 | 346.774 | 61837
5602 | 1510320 | -18487.7 | 78 | 71 | 342.281 | 63221.9
5603 | 1463980 | -13744.1 | 82 | 73 | 326.161 | 63223.3
5604 | 1544170 | -14766.6 | 82 | 74 | 331.689 | 63222.9
5605 | 1777400 | -20546.8 | 85 | 75 | 363.931 | 63223.8
5606 | 1800610 | -19869.3 | 87 | 75 | 372.345 | 61841.7
5607 | 1878680 | -34062.4 | 87 | 75 | 380.69 | 56315.2
5608 | 1933460 | -33715.1 | 88 | 76 | 383.041 | 46642.2
5609 | 1753370 | -35228.2 | 87 | 74 | 341.472 | 35587.1
5610 | 1290040 | -34791.5 | 84 | 74 | 240.171 | 21768.3
5611 | 195580 | 0 | 79 | 73 | 125.952 | 15550
5612 | 174757 | 0 | 74 | 72 | 108.207 | 14859.4
5613 | 161591 | 0 | 74 | 72 | 95.9416 | 9316.99
5614 | 150547 | 0 | 73 | 71 | 84.0008 | 9092.08
5615 | 145368 | 0 | 71 | 70 | 79.9036 | 7928.47
5616 | 143814 | 0 | 70 | 70 | 79.5763 | 7927.02
5617 | 142673 | 0 | 71 | 68 | 80.1119 | 7925.84
5618 | 141727 | 0 | 70 | 67 | 79.4749 | 7925.12
5619 | 140685 | 0 | 70 | 65 | 79.6962 | 7924.35
5620 | 143913 | 0 | 69 | 64 | 82.9996 | 8780.42
5621 | 285718 | 0 | 67 | 64 | 131.114 | 10686.5
5622 | 1202070 | -4840.67 | 66 | 63 | 301.307 | 28650
5623 | 1253850 | -26776.3 | 66 | 64 | 333.512 | 31409.3
5624 | 1177660 | -26534.9 | 67 | 64 | 327.58 | 39724.3
5625 | 1224120 | -26477.6 | 69 | 65 | 331.674 | 61837.8
5626 | 1208410 | -23293.5 | 70 | 65 | 322.482 | 63220.6
5627 | 1164970 | -18887 | 72 | 67 | 306.92 | 63221
5628 | 1182210 | -17747.3 | 72 | 67 | 307.234 | 63221.4
5629 | 1245930 | -21512.8 | 71 | 66 | 328.078 | 63222.5
5630 | 1257610 | -25486.6 | 71 | 66 | 335.706 | 61841.1
5631 | 1285430 | -26711.7 | 71 | 66 | 339.63 | 56313.8
5632 | 1278520 | -25900.7 | 71 | 66 | 334.174 | 46640.2
5633 | 1170880 | -22057.8 | 71 | 66 | 307.517 | 35584.9
5634 | 789305 | -16736.1 | 70 | 65 | 217.4 | 21766
5635 | 194379 | 0 | 69 | 64 | 123.228 | 15548
5636 | 174334 | 0 | 68 | 63 | 103.585 | 14859.1
5637 | 160787 | 0 | 64 | 61 | 91.2877 | 9318.06
5638 | 149724 | 0 | 63 | 61 | 83.5253 | 9094.77
5639 | 144580 | 0 | 62 | 60 | 79.7722 | 7931.9
5640 | 142899 | 0 | 60 | 59 | 78.7679 | 7931.73
5641 | 141682 | 0 | 58 | 57 | 79.2219 | 7931.43
5642 | 140804 | 0 | 56 | 56 | 79.1818 | 7931.6
5643 | 139867 | 0 | 55 | 55 | 79.1392 | 7931.4
5644 | 142829 | 0 | 55 | 55 | 82.855 | 8788.52
5645 | 252173 | 0 | 53 | 53 | 129.511 | 10695.4
5646 | 653587 | -9900.27 | 54 | 54 | 249.601 | 28659.6
5647 | 869403 | -29186.3 | 60 | 58 | 282.911 | 31419.5
5648 | 940174 | -27820.8 | 63 | 60 | 311.883 | 39728.2
5649 | 934243 | -27190.9 | 63 | 60 | 310.641 | 61840.4
5650 | 998981 | -23945.9 | 66 | 62 | 306.908 | 63222.9
5651 | 905893 | -19829 | 66 | 62 | 287.169 | 63223.3
5652 | 950160 | -18331.5 | 67 | 63 | 289.823 | 63223.8
5653 | 1152610 | -20785.1 | 72 | 64 | 322.583 | 63224.5
5654 | 1247630 | -23473.8 | 75 | 65 | 335.154 | 61842.9
5655 | 1260140 | -24646.1 | 74 | 64 | 335.053 | 56316.4
5656 | 1272580 | -22860.3 | 78 | 65 | 332.984 | 46642.9
5657 | 1130970 | -19184.1 | 76 | 63 | 305.693 | 35587.8
5658 | 787200 | -13735.7 | 74 | 63 | 215.834 | 21768.7
5659 | 194252 | 0 | 70 | 62 | 118.563 | 15550.3
5660 | 174147 | 0 | 66 | 61 | 102.647 | 14860.9
5661 | 160606 | 0 | 64 | 60 | 91.8029 | 9320.05
5662 | 149409 | 0 | 63 | 59 | 83.5108 | 9096.69
5663 | 144479 | 0 | 63 | 59 | 80.0651 | 7934.02
5664 | 142645 | 0 | 61 | 57 | 78.9097 | 7933.92
5665 | 141939 | 0 | 60 | 58 | 79.0971 | 7933.96
5666 | 140690 | 0 | 58 | 56 | 79.2958 | 7934.08
5667 | 139832 | 0 | 56 | 55 | 79.2565 | 7934.25
5668 | 142680 | 0 | 54 | 54 | 82.8483 | 8791.22
5669 | 236304 | 0 | 55 | 54 | 128.772 | 10698.5
5670 | 642135 | -10369.6 | 56 | 55 | 250.884 | 28663.1
5671 | 781902 | -30866.4 | 58 | 57 | 281.893 | 31423.5
5672 | 861100 | -28606.8 | 62 | 59 | 306.501 | 39730.4
5673 | 942986 | -28178.8 | 64 | 61 | 311.685 | 61842.1
5674 | 988315 | -23818 | 67 | 62 | 307.448 | 63224.7
5675 | 967510 | -18864.5 | 70 | 64 | 293.701 | 63225.1
5676 | 1163000 | -26373.8 | 75 | 66 | 307.647 | 63225.4
5677 | 1307350 | -18550.5 | 77 | 68 | 333.422 | 63226
5678 | 1277720 | -22790.1 | 75 | 67 | 337.54 | 61845.5
5679 | 1310050 | -24099 | 76 | 67 | 341.026 | 56317.5
5680 | 1380550 | -23211.4 | 76 | 68 | 339.946 | 46643.6
5681 | 1263380 | -19182.6 | 76 | 68 | 313.968 | 35588
5682 | 857337 | -14215 | 74 | 67 | 220.283 | 21769.4
5683 | 194735 | 0 | 73 | 67 | 124.946 | 15550.9
5684 | 174439 | 0 | 72 | 67 | 107.403 | 14861.8
5685 | 161008 | 0 | 72 | 66 | 95.7885 | 9320.91
5686 | 149980 | 0 | 71 | 66 | 85.9392 | 9097.41
5687 | 144753 | 0 | 72 | 65 | 83.128 | 7934.33
5688 | 143247 | 0 | 71 | 65 | 77.3354 | 7933.68
5689 | 142227 | 0 | 70 | 65 | 77.1446 | 7933.08
5690 | 141164 | 0 | 69 | 64 | 76.9571 | 7933.12
5691 | 140521 | 0 | 68 | 64 | 76.8088 | 7932.83
5692 | 139540 | 0 | 67 | 63 | 76.6395 | 7932.61
5693 | 138950 | 0 | 67 | 63 | 77.0382 | 7932.43
5694 | 138102 | 0 | 67 | 62 | 72.8003 | 7932.29
5695 | 509958 | -4301.83 | 69 | 64 | 106.223 | 7932.24
5696 | 457349 | -6084.09 | 70 | 64 | 118.359 | 7932.09
5697 | 455337 | -10876.6 | 70 | 65 | 118.839 | 7948.46
5698 | 474014 | -12375.1 | 70 | 66 | 119.402 | 7950.43
5699 | 412984 | -13423.6 | 65 | 65 | 114.323 | 7952.21
5700 | 465460 | -14143.3 | 68 | 67 | 119.74 | 7953.29
5701 | 557446 | -14538.8 | 73 | 70 | 126.682 | 7954.12
5702 | 134007 | 0 | 73 | 70 | 73.6305 | 7954.99
5703 | 133656 | 0 | 73 | 70 | 72.9792 | 7955.69
5704 | 133451 | 0 | 76 | 71 | 75.13 | 7949.19
5705 | 133170 | 0 | 77 | 71 | 77.3476 | 7945.97
5706 | 132910 | 0 | 76 | 71 | 79.6852 | 7943.6
5707 | 132572 | 0 | 73 | 70 | 80.4467 | 7941.56
5708 | 132246 | 0 | 70 | 69 | 79.242 | 7940.03
5709 | 132035 | 0 | 70 | 69 | 80.0407 | 7938.92
5710 | 131707 | 0 | 68 | 68 | 78.6116 | 7938.09
5711 | 131328 | 0 | 67 | 67 | 78.0224 | 7937.63
5712 | 131084 | 0 | 68 | 68 | 74.0903 | 3100.75
5713 | 130809 | 0 | 68 | 68 | 73.8098 | 3100.29
5714 | 130441 | 0 | 67 | 67 | 73.4887 | 3100.04
5715 | 130080 | 0 | 66 | 66 | 73.4353 | 3099.83
5716 | 130003 | 0 | 68 | 68 | 74.3066 | 3099.41
5717 | 129661 | 0 | 67 | 67 | 73.4519 | 3099.06
5718 | 129307 | 0 | 66 | 66 | 70.9318 | 3098.73
5719 | 129115 | 0 | 66 | 66 | 68.5345 | 3098.33
5720 | 185873 | 0 | 67 | 66 | 74.534 | 3098.05
5721 | 128820 | 0 | 71 | 68 | 69.214 | 3097.97
5722 | 195287 | 0 | 73 | 69 | 76.003 | 3097.61
5723 | 208224 | 0 | 78 | 71 | 85.5627 | 3096.35
5724 | 214687 | 0 | 81 | 72 | 85.5509 | 3094.04
5725 | 226416 | 0 | 82 | 70 | 87.3743 | 3092.43
5726 | 211117 | 0 | 83 | 69 | 84.8773 | 3090.07
5727 | 283322 | 0 | 85 | 69 | 100.002 | 3088.07
5728 | 285314 | 0 | 84 | 70 | 101.856 | 3085.78
5729 | 278682 | 0 | 82 | 70 | 103.401 | 3084.34
5730 | 128664 | 0 | 78 | 72 | 76.1934 | 3082.18
5731 | 128525 | 0 | 75 | 70 | 77.4573 | 3080.54
5732 | 128584 | 0 | 73 | 70 | 77.313 | 3079.17
5733 | 128550 | 0 | 72 | 70 | 77.5463 | 3078.13
5734 | 128384 | 0 | 72 | 69 | 77.0119 | 3077.45
5735 | 128309 | 0 | 71 | 69 | 75.8956 | 3076.9
5736 | 128429 | 0 | 72 | 68 | 79.4589 | 7912.61
5737 | 128285 | 0 | 72 | 67 | 79.1778 | 7912.2
5738 | 128092 | 0 | 71 | 66 | 78.8559 | 7910.86
5739 | 193726 | 0 | 71 | 66 | 86.3152 | 7910.01
5740 | 131894 | 0 | 67 | 66 | 81.6078 | 8765.84
5741 | 277427 | 0 | 66 | 65 | 130.892 | 10672
5742 | 1424370 | -6278.02 | 66 | 66 | 296.158 | 28635.5
5743 | 1407850 | -32017.5 | 67 | 66 | 324.189 | 31394.8
5744 | 1315250 | -23397.9 | 68 | 67 | 313.44 | 39717
5745 | 1331320 | -19283.4 | 70 | 68 | 315.396 | 61830.9
5746 | 1348190 | -17340.4 | 70 | 69 | 305.575 | 63213.8
5747 | 1199770 | -14051.6 | 71 | 68 | 301.459 | 63214.6
5748 | 1371310 | -15404.7 | 74 | 71 | 317.016 | 63215.2
5749 | 1666180 | -14387.7 | 81 | 74 | 353.751 | 63216.7
5750 | 1720590 | -17674.3 | 82 | 75 | 363.171 | 61835.8
5751 | 1821760 | -21830.1 | 85 | 75 | 370.517 | 56309.8
5752 | 1799290 | -17683.5 | 82 | 76 | 366.201 | 46636.7
5753 | 1686570 | -22625.4 | 82 | 75 | 339.215 | 35582.3
5754 | 1163030 | -11689.7 | 79 | 74 | 237.323 | 21763.2
5755 | 190945 | 0 | 77 | 73 | 123.997 | 15545.2
5756 | 170303 | 0 | 75 | 72 | 104.023 | 14854.7
5757 | 157314 | 0 | 74 | 72 | 92.3785 | 9312.46
5758 | 146611 | 0 | 73 | 72 | 83.8057 | 9087.94
5759 | 141610 | 0 | 72 | 71 | 80.0372 | 7924.29
5760 | 140255 | 0 | 71 | 71 | 79.0214 | 7923.2
5761 | 139389 | 0 | 70 | 70 | 78.937 | 7922.11
5762 | 138815 | 0 | 72 | 71 | 79.8206 | 7921.24
5763 | 138208 | 0 | 73 | 71 | 79.5611 | 7920.34
5764 | 141791 | 0 | 72 | 70 | 83.0257 | 8776.2
5765 | 292230 | 0 | 70 | 69 | 131.709 | 10682.5
5766 | 1437820 | -4762.97 | 70 | 68 | 294.226 | 28645.7
5767 | 1428190 | -22693.1 | 70 | 68 | 338.816 | 31404.9
5768 | 1351280 | -22149.1 | 73 | 67 | 340.711 | 39721.3
5769 | 1300950 | -22951.5 | 74 | 65 | 337.953 | 61835.1
5770 | 1233030 | -19705 | 75 | 63 | 325.839 | 63220.1
5771 | 1185080 | -18398.7 | 77 | 64 | 308.998 | 63221.6
5772 | 1228720 | -36547 | 78 | 63 | 311.182 | 63222.1
5773 | 1252020 | -20743.2 | 78 | 62 | 330.357 | 63222.8
5774 | 1323610 | -20980.4 | 79 | 63 | 341.411 | 61841.8
5775 | 1355990 | -24560.8 | 79 | 63 | 344.43 | 56314.9
5776 | 1296780 | -22030.5 | 79 | 62 | 336.661 | 46641.8
5777 | 1192210 | -22955.4 | 77 | 62 | 310.354 | 35586.6
5778 | 773872 | -16850.3 | 75 | 60 | 216.654 | 21767.7
5779 | 193890 | 0 | 69 | 60 | 119.199 | 15549
5780 | 173379 | 0 | 68 | 59 | 106.805 | 14858.5
5781 | 159987 | 0 | 67 | 58 | 92.6857 | 9317.15
5782 | 149171 | 0 | 62 | 58 | 82.431 | 9093.3
5783 | 144197 | 0 | 62 | 59 | 80.0129 | 7930.28
5784 | 142400 | 0 | 60 | 58 | 78.8644 | 7929.85
5785 | 141130 | 0 | 60 | 56 | 79.3158 | 7929.68
5786 | 140632 | 0 | 58 | 57 | 79.2926 | 7929.2
5787 | 139471 | 0 | 58 | 56 | 79.2403 | 7928.96
5788 | 142416 | 0 | 56 | 55 | 82.8363 | 8785.86
5789 | 251375 | 0 | 56 | 55 | 129.474 | 10692.6
5790 | 693730 | -9053.95 | 55 | 54 | 272.231 | 28656.5
5791 | 852817 | -29803.1 | 59 | 57 | 300.243 | 31416.8
5792 | 957110 | -26971.6 | 64 | 60 | 313.556 | 39726.7
5793 | 1011690 | -26582.1 | 66 | 60 | 316.254 | 61839.3
5794 | 1080540 | -21459.4 | 71 | 62 | 315.064 | 63221.9
5795 | 938120 | -17264.4 | 73 | 60 | 293.588 | 63224.6
5796 | 1062940 | -20966 | 75 | 62 | 301.578 | 63224.5
5797 | 1222540 | -18370.7 | 77 | 64 | 328.501 | 63224.9
5798 | 1261490 | -22178.3 | 77 | 64 | 337.295 | 61843.6
5799 | 1079660 | -24521.1 | 71 | 59 | 324.678 | 56316.5
5800 | 1078080 | -24961.1 | 67 | 59 | 318.312 | 46643.3
5801 | 1066940 | -21063.9 | 70 | 62 | 301.431 | 35587.2
5802 | 728546 | -16137.3 | 69 | 62 | 210.873 | 21768.4
5803 | 193944 | 0 | 66 | 61 | 120.806 | 15549.8
5804 | 173750 | 0 | 64 | 60 | 106.269 | 14860.7
5805 | 160389 | 0 | 63 | 60 | 94.4566 | 9320.2
5806 | 149110 | 0 | 62 | 59 | 85.3102 | 9097.17
5807 | 144315 | 0 | 63 | 60 | 82.4482 | 7934.58
5808 | 142533 | 0 | 62 | 59 | 80.7155 | 7934.56
5809 | 141638 | 0 | 61 | 59 | 80.563 | 7934.61
5810 | 140696 | 0 | 62 | 59 | 81.4506 | 7934.68
5811 | 139910 | 0 | 62 | 59 | 80.9452 | 7934.71
5812 | 143149 | 0 | 63 | 60 | 85.3275 | 8791.52
5813 | 251434 | 0 | 63 | 61 | 137.689 | 10698.5
5814 | 997262 | -8126.43 | 67 | 64 | 275.095 | 28662.6
5815 | 1117110 | -25064.8 | 69 | 65 | 321.17 | 31422.5
5816 | 1185490 | -24338.9 | 71 | 67 | 330.211 | 39729.7
5817 | 1240660 | -24445.9 | 72 | 68 | 334.145 | 61841.6
5818 | 1340000 | -20874.3 | 75 | 70 | 333.715 | 63224.2
5819 | 1227070 | -17191 | 74 | 71 | 311.09 | 63224.5
5820 | 1246300 | -16572.5 | 72 | 71 | 310.04 | 63224.7
5821 | 1422340 | -20781.6 | 73 | 72 | 340.096 | 63225.3
5822 | 1528790 | -23869.1 | 77 | 73 | 355.117 | 61843.6
5823 | 1605780 | -24763.2 | 80 | 72 | 360.252 | 56316.1
5824 | 1618800 | -23332.7 | 80 | 72 | 356.663 | 46643.2
5825 | 1421980 | -19117.2 | 79 | 71 | 325.194 | 35588.6
5826 | 992928 | -13737.1 | 77 | 71 | 229.743 | 21769.8
5827 | 195547 | 0 | 72 | 70 | 124.434 | 15551.1
5828 | 174840 | 0 | 71 | 69 | 107.027 | 14861.4
5829 | 161137 | 0 | 66 | 65 | 91.1189 | 9320.32
5830 | 149929 | 0 | 66 | 64 | 83.923 | 9096.71
5831 | 144899 | 0 | 66 | 64 | 80.2075 | 7933.72
5832 | 143347 | 0 | 65 | 64 | 79.3485 | 7933.39
5833 | 142109 | 0 | 65 | 63 | 79.5533 | 7894.73
5834 | 141298 | 0 | 64 | 62 | 79.2139 | 7894.54
5835 | 140436 | 0 | 63 | 61 | 79.1366 | 7894.37
5836 | 143447 | 0 | 61 | 60 | 82.4077 | 8746.18
5837 | 254641 | 0 | 59 | 58 | 129.36 | 10642.4
5838 | 732065 | -8792.86 | 56 | 56 | 274.008 | 28506.4
5839 | 795697 | -30844.4 | 58 | 56 | 277.326 | 31251.1
5840 | 886273 | -29292.1 | 62 | 58 | 307.8 | 39513.7
5841 | 955284 | -28401.5 | 65 | 59 | 312.746 | 61503
5842 | 982024 | -24525.9 | 67 | 59 | 306.657 | 62879.2
5843 | 913332 | -19527.9 | 69 | 59 | 290.302 | 62880.6
5844 | 950808 | -32453.8 | 71 | 58 | 292.343 | 62881.3
5845 | 986681 | -20758.3 | 71 | 58 | 311.753 | 62881.3
5846 | 1018340 | -24182.4 | 72 | 58 | 320.923 | 61507.9
5847 | 1053110 | -25658.8 | 72 | 58 | 323.807 | 56010.9
5848 | 1011440 | -25228.1 | 70 | 58 | 316.189 | 46391.1
5849 | 850709 | -22544.4 | 67 | 57 | 287.173 | 35397.2
5850 | 567903 | -18782.1 | 65 | 57 | 205.15 | 21654.7
5851 | 193888 | 0 | 64 | 57 | 122.395 | 15470.7
5852 | 173942 | 0 | 62 | 57 | 105.056 | 14785.5
5853 | 160406 | 0 | 61 | 57 | 91.9296 | 9276.33
5854 | 149232 | 0 | 60 | 57 | 83.3877 | 9054.94
5855 | 144191 | 0 | 60 | 57 | 79.9365 | 7899.05
5856 | 142354 | 0 | 59 | 57 | 75.3196 | 7899.24
5857 | 141103 | 0 | 59 | 56 | 75.2622 | 7899.39
5858 | 140273 | 0 | 58 | 56 | 75.2242 | 7900.17
5859 | 139378 | 0 | 58 | 56 | 75.1836 | 7900.58
5860 | 138487 | 0 | 56 | 55 | 75.1431 | 7900.86
5861 | 137593 | 0 | 55 | 54 | 75.1025 | 7901.39
5862 | 136833 | 0 | 53 | 53 | 72.5655 | 7901.95
5863 | 217221 | -22567.8 | 56 | 54 | 90.3852 | 7902.67
5864 | 233932 | -24475.3 | 60 | 55 | 90.2489 | 7903.31
5865 | 255802 | -21415.9 | 63 | 56 | 91.5397 | 7915.01
5866 | 276724 | -17667.6 | 65 | 56 | 101.805 | 7916.48
5867 | 339291 | -24439.5 | 68 | 57 | 112.433 | 7917.69
5868 | 361224 | -23726.6 | 70 | 56 | 113.729 | 7918.26
5869 | 366750 | -24579.3 | 69 | 56 | 113.227 | 7918.87
5870 | 181292 | 0 | 67 | 55 | 79.8733 | 7919.38
5871 | 177626 | 0 | 66 | 54 | 79.613 | 7919.95
5872 | 131986 | 0 | 65 | 55 | 72.2576 | 7914.37
5873 | 131591 | 0 | 64 | 55 | 75.5786 | 7911.43
5874 | 131340 | 0 | 63 | 55 | 77.9188 | 7909.74
5875 | 131098 | 0 | 60 | 55 | 79.476 | 7908.54
5876 | 130638 | 0 | 57 | 54 | 79.6024 | 7908.01
5877 | 130151 | 0 | 54 | 52 | 79.5804 | 7907.73
5878 | 129908 | 0 | 53 | 52 | 78.7692 | 7907.66
5879 | 129437 | 0 | 52 | 51 | 77.9481 | 7907.72
5880 | 128965 | 0 | 51 | 50 | 73.4348 | 3098.36
5881 | 128555 | 0 | 50 | 49 | 73.4162 | 3098.56
5882 | 128203 | 0 | 48 | 48 | 73.4002 | 3099.48
5883 | 127752 | 0 | 47 | 47 | 73.3799 | 3100.41
5884 | 127380 | 0 | 46 | 46 | 73.363 | 3101.56
5885 | 127118 | -7746.28 | 46 | 46 | 80.0717 | 3102.78
5886 | 126666 | 0 | 45 | 45 | 70.8973 | 3104.11
5887 | 132775 | -1438.7 | 50 | 49 | 72.8278 | 3105.46
5888 | 126609 | 0 | 54 | 53 | 67.2134 | 3106.76
5889 | 126436 | 0 | 59 | 56 | 67.5588 | 3107.81
5890 | 126225 | 0 | 62 | 57 | 68.1303 | 3107.97
5891 | 125982 | 0 | 65 | 57 | 70.0613 | 3107.75
5892 | 149568 | 0 | 68 | 57 | 77.6045 | 3106.21
5893 | 164743 | 0 | 67 | 56 | 76.7777 | 3105.45
5894 | 162926 | 0 | 67 | 55 | 77.185 | 3104.46
5895 | 125704 | 0 | 66 | 54 | 69.5955 | 3103.29
5896 | 126019 | 0 | 65 | 55 | 70.8178 | 3102.25
5897 | 126020 | 0 | 64 | 56 | 74.3973 | 3101.63
5898 | 125912 | 0 | 63 | 56 | 76.1811 | 3101.07
5899 | 125886 | 0 | 61 | 56 | 76.6076 | 3100.69
5900 | 125736 | 0 | 58 | 55 | 76.9931 | 3100.42
5901 | 125668 | 0 | 56 | 55 | 77.2434 | 3100.34
5902 | 125402 | 0 | 55 | 54 | 76.4315 | 3100.4
5903 | 125236 | 0 | 53 | 53 | 75.6239 | 3100.59
5904 | 125002 | 0 | 52 | 52 | 73.2554 | 3100.81
5905 | 124904 | 0 | 52 | 52 | 73.2509 | 3101.05
5906 | 124661 | 0 | 51 | 51 | 73.2401 | 3101.64
5907 | 124563 | 0 | 51 | 51 | 73.2355 | 3102.41
5908 | 124405 | 0 | 51 | 51 | 73.2285 | 3103.28
5909 | 138237 | -3210.54 | 50 | 50 | 78.273 | 3104.1
5910 | 123990 | 0 | 50 | 50 | 70.7468 | 3104.87
5911 | 124030 | 0 | 53 | 52 | 67.8815 | 3105.45
5912 | 133533 | -4144.09 | 57 | 53 | 73.9229 | 3106.4
5913 | 123973 | 0 | 60 | 55 | 67.4561 | 3107.13
5914 | 123947 | 0 | 62 | 56 | 68.0255 | 3107.18
5915 | 124107 | 0 | 65 | 58 | 69.9136 | 3106.62
5916 | 151677 | -1531.55 | 67 | 59 | 77.5094 | 3105.92
5917 | 169619 | -1031.96 | 67 | 60 | 78.25 | 3104.74
5918 | 124137 | 0 | 68 | 60 | 70.273 | 3103.51
5919 | 168126 | -144.525 | 68 | 61 | 78.0902 | 3102.35
5920 | 124372 | 0 | 68 | 61 | 70.8917 | 3101.24
5921 | 124495 | 0 | 67 | 61 | 73.8312 | 3100.48
5922 | 124530 | 0 | 67 | 61 | 75.1467 | 3099.65
5923 | 124517 | 0 | 64 | 60 | 76.2626 | 3098.94
5924 | 124454 | 0 | 62 | 59 | 76.7421 | 3098.56
5925 | 124444 | 0 | 59 | 58 | 76.6822 | 3098.37
5926 | 124570 | 0 | 59 | 59 | 76.3936 | 3098.4
5927 | 124481 | 0 | 59 | 59 | 75.5898 | 3098.62
5928 | 124621 | 0 | 59 | 58 | 78.1417 | 7908.5
5929 | 124797 | 0 | 59 | 59 | 78.1496 | 7908.9
5930 | 124691 | 0 | 59 | 59 | 78.1451 | 7908.48
5931 | 124643 | 0 | 59 | 59 | 78.1428 | 7908.5
5932 | 149278 | -2273.01 | 59 | 59 | 87.5612 | 8760.49
5933 | 229973 | -2212.55 | 59 | 59 | 128.902 | 10656.9
5934 | 631910 | -24575.7 | 59 | 59 | 260.025 | 28521.1
5935 | 756829 | -18195.1 | 60 | 60 | 292.05 | 31265.8
5936 | 761119 | -16215.3 | 60 | 60 | 287.095 | 39521.6
5937 | 793009 | -14557.1 | 61 | 60 | 286.771 | 61509.4
5938 | 833294 | -12981.1 | 63 | 61 | 281.244 | 62884
5939 | 791322 | -9843.79 | 64 | 62 | 263.125 | 62884
5940 | 840803 | -9079.24 | 66 | 63 | 265.752 | 62884.3
5941 | 1032770 | -9197.8 | 70 | 65 | 297.343 | 62884.7
5942 | 1182250 | -12788.9 | 73 | 67 | 314.852 | 61510.5
5943 | 1325290 | -13183.9 | 77 | 69 | 326.841 | 56013
5944 | 1325650 | -12783.4 | 75 | 68 | 320.456 | 46393.5
5945 | 1162050 | -10157.8 | 72 | 67 | 286.847 | 35399.7
5946 | 775119 | -7221.37 | 70 | 67 | 190.8 | 21657.8
5947 | 187382 | 0 | 67 | 65 | 117.004 | 15473.7
5948 | 167364 | 0 | 64 | 63 | 102.506 | 14788.3
5949 | 154105 | 0 | 61 | 61 | 91.1259 | 9279.49
5950 | 143621 | 0 | 62 | 62 | 83.7221 | 9057.81
5951 | 138917 | 0 | 64 | 63 | 80.3697 | 7901.7
5952 | 137646 | 0 | 65 | 64 | 79.6073 | 7901.55
5953 | 136652 | 0 | 65 | 63 | 79.2975 | 7901.25
5954 | 136196 | 0 | 64 | 63 | 78.9767 | 7901.26
5955 | 135374 | 0 | 64 | 62 | 79.1995 | 7901.11
5956 | 138799 | 0 | 64 | 61 | 82.8205 | 8752.94
5957 | 250813 | 0 | 64 | 61 | 129.727 | 10649.2
5958 | 795987 | -9442.57 | 64 | 60 | 264.311 | 28513.1
5959 | 882190 | -15951.8 | 64 | 60 | 294.733 | 31257.5
5960 | 886376 | -17789.8 | 65 | 60 | 310.926 | 39517.6
5961 | 903638 | -18731.2 | 65 | 60 | 309.861 | 61506.2
5962 | 970337 | -15851.9 | 68 | 62 | 307.118 | 62880.9
5963 | 944208 | -12312.5 | 70 | 64 | 292.264 | 62881.2
5964 | 1037160 | -10495.6 | 73 | 66 | 299.213 | 62881.5
5965 | 1218710 | -13420.1 | 75 | 67 | 328.976 | 62882
5966 | 1279200 | -16232.5 | 76 | 67 | 338.731 | 61507.9
5967 | 1400630 | -17427 | 78 | 68 | 347.195 | 56011.2
5968 | 1331870 | -16678.4 | 77 | 67 | 338.73 | 46391.6
5969 | 1205500 | -13524.5 | 75 | 67 | 311.333 | 35398.5
5970 | 804933 | -9647.75 | 74 | 66 | 223.34 | 21656.2
5971 | 192819 | 0 | 73 | 67 | 125.278 | 15472.1
5972 | 172461 | 0 | 72 | 67 | 107.021 | 14786.5
5973 | 159268 | 0 | 71 | 68 | 92.3255 | 9276.76
5974 | 148178 | 0 | 71 | 67 | 84.0658 | 9054.57
5975 | 143237 | 0 | 70 | 67 | 80.0296 | 7898.02
5976 | 141723 | 0 | 70 | 67 | 79.6278 | 7897.47
5977 | 140784 | 0 | 68 | 66 | 78.9605 | 7896.96
5978 | 139908 | 0 | 67 | 65 | 79.1459 | 7896.5
5979 | 139089 | 0 | 65 | 64 | 78.7679 | 7896.03
5980 | 142003 | 0 | 63 | 62 | 82.4121 | 8747.6
5981 | 262066 | 0 | 61 | 60 | 129.507 | 10643.6
5982 | 801994 | -7801.17 | 59 | 58 | 278.178 | 28507.5
5983 | 938653 | -22734 | 61 | 60 | 306.551 | 31251.9
5984 | 966576 | -22516.9 | 62 | 61 | 312.612 | 39514.6
5985 | 974891 | -23054.8 | 64 | 61 | 313.917 | 61504.2
5986 | 1050010 | -19858.6 | 66 | 63 | 310.387 | 62879
5987 | 1031070 | -15501.5 | 69 | 64 | 296.674 | 62879.2
5988 | 1136400 | -32552.2 | 71 | 64 | 302.523 | 62879.6
5989 | 1203180 | -16096.6 | 71 | 65 | 324.215 | 62881.4
5990 | 1241000 | -19705.4 | 72 | 65 | 333.593 | 61508.2
5991 | 1256660 | -21413.8 | 72 | 65 | 335.479 | 56011.5
5992 | 1219530 | -21220.1 | 70 | 64 | 327.409 | 46392
5993 | 1059190 | -18304.4 | 68 | 64 | 298.407 | 35397.8
5994 | 694839 | -14810.6 | 66 | 63 | 208.806 | 21655.7
5995 | 193257 | 0 | 65 | 62 | 123.305 | 15471.2
5996 | 173363 | 0 | 63 | 61 | 106.015 | 14785.9
5997 | 159619 | 0 | 62 | 59 | 94.234 | 9276.73
5998 | 148652 | 0 | 61 | 59 | 85.1542 | 9055.19
5999 | 143524 | 0 | 60 | 58 | 81.1989 | 7899.25
6000 | 141860 | 0 | 59 | 57 | 81.0132 | 7899.38
6001 | 140706 | 0 | 57 | 55 | 80.9253 | 7899.55
6002 | 139830 | 0 | 56 | 54 | 80.8589 | 7899.8
6003 | 138979 | 0 | 54 | 53 | 80.795 | 7900.07
6004 | 141787 | 0 | 53 | 52 | 84.4672 | 8752.47
6005 | 223117 | 0 | 51 | 51 | 133.46 | 10649.3
6006 | 407130 | -15606.6 | 50 | 49 | 239.323 | 28514
6007 | 556131 | -38085.8 | 53 | 51 | 284.715 | 31259.2
6008 | 654458 | -33049 | 57 | 53 | 293.659 | 39518
6009 | 736582 | -27919.6 | 60 | 54 | 297.907 | 61506.4
6010 | 792223 | -22365.6 | 63 | 55 | 294.794 | 62882
6011 | 788208 | -21107.6 | 65 | 56 | 281.668 | 62883.2
6012 | 861906 | -39789.1 | 68 | 56 | 286.278 | 62883.5
6013 | 945572 | -21519.8 | 69 | 57 | 308.771 | 62884
6014 | 994087 | -20168.6 | 69 | 57 | 317.684 | 61510.3
6015 | 1061230 | -22757 | 70 | 58 | 323.535 | 56013.8
6016 | 1001890 | -21551.4 | 69 | 57 | 314.865 | 46394.3
6017 | 874615 | -18826.7 | 67 | 57 | 287.428 | 35400.4
6018 | 552438 | -14747 | 66 | 56 | 200.89 | 21657.9
6019 | 193086 | 0 | 61 | 55 | 119.691 | 15473.3
6020 | 172899 | 0 | 57 | 53 | 106.193 | 14787.7
6021 | 159418 | 0 | 52 | 51 | 94.518 | 9279.25
6022 | 147998 | 0 | 50 | 49 | 83.6046 | 9058.03
6023 | 143134 | 0 | 48 | 48 | 79.8999 | 7902.54
6024 | 140996 | 0 | 46 | 46 | 75.2673 | 7903.11
6025 | 140052 | 0 | 46 | 46 | 75.2225 | 7903.46
6026 | 138979 | 0 | 45 | 45 | 75.1727 | 7904.55
6027 | 138096 | 0 | 45 | 45 | 75.1316 | 7905.31
6028 | 137201 | 0 | 45 | 45 | 75.0901 | 7906.03
6029 | 136360 | 0 | 45 | 45 | 75.051 | 7906.75
6030 | 135556 | 0 | 45 | 45 | 74.3911 | 7907.43
6031 | 184371 | -28719.6 | 48 | 47 | 85.5842 | 7908.09
6032 | 230080 | -78971.6 | 50 | 50 | 87.6587 | 7908.58
6033 | 272212 | -96142.1 | 53 | 52 | 102.594 | 7918.23
6034 | 273841 | -51680.4 | 59 | 55 | 90.1156 | 7919.52
6035 | 328667 | -35542.8 | 65 | 58 | 113.284 | 7920.41
6036 | 409337 | -40488 | 71 | 60 | 117.818 | 7920.78
6037 | 452327 | -38197 | 72 | 61 | 119.171 | 7921.14
6038 | 186305 | 0 | 73 | 62 | 84.226 | 7921.64
6039 | 186109 | 0 | 74 | 62 | 83.9009 | 7922.06
6040 | 188599 | 0 | 72 | 62 | 82.4762 | 7916.86
6041 | 130904 | 0 | 70 | 61 | 75.7447 | 7913.62
6042 | 130696 | 0 | 68 | 60 | 78.1488 | 7911.56
6043 | 130485 | 0 | 65 | 59 | 80.2835 | 7909.95
6044 | 130186 | 0 | 63 | 58 | 80.0361 | 7909.16
6045 | 129890 | 0 | 60 | 57 | 78.8089 | 7908.7
6046 | 129597 | 0 | 61 | 57 | 79.0447 | 7908.63
6047 | 129353 | 0 | 61 | 57 | 77.9777 | 7908.7
6048 | 128967 | 0 | 62 | 57 | 73.7599 | 3099.41
6049 | 128707 | 0 | 62 | 57 | 73.4906 | 3099.62
6050 | 128308 | 0 | 61 | 56 | 73.1833 | 3099.99
6051 | 127974 | 0 | 61 | 55 | 73.4231 | 3100.23
6052 | 127877 | 0 | 60 | 55 | 73.1317 | 3100.48
6053 | 127464 | 0 | 60 | 54 | 73.3669 | 3100.78
6054 | 127375 | 0 | 59 | 54 | 70.9324 | 3101.11
6055 | 127151 | 0 | 59 | 54 | 68.4453 | 3101.51
6056 | 127030 | 0 | 60 | 55 | 67.4286 | 3101.96
6057 | 126784 | 0 | 60 | 55 | 67.9005 | 3102.43
6058 | 126677 | 0 | 62 | 56 | 68.5837 | 3102.67
6059 | 126741 | 0 | 64 | 58 | 68.6545 | 3102.5
6060 | 126562 | 0 | 66 | 59 | 68.5546 | 3102.31
6061 | 126591 | 0 | 66 | 60 | 68.068 | 3102.06
6062 | 126414 | 0 | 65 | 60 | 68.829 | 3101.73
6063 | 126445 | 0 | 65 | 61 | 69.4925 | 3101.1
6064 | 126159 | 0 | 65 | 60 | 69.4932 | 3100.54
6065 | 126170 | 0 | 64 | 60 | 73.0315 | 3099.97
6066 | 126070 | 0 | 64 | 60 | 76.4305 | 3099.6
6067 | 125893 | 0 | 63 | 59 | 77.044 | 3099.31
6068 | 162189 | 0 | 63 | 59 | 83.0186 | 3099.24
6069 | 125753 | 0 | 62 | 59 | 77.0846 | 3099.31
6070 | 125675 | 0 | 61 | 59 | 76.2216 | 3099.49
6071 | 125714 | 0 | 61 | 60 | 75.678 | 3099.79
6072 | 125755 | 0 | 60 | 59 | 78.3646 | 7909.49
6073 | 125904 | 0 | 60 | 60 | 78.6246 | 7909.77
6074 | 125741 | 0 | 60 | 60 | 78.6175 | 7909.23
6075 | 149831 | 0 | 60 | 60 | 83.7035 | 7909.15
6076 | 129324 | 0 | 60 | 60 | 82.2599 | 8761.08
6077 | 227603 | 0 | 60 | 60 | 128.358 | 10657.5
6078 | 656229 | -13692.9 | 60 | 60 | 258.369 | 28521.6
6079 | 784933 | -16233.9 | 61 | 61 | 289.235 | 31266.1
6080 | 832922 | -13957.6 | 62 | 62 | 288.961 | 39521.7
6081 | 877331 | -14460.3 | 63 | 62 | 289.9 | 61509.4
6082 | 921720 | -12512.2 | 64 | 63 | 283.799 | 62884
6083 | 877459 | -9205.35 | 66 | 64 | 267.265 | 62884.1
6084 | 924471 | -8299.15 | 67 | 65 | 268.667 | 62884.3
6085 | 1035090 | -11772.9 | 67 | 65 | 292.715 | 62884.6
6086 | 1066680 | -14723.6 | 67 | 65 | 301.314 | 61510.5
6087 | 1107270 | -15918.9 | 67 | 65 | 305.893 | 56013.1
6088 | 1102610 | -15669.1 | 67 | 65 | 302.534 | 46393
6089 | 992530 | -13031.8 | 67 | 65 | 274.342 | 35398.9
6090 | 674059 | -9515.21 | 67 | 65 | 190.85 | 21657
6091 | 187618 | 0 | 66 | 65 | 117.985 | 15473.9
6092 | 167637 | 0 | 65 | 64 | 103.091 | 14788.6
6093 | 154550 | 0 | 64 | 64 | 91.7819 | 9280.09
6094 | 143605 | 0 | 63 | 63 | 83.242 | 9058.63
6095 | 138642 | 0 | 61 | 61 | 79.2084 | 7902.58
6096 | 137441 | 0 | 60 | 60 | 78.4687 | 7902.48
6097 | 136743 | 0 | 60 | 60 | 78.6912 | 7902.31
6098 | 136206 | 0 | 61 | 61 | 78.9587 | 7902.19
6099 | 135562 | 0 | 61 | 61 | 78.6729 | 7901.98
6100 | 138834 | 0 | 61 | 61 | 82.7094 | 8753.73
6101 | 263702 | 0 | 61 | 61 | 130.12 | 10649.8
6102 | 795471 | -9930.26 | 61 | 61 | 263.119 | 28513.6
6103 | 924597 | -16549.1 | 62 | 62 | 293.481 | 31257.8
6104 | 959449 | -17781.4 | 64 | 63 | 295.133 | 39517.9
6105 | 1008150 | -18438.2 | 65 | 64 | 315.605 | 61506.6
6106 | 1042110 | -16063 | 66 | 65 | 309.175 | 62881.3
6107 | 944921 | -13323.5 | 66 | 65 | 289.505 | 62881.5
6108 | 968180 | -12013.3 | 67 | 65 | 291.644 | 62881.8
6109 | 1069090 | -15604 | 67 | 65 | 314.765 | 62882.4
6110 | 1136000 | -18077.4 | 68 | 66 | 326.908 | 61508.4
6111 | 1175210 | -19791.6 | 68 | 66 | 329.971 | 56011
6112 | 1174480 | -19378.1 | 68 | 66 | 325.294 | 46391
6113 | 1054060 | -16459.1 | 67 | 66 | 297.513 | 35397.2
6114 | 715166 | -12568.7 | 67 | 66 | 215.317 | 21655.2
6115 | 192076 | 0 | 66 | 66 | 122.099 | 15472.2
6116 | 171874 | 0 | 66 | 66 | 103.609 | 14787
6117 | 158486 | 0 | 65 | 65 | 92.0097 | 9278.03
6118 | 147498 | 0 | 65 | 65 | 83.7652 | 9056.66
6119 | 142464 | 0 | 64 | 64 | 79.7499 | 7900.65
6120 | 140934 | 0 | 64 | 64 | 79.4587 | 7900.66
6121 | 140055 | 0 | 64 | 64 | 79.4172 | 7900.62
6122 | 139354 | 0 | 65 | 65 | 79.6871 | 7900.63
6123 | 138626 | 0 | 65 | 65 | 79.3897 | 7900.58
6124 | 141771 | 0 | 64 | 64 | 82.6979 | 8752.48
6125 | 257291 | 0 | 64 | 64 | 130.04 | 10648.7
6126 | 876335 | -8388.84 | 63 | 63 | 265.089 | 28512.5
6127 | 1046890 | -19789.3 | 65 | 65 | 296.519 | 31256.9
6128 | 1099320 | -20243 | 66 | 66 | 302.068 | 39517
6129 | 1183050 | -20637.1 | 68 | 68 | 327.198 | 61505.5
6130 | 1183290 | -18281.2 | 68 | 68 | 317.899 | 62880.4
6131 | 1072120 | -14769.4 | 69 | 68 | 297.718 | 62880.5
6132 | 1102600 | -13896.3 | 69 | 68 | 299.375 | 62880.8
6133 | 1210340 | -16938.6 | 70 | 68 | 324.089 | 62881.4
6134 | 1256870 | -20464.2 | 72 | 68 | 334.775 | 61507.4
6135 | 1304340 | -21544.2 | 73 | 68 | 339.17 | 56010
6136 | 1245680 | -21155.9 | 71 | 66 | 329.074 | 46390.6
6137 | 1084720 | -18050.3 | 69 | 65 | 299.148 | 35396.7
6138 | 702008 | -14348.8 | 67 | 64 | 206.502 | 21654.7
6139 | 193203 | 0 | 65 | 63 | 118.018 | 15471.4
6140 | 173345 | 0 | 64 | 63 | 103.314 | 14786.2
6141 | 159704 | 0 | 62 | 62 | 91.6792 | 9276.97
6142 | 148514 | 0 | 61 | 61 | 83.3924 | 9055.63
6143 | 143567 | 0 | 60 | 60 | 79.6528 | 7899.66
6144 | 141705 | 0 | 59 | 58 | 79.2235 | 7899.71
6145 | 140778 | 0 | 57 | 57 | 79.1806 | 7899.61
6146 | 139630 | 0 | 56 | 55 | 79.1286 | 7899.86
6147 | 138884 | 0 | 54 | 54 | 79.0944 | 7900.15
6148 | 141716 | 0 | 53 | 53 | 82.8045 | 8752.58
6149 | 228164 | 0 | 53 | 53 | 128.394 | 10649.4
6150 | 458241 | -14507.9 | 52 | 52 | 242.371 | 28514.1
6151 | 604734 | -33668.3 | 55 | 53 | 269.078 | 31259.3
6152 | 689000 | -30575.2 | 57 | 54 | 276.25 | 39518.1
6153 | 771056 | -26595.2 | 60 | 55 | 280.636 | 61506.4
6154 | 847408 | -22393.9 | 62 | 57 | 277.759 | 62882.6
6155 | 822412 | -18269.1 | 65 | 58 | 263.248 | 62883.6
6156 | 923391 | -34582.2 | 67 | 59 | 269.415 | 62883.7
6157 | 954487 | -19289 | 68 | 58 | 306.704 | 62884.1
6158 | 995189 | -20694.5 | 69 | 58 | 315.89 | 61510.4
6159 | 1053510 | -22051.6 | 70 | 58 | 320.983 | 56014
6160 | 1024280 | -21605.6 | 69 | 58 | 306.63 | 46394.3
6161 | 881422 | -18783.1 | 67 | 57 | 266.127 | 35400.5
6162 | 575701 | -14658.9 | 66 | 57 | 180.723 | 21658
6163 | 193069 | 0 | 62 | 56 | 117.058 | 15473.5
6164 | 173133 | 0 | 58 | 55 | 102.864 | 14787.8
6165 | 159462 | 0 | 54 | 53 | 92.1028 | 9279.31
6166 | 148336 | 0 | 54 | 53 | 83.6026 | 9057.88
6167 | 143476 | 0 | 55 | 54 | 79.9038 | 7902.07
6168 | 141780 | 0 | 55 | 54 | 79.3457 | 7902.25
6169 | 140752 | 0 | 55 | 54 | 79.2984 | 7902.34
6170 | 139791 | 0 | 56 | 54 | 79.2547 | 7902.9
6171 | 138961 | 0 | 56 | 54 | 79.2169 | 7903.4
6172 | 141913 | 0 | 56 | 54 | 82.8134 | 8755.96
6173 | 226701 | 0 | 57 | 54 | 128.326 | 10652.8
6174 | 533511 | -13889.2 | 57 | 54 | 247.599 | 28517.4
6175 | 691811 | -27377.7 | 61 | 56 | 276.297 | 31262.3
6176 | 821309 | -23858.4 | 64 | 59 | 286.663 | 39519.8
6177 | 931136 | -22820.5 | 68 | 60 | 294.685 | 61507.8
6178 | 1023260 | -19121.3 | 70 | 62 | 290.89 | 62882.4
6179 | 1013320 | -19486.7 | 72 | 63 | 276.901 | 62883.9
6180 | 1149680 | -39571.9 | 74 | 64 | 305.576 | 62884
6181 | 1212630 | -21631.5 | 75 | 64 | 324.579 | 62884.9
6182 | 1250960 | -19116.5 | 75 | 64 | 333.055 | 61511.4
6183 | 1294660 | -23249.2 | 76 | 64 | 337.673 | 56014.9
6184 | 1261130 | -20879 | 74 | 64 | 329.57 | 46395.4
6185 | 1083600 | -18073.8 | 71 | 63 | 286.057 | 35401.5
6186 | 687855 | -14120.2 | 69 | 62 | 186.44 | 21659
6187 | 193520 | 0 | 65 | 60 | 117.48 | 15474.5
6188 | 173145 | 0 | 61 | 57 | 102.391 | 14788.3
6189 | 159564 | 0 | 57 | 54 | 91.8505 | 9279.56
6190 | 148494 | 0 | 55 | 53 | 83.6098 | 9058.04
6191 | 143387 | 0 | 52 | 51 | 79.9 | 7902.31
6192 | 141483 | 0 | 50 | 50 | 75.28 | 7902.65
6193 | 140428 | 0 | 50 | 50 | 75.2314 | 7902.72
6194 | 139453 | 0 | 50 | 50 | 75.187 | 7903.61
6195 | 138564 | 0 | 50 | 50 | 75.1466 | 7904.12
6196 | 137670 | 0 | 50 | 50 | 75.106 | 7904.61
6197 | 136746 | 0 | 49 | 49 | 75.0641 | 7905.05
6198 | 136014 | 0 | 49 | 49 | 72.6307 | 7905.49
6199 | 206934 | -14192.4 | 55 | 53 | 87.3531 | 7905.9
6200 | 242471 | -24241.9 | 60 | 57 | 87.7777 | 7906.2
6201 | 293016 | -19614.6 | 66 | 60 | 89.3876 | 7917.11
6202 | 414608 | -18319.9 | 71 | 64 | 117.049 | 7918.51
6203 | 573943 | -29171.7 | 76 | 68 | 126.597 | 7919.84
6204 | 731137 | -35513.8 | 81 | 72 | 135.205 | 7920.1
6205 | 790520 | -35307.9 | 83 | 73 | 139.981 | 7920.48
6206 | 209707 | 0 | 85 | 74 | 87.7879 | 7920.86
6207 | 217791 | 0 | 87 | 75 | 87.4391 | 7921.27
6208 | 266633 | 0 | 85 | 73 | 98.9099 | 7914.72
6209 | 262254 | 0 | 82 | 71 | 101.603 | 7910.36
6210 | 132072 | 0 | 80 | 70 | 77.8754 | 7907.17
6211 | 131769 | 0 | 78 | 68 | 80.2028 | 7904.59
6212 | 131307 | 0 | 77 | 66 | 80.2188 | 7902.93
6213 | 131024 | 0 | 75 | 63 | 80.2045 | 7901.59
6214 | 130989 | 0 | 70 | 62 | 77.8464 | 7900.58
6215 | 130494 | 0 | 66 | 60 | 77.1611 | 7899.73
6216 | 129928 | 0 | 61 | 57 | 72.2421 | 3089.49
6217 | 129795 | 0 | 59 | 57 | 73.2183 | 3089.09
6218 | 129322 | 0 | 58 | 56 | 73.451 | 3089.14
6219 | 128987 | 0 | 56 | 55 | 73.4357 | 3089.28
6220 | 128691 | 0 | 55 | 55 | 73.4222 | 3089.22
6221 | 128229 | 0 | 54 | 54 | 73.4015 | 3089.26
6222 | 127866 | 0 | 53 | 53 | 71.0508 | 3089.34
6223 | 127888 | 0 | 57 | 56 | 68.1849 | 3089.44
6224 | 127691 | 0 | 61 | 58 | 67.5601 | 3089.55
6225 | 127575 | 0 | 65 | 60 | 68.835 | 3089.66
6226 | 189327 | 0 | 69 | 61 | 75.9994 | 3088.97
6227 | 197219 | 0 | 72 | 62 | 76.3667 | 3087.53
6228 | 210275 | 0 | 76 | 62 | 77.2653 | 3085.56
6229 | 220540 | 0 | 75 | 61 | 76.9275 | 3083.56
6230 | 253480 | 0 | 74 | 60 | 80.3023 | 3081.74
6231 | 195834 | 0 | 73 | 60 | 75.2883 | 3080.01
6232 | 127171 | 0 | 72 | 62 | 69.2123 | 3078.23
6233 | 127205 | 0 | 72 | 63 | 73.4516 | 3076.83
6234 | 127438 | 0 | 71 | 65 | 77.0457 | 3076.11
6235 | 127115 | 0 | 70 | 65 | 77.4 | 3075.29
6236 | 126984 | 0 | 70 | 65 | 77.6633 | 3074.78
6237 | 126945 | 0 | 69 | 65 | 77.3544 | 3074.3
6238 | 126674 | 0 | 67 | 64 | 76.2054 | 3073.84
6239 | 126418 | 0 | 65 | 62 | 75.3269 | 3073.51
6240 | 126790 | 0 | 63 | 61 | 78.2501 | 7882.78
6241 | 126919 | 0 | 63 | 62 | 78.7715 | 7882.68
6242 | 126834 | 0 | 64 | 63 | 79.063 | 7881.88
6243 | 126638 | 0 | 64 | 63 | 78.7938 | 7881.64
6244 | 130612 | 0 | 64 | 64 | 82.4398 | 8733.43
6245 | 256486 | 0 | 65 | 64 | 130.345 | 10629.6
6246 | 1240130 | -9992.4 | 65 | 65 | 294.143 | 28493.3
6247 | 1217440 | -27042 | 66 | 65 | 318.956 | 31237.5
6248 | 1139600 | -19808 | 66 | 65 | 306.191 | 39506.2
6249 | 1155840 | -14801.3 | 67 | 66 | 305.562 | 61496.3
6250 | 1154630 | -13368.2 | 68 | 66 | 296.398 | 62871.5
6251 | 1089140 | -10217.4 | 70 | 67 | 278.785 | 62872.1
6252 | 1154680 | -9440.05 | 71 | 68 | 281.282 | 62872.7
6253 | 1267940 | -12722.2 | 72 | 68 | 306.506 | 62873.4
6254 | 1333360 | -15996.1 | 72 | 69 | 317.334 | 61499.9
6255 | 1368410 | -17029 | 73 | 69 | 322.079 | 56003.4
6256 | 1319390 | -16687.1 | 72 | 68 | 314.104 | 46384.2
6257 | 1169110 | -13874.5 | 71 | 67 | 284.205 | 35390.6
6258 | 808086 | -10326 | 70 | 67 | 198.053 | 21648.6
6259 | 188520 | 0 | 69 | 66 | 118.431 | 15465.2
6260 | 168452 | 0 | 68 | 65 | 103.275 | 14780.2
6261 | 155206 | 0 | 67 | 64 | 91.9423 | 9269.9
6262 | 144467 | 0 | 67 | 64 | 83.7066 | 9047.84
6263 | 139794 | 0 | 66 | 64 | 79.7018 | 7891.35
6264 | 138348 | 0 | 66 | 64 | 78.992 | 7891
6265 | 137614 | 0 | 66 | 64 | 78.9569 | 7890.67
6266 | 136915 | 0 | 67 | 64 | 79.2304 | 7890.45
6267 | 136410 | 0 | 67 | 64 | 78.9399 | 7890.21
6268 | 139835 | 0 | 65 | 64 | 82.3834 | 8741.96
6269 | 260414 | 0 | 64 | 63 | 129.914 | 10638
6270 | 935668 | -7642.4 | 62 | 62 | 267.953 | 28501.8
6271 | 1049200 | -20559.6 | 64 | 63 | 303.125 | 31246.2
6272 | 1061340 | -20903 | 65 | 64 | 298.878 | 39510.2
6273 | 1089250 | -20853.3 | 67 | 64 | 320.482 | 61500.1
6274 | 1199380 | -17562.8 | 71 | 66 | 321.837 | 62875.1
6275 | 1232660 | -20790.1 | 74 | 68 | 311.312 | 62875.6
6276 | 1405220 | -42745 | 78 | 69 | 322.911 | 62877.1
6277 | 1508430 | -23926 | 79 | 70 | 346.019 | 62878.9
6278 | 1573760 | -20172.8 | 80 | 71 | 357.221 | 61505.7
6279 | 1681080 | -30547.4 | 81 | 72 | 364.538 | 56009.5
6280 | 1598060 | -16845.9 | 80 | 71 | 354.914 | 46390.3
6281 | 1432570 | -13988 | 78 | 70 | 324.034 | 35396.7
6282 | 954659 | -9904.96 | 77 | 69 | 228.326 | 21654.5
6283 | 193665 | 0 | 76 | 69 | 126.037 | 15470.4
6284 | 173278 | 0 | 75 | 69 | 104.175 | 14783.5
6285 | 160051 | 0 | 74 | 69 | 92.5158 | 9273.28
6286 | 149113 | 0 | 73 | 69 | 83.9297 | 9050.39
6287 | 144114 | 0 | 73 | 69 | 80.4827 | 7893.47
6288 | 142596 | 0 | 72 | 69 | 79.6041 | 7892.53
6289 | 141715 | 0 | 72 | 69 | 79.8358 | 7891.76
6290 | 140936 | 0 | 71 | 69 | 79.479 | 7891.02
6291 | 140200 | 0 | 71 | 69 | 79.7165 | 7890.3
6292 | 143714 | 0 | 71 | 69 | 83.3496 | 8741.59
6293 | 286437 | 0 | 72 | 69 | 132.488 | 10637.3
6294 | 1375990 | -4649.42 | 72 | 69 | 294.145 | 28500.7
6295 | 1462700 | -21717.8 | 73 | 70 | 322.394 | 31244.6
6296 | 1406790 | -22097.1 | 74 | 70 | 341.373 | 39510.8
6297 | 1448720 | -22509.3 | 75 | 70 | 347.477 | 61501
6298 | 1538380 | -21500.6 | 78 | 71 | 344.136 | 62875.9
6299 | 1472020 | -23087.7 | 81 | 72 | 326.345 | 62878
6300 | 1628030 | -38581.7 | 84 | 73 | 341.157 | 62879.2
6301 | 1650040 | -15685 | 81 | 73 | 355.94 | 62880.3
6302 | 1606620 | -21129 | 78 | 72 | 359.333 | 61506.9
6303 | 1571190 | -23237.9 | 75 | 71 | 357.972 | 56010.2
6304 | 1451860 | -23553.2 | 72 | 69 | 343.417 | 46390.5
6305 | 1255830 | -20798.9 | 70 | 68 | 311.24 | 35396.5
6306 | 813979 | -17119.8 | 67 | 66 | 222.414 | 21654.2
6307 | 194425 | 0 | 65 | 64 | 122.896 | 15469.9
6308 | 173939 | 0 | 64 | 62 | 103.346 | 14784.2
6309 | 160308 | 0 | 62 | 59 | 91.707 | 9274.31
6310 | 149432 | 0 | 61 | 59 | 83.4342 | 9052.49
6311 | 144276 | 0 | 59 | 58 | 79.6851 | 7896.34
6312 | 142553 | 0 | 58 | 57 | 79.2619 | 7896.37
6313 | 141361 | 0 | 56 | 55 | 79.2073 | 7896.5
6314 | 140330 | 0 | 54 | 53 | 79.1603 | 7896.75
6315 | 139334 | 0 | 52 | 51 | 79.1151 | 7896.98
6316 | 142188 | 0 | 52 | 50 | 82.8259 | 8748.99
6317 | 241010 | 0 | 53 | 49 | 128.99 | 10645.5
6318 | 502348 | -11249 | 53 | 49 | 245.066 | 28509.7
6319 | 572417 | -32966.7 | 54 | 48 | 268.534 | 31254.4
6320 | 626784 | -33923.5 | 55 | 48 | 292.722 | 39515.3
6321 | 668835 | -31617 | 56 | 47 | 294.776 | 61504.1
6322 | 682395 | -27741 | 57 | 48 | 286.831 | 62880.1
6323 | 686274 | -27774.5 | 58 | 48 | 272.99 | 62881.2
6324 | 731135 | -44878.5 | 59 | 48 | 274.825 | 62882
6325 | 774841 | -26173.1 | 60 | 49 | 295.426 | 62882.8
6326 | 813840 | -25463.4 | 60 | 49 | 304.3 | 61509
6327 | 837170 | -26421.2 | 61 | 49 | 307.082 | 56012.5
6328 | 774233 | -26952 | 59 | 49 | 298.832 | 46393.1
6329 | 646809 | -24766.5 | 58 | 48 | 273.111 | 35399.2
6330 | 409768 | -24094.2 | 56 | 47 | 193.645 | 21656.5
6331 | 192182 | 0 | 53 | 46 | 122.521 | 15472.3
6332 | 172354 | 0 | 50 | 45 | 106.671 | 14787.2
6333 | 158765 | 0 | 47 | 44 | 94.792 | 9279.8
6334 | 147422 | 0 | 45 | 43 | 85.8185 | 9059.4
6335 | 142395 | 0 | 44 | 42 | 81.9331 | 7904.61
6336 | 140712 | 0 | 42 | 41 | 81.3169 | 7905.76
6337 | 139686 | 0 | 41 | 41 | 81.2353 | 7906.55
6338 | 138498 | 0 | 41 | 40 | 81.1425 | 7907.43
6339 | 137747 | 0 | 40 | 40 | 81.0833 | 7908.26
6340 | 140241 | 0 | 40 | 40 | 84.7394 | 8761.08
6341 | 211977 | -3432.16 | 39 | 39 | 133.522 | 10658.2
6342 | 331430 | -36323.3 | 39 | 39 | 237.687 | 28523.2
6343 | 455132 | -122665 | 41 | 41 | 291.943 | 31268.4
6344 | 499963 | -113621 | 43 | 43 | 289.435 | 39523
6345 | 558153 | -106537 | 45 | 45 | 292.834 | 61510.8
6346 | 534161 | -59242.9 | 50 | 48 | 281.228 | 62885.4
6347 | 545427 | -27945.9 | 56 | 49 | 266.466 | 62885.3
6348 | 656749 | -37745.7 | 61 | 51 | 273.688 | 62885.1
6349 | 724919 | -20002.6 | 62 | 52 | 289.772 | 62885.8
6350 | 789840 | -18839.3 | 63 | 52 | 303.83 | 61512.4
6351 | 839407 | -20543.4 | 64 | 53 | 307.712 | 56015.6
6352 | 775865 | -20906 | 62 | 52 | 299.045 | 46396
6353 | 644495 | -19360.5 | 60 | 52 | 271.91 | 35402
6354 | 402080 | -18416 | 58 | 51 | 193.872 | 21659.2
6355 | 191387 | 0 | 55 | 50 | 122.451 | 15475.2
6356 | 171457 | 0 | 51 | 48 | 106.35 | 14790
6357 | 157860 | 0 | 48 | 46 | 94.012 | 9282.9
6358 | 146797 | 0 | 47 | 46 | 83.5325 | 9062.52
6359 | 141706 | 0 | 47 | 45 | 79.8235 | 7907.77
6360 | 139860 | 0 | 46 | 44 | 75.2062 | 7909.05
6361 | 138969 | -6292.55 | 46 | 45 | 81.75 | 7910.33
6362 | 137827 | 0 | 45 | 45 | 75.1133 | 7912.23
6363 | 137076 | -1840.85 | 45 | 45 | 79.5077 | 7913.82
6364 | 136032 | 0 | 45 | 45 | 75.0317 | 7915.45
6365 | 135192 | 0 | 44 | 44 | 74.9935 | 7916.82
6366 | 141145 | -5519.84 | 44 | 44 | 79.3584 | 7918.25
6367 | 183539 | -77393.9 | 47 | 46 | 86.8199 | 7919.27
6368 | 222907 | -165761 | 51 | 49 | 98.3809 | 7920.18
6369 | 224082 | -124236 | 54 | 51 | 90.7573 | 7925.78
6370 | 226791 | -83349.4 | 58 | 53 | 89.9749 | 7926.51
6371 | 259291 | -59770.1 | 63 | 55 | 91.9776 | 7927.6
6372 | 336980 | -58547.9 | 67 | 57 | 97.312 | 7928.07
6373 | 386702 | -57688.1 | 68 | 58 | 100.053 | 7928.45
6374 | 177408 | 0 | 69 | 58 | 81.5468 | 7928.7
6375 | 174736 | 0 | 70 | 59 | 80.9834 | 7928.91
6376 | 174994 | 0 | 68 | 58 | 79.7718 | 7925.28
6377 | 130033 | 0 | 66 | 58 | 75.2038 | 7922.36
6378 | 129709 | 0 | 64 | 57 | 79.3599 | 7920.75
6379 | 129606 | 0 | 63 | 57 | 79.4003 | 7919.52
6380 | 129363 | 0 | 62 | 57 | 79.3558 | 7919.05
6381 | 129123 | 0 | 61 | 57 | 79.3121 | 7918.89
6382 | 128972 | 0 | 61 | 58 | 78.7604 | 7918.95
6383 | 128674 | 0 | 60 | 58 | 77.6598 | 7919.06
6384 | 128287 | 0 | 60 | 58 | 73.4041 | 3109.71
6385 | 128009 | 0 | 60 | 58 | 73.3914 | 3109.89
6386 | 127902 | 0 | 59 | 59 | 73.3864 | 3110.28
6387 | 127565 | 0 | 59 | 59 | 73.3714 | 3110.65
6388 | 127322 | 0 | 59 | 59 | 73.3603 | 3111.02
6389 | 127062 | 0 | 60 | 59 | 73.3486 | 3111.42
6390 | 126869 | 0 | 60 | 59 | 70.9398 | 3111.84
6391 | 126786 | 0 | 61 | 60 | 69.2905 | 3112.25
6392 | 126564 | 0 | 61 | 60 | 67.8584 | 3112.61
6393 | 126508 | 0 | 62 | 61 | 68.4972 | 3112.95
6394 | 126449 | 0 | 63 | 62 | 68.4225 | 3113.17
6395 | 126302 | 0 | 65 | 63 | 68.6149 | 3113.2
6396 | 126344 | 0 | 66 | 65 | 68.3126 | 3112.93
6397 | 126221 | 0 | 69 | 66 | 69.4702 | 3112.56
6398 | 167025 | 0 | 71 | 67 | 78.7046 | 3111.94
6399 | 178604 | 0 | 74 | 68 | 81.9654 | 3111.19
6400 | 126053 | 0 | 72 | 67 | 69.9876 | 3110.17
6401 | 126089 | 0 | 71 | 67 | 72.4803 | 3108.82
6402 | 126037 | 0 | 69 | 66 | 75.9916 | 3107.74
6403 | 126045 | 0 | 67 | 66 | 76.9757 | 3106.68
6404 | 125948 | 0 | 66 | 65 | 77.1998 | 3106.1
6405 | 125831 | 0 | 64 | 64 | 76.8674 | 3105.78
6406 | 125662 | 0 | 63 | 63 | 76.2853 | 3105.64
6407 | 125649 | 0 | 63 | 63 | 75.7425 | 3105.57
6408 | 125774 | 0 | 62 | 62 | 78.4285 | 7915.12
6409 | 125835 | 0 | 62 | 62 | 78.6877 | 7915.22
6410 | 125768 | 0 | 62 | 62 | 78.6847 | 7914.5
6411 | 125691 | 0 | 62 | 62 | 78.6812 | 7914.23
6412 | 129328 | 0 | 61 | 61 | 82.0204 | 8765.97
6413 | 235485 | 0 | 61 | 61 | 128.787 | 10662.1
6414 | 682354 | -13258.3 | 60 | 60 | 259.494 | 28525.9
6415 | 809792 | -16078.3 | 61 | 61 | 293.446 | 31270.2
6416 | 840922 | -13931 | 62 | 62 | 289.988 | 39525.1
6417 | 861521 | -12674.3 | 63 | 62 | 288.83 | 61512.7
6418 | 861803 | -11980.7 | 62 | 62 | 278.764 | 62887.1
6419 | 777431 | -9755.11 | 62 | 62 | 259.091 | 62887
6420 | 734446 | -9667.25 | 61 | 61 | 254.493 | 62887.2
6421 | 867941 | -13125.5 | 62 | 62 | 281.05 | 62887.5
6422 | 911001 | -14850.9 | 64 | 62 | 290.985 | 61513.3
6423 | 986185 | -15507.3 | 65 | 63 | 296.604 | 56015.9
6424 | 988865 | -15421.5 | 65 | 63 | 293.465 | 46395.7
6425 | 907835 | -12727.4 | 65 | 64 | 269.923 | 35401.6
6426 | 614762 | -9540.12 | 65 | 64 | 189.613 | 21659.5
6427 | 186950 | 0 | 63 | 63 | 117.616 | 15476.3
6428 | 167019 | 0 | 62 | 62 | 102.927 | 14790.9
6429 | 153725 | 0 | 60 | 60 | 91.328 | 9283.21
6430 | 143002 | 0 | 59 | 59 | 83.3593 | 9062.15
6431 | 138068 | 0 | 57 | 57 | 79.658 | 7906.6
6432 | 136663 | 0 | 56 | 56 | 78.6881 | 7907.05
6433 | 135878 | 0 | 55 | 55 | 78.652 | 7907.49
6434 | 135131 | 0 | 54 | 54 | 78.6181 | 7908.01
6435 | 134461 | 0 | 53 | 53 | 78.5876 | 7908.51
6436 | 137478 | 0 | 52 | 52 | 82.6118 | 8761.05
6437 | 208081 | -2064.17 | 52 | 51 | 130.849 | 10658
6438 | 386863 | -20952.5 | 51 | 50 | 241.462 | 28522.8
6439 | 470414 | -45141.4 | 50 | 49 | 271.639 | 31268.1
6440 | 514779 | -68904.1 | 49 | 48 | 269.679 | 39523.5
6441 | 505426 | -74895.6 | 48 | 46 | 287.116 | 61511.3
6442 | 491270 | -62179.1 | 49 | 47 | 277.269 | 62886
6443 | 484686 | -67844.5 | 50 | 47 | 262.63 | 62886.2
6444 | 458956 | -57089.6 | 51 | 47 | 259.481 | 62886.6
6445 | 522255 | -61496.2 | 51 | 47 | 281.424 | 62887.1
6446 | 530973 | -49820.7 | 51 | 47 | 287.013 | 61513.1
6447 | 518294 | -38513.3 | 51 | 47 | 288.089 | 56015.8
6448 | 509553 | -37364.2 | 51 | 47 | 284.275 | 46395.7
6449 | 442873 | -49552.6 | 50 | 46 | 263.148 | 35401.7
6450 | 362416 | -86688.8 | 50 | 46 | 197.426 | 21659.8
6451 | 188855 | 0 | 50 | 46 | 121.565 | 15476.8
6452 | 169215 | 0 | 49 | 45 | 103.2 | 14791.7
6453 | 155870 | 0 | 49 | 45 | 91.9382 | 9286.72
6454 | 144769 | 0 | 49 | 45 | 83.4401 | 9066.95
6455 | 139836 | -6617.86 | 48 | 44 | 86.631 | 7912.7
6456 | 138303 | 0 | 48 | 44 | 79.1876 | 7914.12
6457 | 137361 | -1516.14 | 46 | 43 | 83.5732 | 7915.42
6458 | 136553 | 0 | 44 | 43 | 79.1075 | 7916.78
6459 | 135626 | -2709.45 | 42 | 42 | 83.4944 | 7917.92
6460 | 138221 | 0 | 42 | 41 | 82.6458 | 8771.24
6461 | 191858 | -4027.65 | 41 | 41 | 127.288 | 10668.8
6462 | 329854 | -70757.8 | 41 | 41 | 238.696 | 28534.2
6463 | 463474 | -161721 | 44 | 43 | 272.24 | 31279.6
6464 | 493046 | -125490 | 46 | 45 | 270.684 | 39529.5
6465 | 505595 | -101712 | 49 | 46 | 270.027 | 61516.9
6466 | 492523 | -60188 | 52 | 48 | 260.13 | 62890.9
6467 | 506905 | -52044.1 | 54 | 50 | 264.555 | 62890.4
6468 | 541935 | -40160.2 | 57 | 51 | 265.557 | 62890.2
6469 | 621373 | -15389.9 | 59 | 52 | 270.941 | 62890.3
6470 | 712843 | -13946 | 61 | 53 | 298.55 | 61516.1
6471 | 790628 | -17751.4 | 63 | 54 | 304.782 | 56019
6472 | 731694 | -15842.3 | 61 | 54 | 295.921 | 46398.9
6473 | 604696 | -14661.9 | 60 | 53 | 269.445 | 35404.8
6474 | 376490 | -16109.1 | 58 | 53 | 174.46 | 21661.8
6475 | 190487 | 0 | 57 | 53 | 117.965 | 15478.5
6476 | 170543 | 0 | 56 | 52 | 103.261 | 14793.2
6477 | 157242 | 0 | 55 | 52 | 92.0009 | 9287.04
6478 | 146106 | 0 | 55 | 52 | 83.501 | 9066.81
6479 | 141208 | 0 | 55 | 52 | 79.8007 | 7912.02
6480 | 139639 | 0 | 55 | 52 | 79.1293 | 7913.01
6481 | 138807 | 0 | 56 | 53 | 79.091 | 7913.86
6482 | 138058 | 0 | 56 | 54 | 79.0569 | 7914.63
6483 | 137278 | 0 | 57 | 55 | 79.0215 | 7915.28
6484 | 140430 | 0 | 58 | 56 | 82.7458 | 8767.83
6485 | 187401 | 0 | 59 | 57 | 122.511 | 10664.7
6486 | 485544 | -30218 | 60 | 59 | 257.672 | 28529.2
6487 | 706763 | -16660 | 61 | 60 | 278.168 | 31274.1
6488 | 775572 | -20281.6 | 62 | 62 | 277.036 | 39527
6489 | 832800 | -17667.1 | 63 | 63 | 285.519 | 61514.3
6490 | 884587 | -16038.6 | 64 | 64 | 282.372 | 62888.5
6491 | 801302 | -12947.4 | 64 | 64 | 279.594 | 62888.3
6492 | 831602 | -11817.2 | 65 | 65 | 280.77 | 62888.3
6493 | 859228 | -16794.7 | 62 | 62 | 298.407 | 62888.5
6494 | 772496 | -21138.6 | 59 | 58 | 300.132 | 61514.2
6495 | 704747 | -24233.6 | 56 | 55 | 298.407 | 56016.7
6496 | 651055 | -26201.8 | 55 | 53 | 290.576 | 46396.5
6497 | 492535 | -27493.3 | 53 | 50 | 263.744 | 35402.5
6498 | 362604 | -58290.2 | 52 | 48 | 195.317 | 21660.6
6499 | 190572 | 0 | 51 | 47 | 117.958 | 15477.5
6500 | 170917 | 0 | 49 | 46 | 103.278 | 14792.4
6501 | 157370 | 0 | 48 | 45 | 92.007 | 9286.84
6502 | 146281 | 0 | 46 | 45 | 83.5089 | 9067.06
6503 | 141167 | -6975.71 | 45 | 44 | 86.7995 | 7912.81
6504 | 139463 | 0 | 43 | 43 | 79.2404 | 7914.38
6505 | 138386 | -11911 | 42 | 42 | 87.0453 | 7915.95
6506 | 137245 | 0 | 41 | 40 | 79.1392 | 7917.63
6507 | 136488 | -15675.4 | 40 | 39 | 87.6775 | 7919.19
6508 | 139047 | -4093.23 | 39 | 38 | 87.2589 | 8772.9
6509 | 197877 | -10085.3 | 38 | 38 | 129.938 | 10670.9
6510 | 330167 | -127794 | 37 | 37 | 238.418 | 28536.7
6511 | 423228 | -197223 | 40 | 39 | 266.852 | 31282.8
6512 | 465876 | -162178 | 43 | 41 | 271.068 | 39531.4
6513 | 494765 | -146227 | 46 | 43 | 273.629 | 61519.4
6514 | 462281 | -111209 | 47 | 43 | 263.524 | 62893.6
6515 | 475057 | -102794 | 49 | 43 | 249.358 | 62893
6516 | 438491 | -84119.2 | 50 | 43 | 244.599 | 62892
6517 | 495930 | -89706.4 | 50 | 42 | 283.646 | 62892.1
6518 | 506890 | -79562 | 50 | 42 | 288.815 | 61517.8
6519 | 497013 | -66092.6 | 50 | 42 | 288.545 | 56020.3
6520 | 490449 | -71518.1 | 49 | 42 | 283.903 | 46400.1
6521 | 433633 | -87997.3 | 48 | 41 | 264.42 | 35405.9
6522 | 362335 | -151485 | 47 | 41 | 183.359 | 21663.8
6523 | 189110 | 0 | 46 | 40 | 117.891 | 15480.7
6524 | 169630 | 0 | 44 | 39 | 103.219 | 14795.6
6525 | 156158 | -7494.43 | 43 | 39 | 99.3257 | 9292.08
6526 | 144747 | 0 | 43 | 38 | 83.4393 | 9072.94
6527 | 140025 | -13800.5 | 42 | 38 | 88.2223 | 7919.39
6528 | 138026 | 0 | 42 | 38 | 75.123 | 7921.5
6529 | 136988 | -17198.2 | 40 | 37 | 83.9869 | 7923.33
6530 | 135943 | -5035.88 | 39 | 35 | 79.4565 | 7925.91
6531 | 137110 | -12645.4 | 37 | 34 | 79.5078 | 7927.97
6532 | 134140 | -11229.1 | 35 | 33 | 79.3762 | 7930.22
6533 | 133306 | -14699.7 | 34 | 32 | 81.9023 | 7932.4
6534 | 132465 | -15894.2 | 32 | 31 | 79.564 | 7934.71
6535 | 149307 | -399376 | 35 | 33 | 94.5747 | 7937.08
6536 | 186702 | -370666 | 39 | 35 | 92.7976 | 7939.22
6537 | 196047 | -317471 | 42 | 37 | 90.4782 | 7942.72
6538 | 197581 | -275559 | 45 | 39 | 88.0404 | 7942.03
6539 | 199074 | -246299 | 47 | 40 | 93.5601 | 7943.22
6540 | 196289 | -224198 | 50 | 41 | 94.3224 | 7943.95
6541 | 195212 | -197429 | 52 | 42 | 94.379 | 7944.7
6542 | 128257 | 0 | 53 | 44 | 71.6576 | 7945.32
6543 | 127970 | 0 | 55 | 45 | 71.67 | 7946.09
6544 | 127741 | -5519.05 | 55 | 45 | 76.353 | 7945.52
6545 | 127586 | 0 | 54 | 46 | 75.9338 | 7945.63
6546 | 127216 | -873.571 | 54 | 46 | 84.86 | 7945.78
6547 | 127183 | 0 | 54 | 48 | 79.4458 | 7946.12
6548 | 126723 | -1350.41 | 55 | 48 | 83.8541 | 7946.6
6549 | 126625 | 0 | 55 | 49 | 79.4206 | 7947.37
6550 | 127530 | -1609.17 | 55 | 50 | 83.0896 | 7948.05
6551 | 126040 | 0 | 55 | 50 | 77.7952 | 7948.81
6552 | 126040 | -1736.74 | 56 | 50 | 77.731 | 3139.89
6553 | 125528 | 0 | 56 | 51 | 73.2794 | 3251.05
6554 | 125171 | 0 | 57 | 51 | 73.2632 | 3251.79
6555 | 125074 | 0 | 57 | 51 | 73.2586 | 3252.54
6556 | 124882 | -8166.55 | 57 | 51 | 79.4962 | 3253.24
6557 | 124592 | 0 | 56 | 50 | 73.237 | 3253.88
6558 | 124398 | 0 | 56 | 49 | 70.8281 | 3254.5
6559 | 124485 | 0 | 57 | 50 | 68.4819 | 3255.19
6560 | 124340 | -8570.4 | 59 | 51 | 73.4339 | 3255.81
6561 | 124192 | 0 | 62 | 52 | 68.0603 | 3256.49
6562 | 124574 | 0 | 66 | 56 | 68.74 | 3256.4
6563 | 142457 | -825.022 | 70 | 58 | 74.2002 | 3255.51
6564 | 156065 | -0.0030222 | 73 | 60 | 74.3495 | 3253.85
6565 | 163100 | 0 | 73 | 60 | 73.8649 | 3252.28
6566 | 170549 | 0 | 72 | 61 | 73.9036 | 3250.67
6567 | 167953 | 0 | 73 | 61 | 74.3989 | 3249.07
6568 | 124462 | 0 | 72 | 61 | 68.8718 | 3247.29
6569 | 124385 | 0 | 71 | 60 | 72.4423 | 3245.77
6570 | 124508 | 0 | 70 | 60 | 76.7481 | 3244.52
6571 | 124529 | 0 | 69 | 60 | 77.2393 | 3243.43
6572 | 124562 | 0 | 68 | 60 | 77.2049 | 3242.84
6573 | 124527 | 0 | 67 | 60 | 77.168 | 3242.35
6574 | 124475 | 0 | 67 | 60 | 76.6298 | 3242
6575 | 124397 | 0 | 62 | 59 | 74.3767 | 3241.65
6576 | 124665 | 0 | 60 | 59 | 78.0627 | 8308.69
6577 | 124014 | 0 | 55 | 54 | 78.5398 | 8308.43
6578 | 124058 | 0 | 53 | 53 | 78.5413 | 8307.66
6579 | 123900 | 0 | 52 | 52 | 78.5344 | 8307.55
6580 | 127533 | 0 | 52 | 52 | 82.1607 | 9205.36
6581 | 174584 | 0 | 51 | 51 | 121.919 | 11203.8
6582 | 320246 | -49343.3 | 51 | 50 | 241.546 | 30025.6
6583 | 434939 | -68947.5 | 51 | 50 | 269.201 | 32917.5
6584 | 489021 | -61092 | 54 | 50 | 268.643 | 41605
6585 | 521393 | -31177.8 | 57 | 50 | 271.172 | 64770.1
6586 | 560947 | -30560.7 | 59 | 50 | 265.907 | 66216.8
6587 | 605885 | -28536.2 | 62 | 50 | 253.674 | 66215.6
6588 | 672704 | -45683.2 | 63 | 49 | 256.324 | 66215.3
6589 | 742721 | -26204.3 | 65 | 50 | 277.482 | 66215.3
6590 | 738741 | -15163.5 | 63 | 49 | 280.167 | 64767.4
6591 | 766243 | -22471.2 | 63 | 49 | 283.473 | 58975.6
6592 | 702456 | -9892.57 | 63 | 48 | 276.028 | 48839.7
6593 | 593223 | -8824.12 | 63 | 49 | 250.966 | 37255.9
6594 | 371283 | -8626.7 | 60 | 48 | 175.623 | 22776.2
6595 | 185275 | 0 | 58 | 47 | 117.723 | 16260.3
6596 | 165800 | 0 | 57 | 47 | 103.042 | 15537.6
6597 | 152418 | 0 | 55 | 46 | 91.7804 | 9738.31
6598 | 141560 | 0 | 55 | 46 | 83.2939 | 9506.3
6599 | 136891 | 0 | 55 | 46 | 79.6044 | 8289.83
6600 | 135409 | 0 | 53 | 45 | 78.6312 | 8290.82
6601 | 134730 | 0 | 51 | 45 | 78.5998 | 8291.73
6602 | 133943 | 0 | 50 | 45 | 78.5642 | 8292.54
6603 | 133254 | -7008.5 | 50 | 45 | 85.0468 | 8293.34
6604 | 136153 | 0 | 49 | 44 | 82.5517 | 9191.86
6605 | 183012 | -1973.89 | 50 | 45 | 126.883 | 11190.8
6606 | 336948 | -42604.1 | 51 | 45 | 238.572 | 30013.2
6607 | 455666 | -89206.8 | 52 | 45 | 275.244 | 32905.9
6608 | 496778 | -49836.5 | 56 | 47 | 270.202 | 41596.8
6609 | 547920 | -21834.7 | 60 | 49 | 273.237 | 64762.3
6610 | 685172 | -30299.1 | 65 | 50 | 272.71 | 66209.6
6611 | 739065 | -31804.8 | 69 | 51 | 262.578 | 66208.8
6612 | 835781 | -50791.5 | 71 | 52 | 269.247 | 66209.4
6613 | 904780 | -31078.8 | 72 | 53 | 307.324 | 66209.6
6614 | 909373 | -21081.4 | 70 | 53 | 310.96 | 64761.7
6615 | 938302 | -27019.2 | 69 | 55 | 313.723 | 58970.2
6616 | 817955 | -7689.91 | 67 | 53 | 302.094 | 48834.7
6617 | 657685 | -7057.39 | 64 | 49 | 273.533 | 37251.1
6618 | 422327 | -6554.73 | 62 | 49 | 177.422 | 22771.7
6619 | 189871 | 0 | 61 | 48 | 117.762 | 16255.3
6620 | 170036 | 0 | 59 | 47 | 102.979 | 15532.8
6621 | 156604 | 0 | 57 | 46 | 91.9718 | 9732.12
6622 | 145464 | 0 | 55 | 45 | 83.4718 | 9499.8
6623 | 140613 | 0 | 54 | 45 | 79.7736 | 8283.01
6624 | 139048 | 0 | 52 | 45 | 79.2214 | 8283.86
6625 | 137888 | 0 | 48 | 43 | 79.1684 | 8284.74
6626 | 137013 | 0 | 48 | 43 | 79.1285 | 8285.67
6627 | 136175 | -7837.88 | 45 | 42 | 86.2357 | 8286.59
6628 | 138829 | 0 | 46 | 42 | 82.6734 | 9185.39
6629 | 185323 | -2305.97 | 45 | 42 | 126.99 | 11184.6
6630 | 335645 | -45979.6 | 48 | 44 | 238.201 | 30007.4
6631 | 459119 | -126740 | 47 | 43 | 277.533 | 32900.4
6632 | 483066 | -104404 | 48 | 44 | 277.623 | 41592.9
6633 | 490088 | -105564 | 48 | 44 | 275.466 | 64758.7
6634 | 461682 | -88647.7 | 48 | 45 | 261.033 | 66206.5
6635 | 477360 | -93762.9 | 49 | 44 | 247.387 | 66206.3
6636 | 459709 | -71371.1 | 51 | 45 | 244.938 | 66206.4
6637 | 517682 | -62188.8 | 52 | 45 | 282.631 | 66206.4
6638 | 509106 | -47639.7 | 52 | 46 | 285.676 | 64758.5
6639 | 477917 | -66437.3 | 46 | 44 | 284.972 | 58966.3
6640 | 484422 | -71431 | 48 | 45 | 284.199 | 48830.5
6641 | 430236 | -85593.4 | 48 | 44 | 251.712 | 37247.2
6642 | 363107 | -149290 | 47 | 44 | 184.669 | 22768.8
6643 | 188944 | 0 | 45 | 44 | 117.884 | 16254.4
6644 | 169009 | 0 | 45 | 42 | 103.19 | 15532.3
6645 | 155857 | -8713.43 | 44 | 42 | 99.848 | 9734.38
6646 | 144541 | 0 | 44 | 42 | 83.4299 | 9503.59
6647 | 139510 | -13520.3 | 43 | 40 | 88.2399 | 8288.22
6648 | 137928 | 0 | 42 | 39 | 79.0516 | 8290.32
6649 | 136935 | -16636 | 41 | 38 | 87.8802 | 8292.15
6650 | 135995 | -4310.03 | 39 | 37 | 83.3922 | 8294.06
6651 | 137383 | -11661.4 | 37 | 36 | 85.5164 | 8295.77
6652 | 137628 | -9765.71 | 39 | 36 | 88.9769 | 9195.27
6653 | 184084 | -7313.61 | 39 | 37 | 129.165 | 11195.1
6654 | 329333 | -164791 | 40 | 38 | 239.35 | 30018.3
6655 | 415132 | -243289 | 40 | 38 | 287.506 | 32911.4
6656 | 457684 | -193835 | 43 | 39 | 270.525 | 41600.1
6657 | 494219 | -179884 | 45 | 40 | 292.28 | 64765.1
6658 | 466464 | -127564 | 48 | 42 | 263.943 | 66212.7
6659 | 450690 | -118711 | 49 | 42 | 249.377 | 66212
6660 | 421295 | -108219 | 49 | 42 | 246.086 | 66210.7
6661 | 479606 | -112065 | 50 | 41 | 267.739 | 66209.9
6662 | 492519 | -97730.1 | 50 | 41 | 273.381 | 64761.9
6663 | 475976 | -95548.8 | 48 | 40 | 290.684 | 58969.7
6664 | 476608 | -100853 | 48 | 40 | 288.732 | 48833.9
6665 | 431042 | -114482 | 48 | 40 | 249.534 | 37250.5
6666 | 357518 | -185639 | 46 | 38 | 204.036 | 22771.9
6667 | 188114 | 0 | 44 | 37 | 121.386 | 16257.3
6668 | 168625 | -6537.21 | 42 | 36 | 110.308 | 15535.2
6669 | 155050 | 0 | 41 | 35 | 91.9008 | 9738.05
6670 | 143924 | -16124.8 | 39 | 34 | 92.6077 | 9507.72
6671 | 138942 | -5105.6 | 35 | 33 | 84.2733 | 8292.87
6672 | 140436 | -7963.39 | 37 | 34 | 83.711 | 8295.3
6673 | 137138 | -5314.28 | 41 | 37 | 83.5648 | 8297.58
6674 | 135353 | -6456.12 | 38 | 36 | 83.4827 | 8299.41
6675 | 134485 | -11347.9 | 37 | 36 | 83.4426 | 8300.93
6676 | 137006 | -12334.4 | 37 | 36 | 89.2735 | 9200.01
6677 | 186850 | -14238.5 | 37 | 36 | 130.182 | 11200
6678 | 328341 | -312135 | 37 | 36 | 239.952 | 30023.4
6679 | 390126 | -302985 | 37 | 36 | 289.198 | 32917.1
6680 | 411532 | -254281 | 37 | 36 | 284.546 | 41604.9
6681 | 426286 | -242346 | 38 | 36 | 285.08 | 64770
6682 | 438063 | -227377 | 40 | 37 | 277.763 | 66218
6683 | 444714 | -212615 | 42 | 36 | 265.254 | 66217.2
6684 | 412455 | -190402 | 44 | 37 | 262.683 | 66216.3
6685 | 468859 | -180697 | 45 | 37 | 284.758 | 66215.6
6686 | 488538 | -136954 | 47 | 38 | 293.181 | 64766.5
6687 | 471799 | -125115 | 45 | 37 | 273.96 | 58973.7
6688 | 474442 | -128771 | 45 | 37 | 270.793 | 48837.6
6689 | 434444 | -158259 | 44 | 37 | 268.077 | 37254.1
6690 | 322049 | -211862 | 41 | 35 | 199.004 | 22775.6
6691 | 187170 | 0 | 38 | 34 | 117.772 | 16260.9
6692 | 167771 | 0 | 36 | 33 | 103.133 | 15538.7
6693 | 154156 | -10757.6 | 33 | 32 | 99.186 | 9742.37
6694 | 142997 | -8753.53 | 34 | 33 | 87.9349 | 9511.88
6695 | 138081 | -13306.3 | 35 | 34 | 86.7244 | 8296.88
6696 | 136117 | -13641.5 | 36 | 33 | 81.9254 | 8299.94
6697 | 135726 | -14414.3 | 40 | 35 | 82.1419 | 8302.51
6698 | 134309 | -13797.7 | 41 | 36 | 81.9123 | 8305.58
6699 | 133508 | -13425.4 | 41 | 36 | 81.7483 | 8308.08
6700 | 132748 | -13370.7 | 42 | 37 | 81.6755 | 8310.28
6701 | 132459 | -14171.3 | 42 | 37 | 81.7754 | 8312.31
6702 | 131276 | -13822.4 | 43 | 37 | 79.154 | 8314.29
6703 | 140882 | -406711 | 43 | 38 | 97.8349 | 8316.2
6704 | 195774 | -407702 | 45 | 39 | 96.0576 | 8317.88
6705 | 184342 | -331023 | 47 | 40 | 93.1735 | 8319.93
6706 | 187793 | -275785 | 51 | 43 | 90.2247 | 8318.49
6707 | 187857 | -228610 | 54 | 45 | 93.8697 | 8319.43
6708 | 188620 | -190758 | 56 | 47 | 94.369 | 8319.62
6709 | 183508 | -145173 | 60 | 50 | 88.4614 | 8320.09
6710 | 128003 | 0 | 61 | 52 | 71.7875 | 8320.27
6711 | 127482 | 0 | 61 | 51 | 71.5406 | 8320.5
6712 | 127388 | 0 | 61 | 51 | 72.7576 | 8320.26
6713 | 127384 | 0 | 58 | 52 | 76.4243 | 8319.7
6714 | 126779 | 0 | 58 | 51 | 79.1885 | 8319.55
6715 | 126588 | 0 | 57 | 50 | 79.419 | 8319.53
6716 | 126443 | 0 | 57 | 50 | 79.4124 | 8319.89
6717 | 128482 | -5023.64 | 54 | 48 | 83.9318 | 8320.39
6718 | 125710 | 0 | 51 | 46 | 78.5813 | 8320.96
6719 | 125371 | -1527.43 | 49 | 44 | 82.1929 | 8321.58
6720 | 125130 | 0 | 48 | 44 | 73.2612 | 3255.16
6721 | 124933 | -12492 | 48 | 45 | 80.7335 | 3256.09
6722 | 124533 | 0 | 48 | 45 | 73.2344 | 3257.47
6723 | 124298 | -14293 | 47 | 45 | 81.0115 | 3258.72
6724 | 123830 | -4914.63 | 45 | 43 | 77.6315 | 3260.11
6725 | 124377 | -10432.5 | 44 | 42 | 77.6554 | 3261.31
6726 | 123361 | -9725.16 | 45 | 42 | 75.2107 | 3262.71
6727 | 123649 | -11504 | 44 | 40 | 75.3365 | 3264.19
6728 | 122817 | -10956.4 | 43 | 39 | 73.855 | 3265.8
6729 | 133337 | -19163.8 | 43 | 39 | 77.4144 | 3267.34
6730 | 122407 | -11607.9 | 43 | 39 | 74.1329 | 3268.79
6731 | 133063 | -19581.4 | 43 | 39 | 77.0061 | 3270.59
6732 | 122008 | -11617.7 | 43 | 39 | 73.695 | 3272.04
6733 | 132863 | -19788.7 | 44 | 39 | 76.7783 | 3273.36
6734 | 153043 | -21400.1 | 41 | 38 | 80.883 | 3274.69
6735 | 132383 | -20746.8 | 41 | 37 | 77.1397 | 3275.77
6736 | 150022 | -24014 | 41 | 37 | 82.1876 | 3277.43
6737 | 130752 | -23515.8 | 41 | 37 | 83.1339 | 3278.73
6738 | 147125 | -25903 | 41 | 37 | 90.0403 | 3280.41
6739 | 144307 | -28099.1 | 40 | 36 | 90.1812 | 3282.06
6740 | 142974 | -32964.1 | 39 | 35 | 90.2851 | 3283.88
6741 | 141812 | -38326.8 | 39 | 34 | 90.4762 | 3285.7
6742 | 140827 | -47234.9 | 37 | 33 | 89.8692 | 3287.55
6743 | 139934 | -55271.7 | 36 | 33 | 89.0619 | 3289.41
6744 | 139011 | -65490.4 | 35 | 32 | 86.9663 | 3291.26
6745 | 138306 | -74292.6 | 34 | 31 | 87.2466 | 3293.06
6746 | 137676 | -83405.3 | 33 | 31 | 87.2238 | 3294.86
6747 | 136971 | -91297.7 | 32 | 29 | 87.11 | 3296.66
6748 | 136372 | -99968.5 | 31 | 29 | 87.0215 | 3298.47
6749 | 135767 | -105049 | 31 | 29 | 86.9312 | 3300.3
6750 | 135097 | -113871 | 30 | 27 | 84.4482 | 3302.15
6751 | 134833 | -107333 | 31 | 28 | 82.2868 | 3303.98
6752 | 136363 | -87640.4 | 33 | 29 | 80.8753 | 3305.82
6753 | 137530 | -66590.1 | 36 | 30 | 81.3422 | 3307.6
6754 | 139403 | -50480.9 | 39 | 32 | 81.5422 | 3309.16
6755 | 140631 | -43990.8 | 40 | 32 | 81.4841 | 3309.8
6756 | 141464 | -38436 | 42 | 34 | 80.947 | 3310.06
6757 | 144076 | -35183 | 43 | 35 | 80.9081 | 3310.16
6758 | 142879 | -30396.7 | 43 | 35 | 80.3846 | 3310.57
6759 | 131130 | -27601.6 | 43 | 35 | 77.4438 | 3310.87
6760 | 130295 | -27506 | 43 | 35 | 78.5926 | 3311.15
6761 | 143096 | -28947.8 | 43 | 35 | 85.2055 | 3311.58
6762 | 140196 | -31401.5 | 40 | 33 | 89.8563 | 3312.2
6763 | 137874 | -39067.3 | 38 | 32 | 90.1237 | 3313.15
6764 | 136110 | -49438.7 | 35 | 31 | 90.4802 | 3314.37
6765 | 134847 | -57277.6 | 37 | 31 | 90.5878 | 3315.74
6766 | 134130 | -68496.7 | 33 | 29 | 90.2015 | 3317.09
6767 | 136662 | -74615.6 | 30 | 27 | 89.7221 | 3318.56
6768 | 132588 | -71196.4 | 30 | 27 | 90.9586 | 8387.3
6769 | 133541 | -85295.4 | 28 | 26 | 91.3143 | 8388.77
6770 | 131851 | -90004.4 | 27 | 25 | 90.9269 | 8388.93
6771 | 132040 | -97693.1 | 26 | 25 | 91.0487 | 8389.58
6772 | 134324 | -103371 | 25 | 24 | 95.1962 | 9287.82
6773 | 182046 | -90732.6 | 25 | 24 | 135.995 | 11286.4
6774 | 313011 | -809595 | 24 | 23 | 261.462 | 30108.5
6775 | 375570 | -745773 | 25 | 23 | 283.499 | 33001.1
6776 | 394888 | -564784 | 28 | 26 | 267.415 | 41671.4
6777 | 393655 | -436329 | 34 | 30 | 263.51 | 64833.1
6778 | 399084 | -361279 | 39 | 33 | 275.252 | 66278.4
6779 | 411273 | -311693 | 42 | 35 | 262.418 | 66275.8
6780 | 391264 | -253838 | 45 | 36 | 242.365 | 66272.8
6781 | 453982 | -218004 | 47 | 36 | 264.813 | 66269
6782 | 466868 | -170184 | 49 | 39 | 273.208 | 64816.8
6783 | 465019 | -146927 | 49 | 40 | 274.389 | 59021.2
6784 | 447221 | -158651 | 48 | 40 | 269.735 | 48882.5
6785 | 416719 | -196033 | 47 | 38 | 248.246 | 37296.3
6786 | 332552 | -280490 | 43 | 35 | 182.484 | 22815.2
6787 | 179588 | 0 | 37 | 32 | 117.434 | 16298.4
6788 | 160674 | -12070.1 | 37 | 32 | 111.308 | 15575.2
6789 | 147483 | -8772.02 | 36 | 31 | 96.1305 | 9784.4
6790 | 136602 | -14561.6 | 36 | 32 | 90.5552 | 9555.27
6791 | 131928 | -14429.6 | 35 | 31 | 86.7566 | 8341.71
6792 | 139795 | -25727.6 | 34 | 30 | 89.649 | 8344.6
6793 | 154091 | -30332.1 | 35 | 31 | 92.8873 | 8347.18
6794 | 150944 | -34509 | 33 | 30 | 93.174 | 8349.75
6795 | 148502 | -36455.1 | 34 | 30 | 92.7971 | 8352.31
6796 | 150402 | -47907.4 | 34 | 30 | 97.1466 | 9252.04
6797 | 191004 | -28392.4 | 37 | 32 | 134.893 | 11252.1
6798 | 322797 | -493472 | 36 | 31 | 241.128 | 30075.4
6799 | 385058 | -460064 | 37 | 32 | 269.427 | 32968.6
6800 | 415206 | -356643 | 39 | 33 | 265.945 | 41647.6
6801 | 432702 | -308174 | 41 | 35 | 285.886 | 64809.6
6802 | 436638 | -319584 | 42 | 36 | 278.713 | 66254.7
6803 | 434099 | -290164 | 44 | 38 | 265.227 | 66252.5
6804 | 402977 | -258348 | 45 | 38 | 262.146 | 66250.3
6805 | 444853 | -206719 | 48 | 41 | 283.988 | 66247.8
6806 | 463875 | -172742 | 50 | 42 | 292.511 | 64797.3
6807 | 457588 | -154877 | 50 | 42 | 293.547 | 59002.5
6808 | 468229 | -203985 | 47 | 41 | 295.549 | 48864.7
6809 | 442950 | -242403 | 45 | 42 | 277.458 | 37279.5
6810 | 356025 | -309646 | 44 | 43 | 203.998 | 22799.6
6811 | 184620 | 0 | 43 | 43 | 117.682 | 16283.8
6812 | 165242 | -9548.45 | 43 | 43 | 111.363 | 15560.5
6813 | 151846 | 0 | 43 | 43 | 91.7542 | 9768.09
6814 | 140794 | -16838.7 | 43 | 43 | 92.5456 | 9538.72
6815 | 136032 | -5868.92 | 43 | 43 | 84.141 | 8324.58
6816 | 136616 | -11564.8 | 43 | 43 | 83.4192 | 8327.05
6817 | 133748 | -9567.11 | 44 | 44 | 83.2918 | 8329.21
6818 | 133285 | -10909.7 | 44 | 44 | 85.2662 | 8331.07
6819 | 132098 | -10759 | 43 | 43 | 85.0521 | 8332.73
6820 | 138466 | -11680.2 | 43 | 43 | 89.4257 | 9231.84
6821 | 181477 | -8573.74 | 43 | 43 | 129.282 | 11231.2
6822 | 327069 | -298026 | 44 | 44 | 240.6 | 30054
6823 | 462405 | -331042 | 44 | 44 | 296.55 | 32946.8
6824 | 471113 | -247687 | 45 | 44 | 291.448 | 41628.3
6825 | 463916 | -181691 | 49 | 45 | 272.334 | 64791.3
6826 | 439306 | -124108 | 53 | 48 | 263.323 | 66237.1
6827 | 441981 | -87309.2 | 56 | 48 | 248.93 | 66234.3
6828 | 460902 | -62382.8 | 58 | 49 | 245.767 | 66231.1
6829 | 479757 | -39820.8 | 58 | 50 | 262.372 | 66228.9
6830 | 513519 | -40797.3 | 56 | 51 | 269.547 | 64779.6
6831 | 507561 | -30976.6 | 56 | 51 | 286.914 | 58986.4
6832 | 468124 | -45949.8 | 53 | 49 | 264.128 | 48849.6
6833 | 420079 | -68257.2 | 52 | 49 | 245.143 | 37265.4
6834 | 342208 | -167161 | 48 | 46 | 182.484 | 22786.1
6835 | 187330 | 0 | 46 | 45 | 117.794 | 16270.9
6836 | 167820 | 0 | 44 | 44 | 103.135 | 15548.2
6837 | 154268 | -6855.13 | 43 | 43 | 99.1327 | 9752.88
6838 | 143060 | 0 | 42 | 42 | 83.3624 | 9522.63
6839 | 141990 | -2225.99 | 40 | 40 | 84.4089 | 8307.71
6840 | 136581 | 0 | 40 | 40 | 79.1123 | 8309.57
6841 | 139682 | -3425.66 | 38 | 38 | 83.6755 | 8311.13
6842 | 136759 | -3909.64 | 38 | 38 | 83.5473 | 8312.6
6843 | 137625 | -4892.44 | 38 | 38 | 83.5837 | 8313.79
6844 | 136490 | -8642.77 | 39 | 39 | 88.9889 | 9212.75
6845 | 182667 | -6445.88 | 39 | 39 | 126.868 | 11212.7
6846 | 328100 | -288244 | 40 | 40 | 240.402 | 30035.7
6847 | 414355 | -302156 | 40 | 40 | 292.634 | 32928.5
6848 | 435916 | -252156 | 40 | 40 | 296.431 | 41613.5
6849 | 450831 | -264082 | 41 | 41 | 289.331 | 64778
6850 | 458913 | -266490 | 42 | 42 | 280.919 | 66224.7
6851 | 459842 | -230908 | 44 | 44 | 267.222 | 66223.8
6852 | 416543 | -172402 | 47 | 46 | 263.938 | 66223.2
6853 | 456055 | -116575 | 51 | 49 | 266.471 | 66222.4
6854 | 557328 | -57907.3 | 57 | 54 | 281.19 | 64773.1
6855 | 620188 | -21796.4 | 61 | 56 | 291.853 | 58979.9
6856 | 639441 | -16531.2 | 63 | 56 | 289.805 | 48843.2
6857 | 472691 | -13113.9 | 59 | 54 | 241.139 | 37259
6858 | 331328 | -24628 | 54 | 51 | 179.556 | 22779.7
6859 | 188142 | 0 | 52 | 50 | 117.823 | 16264.4
6860 | 168401 | 0 | 49 | 48 | 103.162 | 15541.8
6861 | 154939 | 0 | 47 | 46 | 91.8957 | 9744.83
6862 | 143874 | 0 | 46 | 45 | 83.3993 | 9513.61
6863 | 139081 | -7412.34 | 46 | 45 | 86.8342 | 8298.34
6864 | 137191 | 0 | 46 | 45 | 75.085 | 8300.26
6865 | 136220 | -12070.7 | 45 | 45 | 82.8702 | 8302.06
6866 | 135148 | 0 | 44 | 44 | 74.9917 | 8304.46
6867 | 134130 | -14522.5 | 41 | 41 | 83.1149 | 8306.25
6868 | 133400 | -4215.31 | 40 | 40 | 79.341 | 8308.16
6869 | 134666 | -10985 | 39 | 39 | 81.3089 | 8309.8
6870 | 131889 | -9275.94 | 39 | 39 | 78.4891 | 8311.7
6871 | 139312 | -371596 | 41 | 41 | 96.0035 | 8313.59
6872 | 205695 | -401272 | 42 | 42 | 95.4548 | 8315.36
6873 | 188659 | -301705 | 45 | 45 | 90.11 | 8317.54
6874 | 193478 | -233064 | 50 | 48 | 93.3738 | 8316.79
6875 | 189969 | -155870 | 58 | 52 | 88.8034 | 8317.89
6876 | 221987 | -110182 | 64 | 56 | 93.8185 | 8318.28
6877 | 280282 | -93071 | 68 | 57 | 94.9842 | 8318.13
6878 | 162771 | 0 | 68 | 58 | 78.5184 | 8317.79
6879 | 161881 | 0 | 70 | 58 | 79.7725 | 8317.41
6880 | 163470 | 0 | 70 | 58 | 79.5601 | 8316.17
6881 | 127836 | 0 | 67 | 57 | 73.4044 | 8314.11
6882 | 127430 | 0 | 62 | 54 | 78.0891 | 8312.95
6883 | 127344 | 0 | 59 | 53 | 78.9467 | 8312
6884 | 127117 | 0 | 56 | 52 | 79.443 | 8311.68
6885 | 126793 | 0 | 54 | 51 | 79.4284 | 8311.81
6886 | 126469 | 0 | 53 | 50 | 78.6137 | 8312.24
6887 | 126257 | 0 | 53 | 50 | 77.8041 | 8312.83
6888 | 125922 | 0 | 52 | 50 | 73.2971 | 3246.3
6889 | 125493 | -7359.2 | 51 | 49 | 79.7002 | 3247.08
6890 | 125158 | 0 | 50 | 48 | 73.2626 | 3248.05
6891 | 124962 | -9317.62 | 49 | 48 | 80.0363 | 3249.03
6892 | 124513 | 0 | 49 | 47 | 73.2335 | 3250.15
6893 | 124400 | -11348.2 | 48 | 47 | 80.4168 | 3251.17
6894 | 123898 | 0 | 47 | 45 | 70.8058 | 3252.35
6895 | 123911 | -13290.8 | 48 | 46 | 76.4555 | 3253.45
6896 | 123767 | 0 | 51 | 48 | 67.1695 | 3254.7
6897 | 123637 | -12163.1 | 55 | 50 | 74.7843 | 3255.89
6898 | 123676 | 0 | 60 | 53 | 67.4412 | 3256.85
6899 | 130428 | -1779.75 | 65 | 55 | 73.6618 | 3256.39
6900 | 152088 | -1148.15 | 69 | 57 | 74.6206 | 3255.39
6901 | 167900 | -741.86 | 72 | 57 | 75.304 | 3253.81
6902 | 169829 | 0 | 72 | 58 | 74.1525 | 3252.45
6903 | 167862 | 0 | 72 | 59 | 74.059 | 3250.79
6904 | 166178 | 0 | 71 | 59 | 74.8592 | 3249.03
6905 | 123604 | 0 | 69 | 57 | 72.2631 | 3247.41
6906 | 123660 | 0 | 65 | 55 | 76.192 | 3246.09
6907 | 123676 | 0 | 59 | 53 | 75.8937 | 3245.24
6908 | 123627 | 0 | 58 | 53 | 77.1512 | 3244.85
6909 | 123560 | 0 | 58 | 53 | 77.1481 | 3244.82
6910 | 123396 | 0 | 57 | 52 | 76.3408 | 3244.92
6911 | 123386 | 0 | 56 | 52 | 75.5403 | 3244.97
6912 | 123403 | 0 | 53 | 50 | 78.5118 | 8312.68
6913 | 123314 | 0 | 52 | 49 | 78.5079 | 8313.1
6914 | 123252 | 0 | 52 | 49 | 78.505 | 8312.82
6915 | 123213 | 0 | 53 | 50 | 78.5032 | 8312.73
6916 | 129857 | -7907.07 | 53 | 50 | 88.618 | 9210.38
6917 | 198589 | -3563.52 | 52 | 49 | 127.589 | 22096.5
6918 | 319726 | -69931 | 52 | 49 | 240.94 | 65113.4
6919 | 432467 | -100825 | 52 | 49 | 273.925 | 79039.5
6920 | 473657 | -66638.1 | 55 | 50 | 271.797 | 109345
6921 | 533328 | -24456.6 | 61 | 52 | 273.47 | 128631
6922 | 667179 | -41503.6 | 63 | 54 | 275.175 | 131381
6923 | 718781 | -42053 | 68 | 55 | 265.183 | 131380
6924 | 873428 | -58718.7 | 73 | 58 | 276.407 | 131380
6925 | 980033 | -44503.2 | 75 | 59 | 297.831 | 131380
6926 | 1048960 | -36428.2 | 76 | 60 | 306.879 | 129686
6927 | 1131370 | -41673.6 | 76 | 61 | 313.755 | 117912
6928 | 1022240 | -19934.2 | 75 | 60 | 299.083 | 96277.8
6929 | 874512 | -9966.45 | 73 | 60 | 268.939 | 72240.2
6930 | 502170 | -7831.19 | 69 | 57 | 184.315 | 44786.3
6931 | 185862 | 0 | 67 | 56 | 117.685 | 32087.1
6932 | 166210 | 0 | 66 | 56 | 103.07 | 28496.7
6933 | 152783 | 0 | 65 | 54 | 91.7413 | 17542.2
6934 | 142210 | 0 | 64 | 54 | 83.215 | 9505.7
6935 | 137513 | 0 | 63 | 54 | 79.4832 | 8288.52
6936 | 136141 | 0 | 61 | 54 | 78.1886 | 8288.74
6937 | 135241 | 0 | 59 | 53 | 78.3688 | 8288.93
6938 | 134518 | 0 | 57 | 52 | 78.5903 | 8289.09
6939 | 134071 | 0 | 57 | 53 | 78.5698 | 8289.28
6940 | 137034 | 0 | 54 | 52 | 82.5916 | 9187.21
6941 | 183341 | 0 | 51 | 49 | 122.323 | 22073.2
6942 | 361706 | -30703.8 | 52 | 50 | 246.255 | 65090.2
6943 | 440651 | -25875.2 | 50 | 49 | 266.532 | 79016.3
6944 | 578108 | -25445.7 | 56 | 53 | 267.037 | 109331
6945 | 598967 | -14270.4 | 57 | 53 | 267.586 | 128618
6946 | 680457 | -18381 | 61 | 54 | 268.806 | 131370
6947 | 749474 | -27988.3 | 65 | 56 | 263.176 | 131369
6948 | 822592 | -44988.4 | 68 | 56 | 284.998 | 131369
6949 | 762226 | -8289.67 | 67 | 56 | 295.771 | 131370
6950 | 744658 | -8251.21 | 66 | 55 | 301.381 | 129676
6951 | 730560 | -8054.94 | 65 | 54 | 301.881 | 117902
6952 | 705052 | -8003.47 | 63 | 54 | 296.345 | 96266.9
6953 | 581629 | -7668.14 | 60 | 53 | 277.688 | 72229
6954 | 365287 | -8036.47 | 57 | 52 | 178.741 | 44776.1
6955 | 189527 | 0 | 55 | 51 | 117.912 | 32078.7
6956 | 169697 | 0 | 54 | 50 | 103.222 | 28489.6
6957 | 156400 | 0 | 53 | 50 | 91.9624 | 17534.8
6958 | 145064 | 0 | 50 | 48 | 83.4537 | 9499.17
6959 | 140158 | 0 | 48 | 47 | 79.753 | 8282.64
6960 | 138520 | 0 | 47 | 46 | 79.1975 | 8283.67
6961 | 137428 | 0 | 45 | 44 | 79.1475 | 8284.4
6962 | 136543 | 0 | 44 | 43 | 79.1072 | 8285.14
6963 | 135757 | 0 | 45 | 43 | 79.0714 | 8285.79
6964 | 138489 | -1672.71 | 44 | 42 | 87.2334 | 9184.15
6965 | 184531 | 0 | 42 | 40 | 122.379 | 22070.5
6966 | 329766 | -62994.4 | 41 | 39 | 239.448 | 65088.6
6967 | 424304 | -142645 | 39 | 38 | 272.718 | 79015.5
6968 | 496815 | -131175 | 45 | 42 | 275.571 | 109329
6969 | 516537 | -92973.5 | 48 | 42 | 270.823 | 128618
6970 | 509759 | -63946.5 | 50 | 42 | 272.362 | 131369
6971 | 531138 | -51540.1 | 53 | 43 | 250.405 | 131368
6972 | 568621 | -46109.1 | 56 | 44 | 252.945 | 131368
6973 | 573142 | -14928.7 | 57 | 44 | 268.264 | 131369
6974 | 592743 | -12642.7 | 56 | 43 | 291.313 | 129674
6975 | 544292 | -14161.4 | 53 | 42 | 289.632 | 117901
6976 | 523255 | -16640 | 53 | 42 | 284.022 | 96266
6977 | 429991 | -30922.8 | 51 | 41 | 264.542 | 72228.2
6978 | 343675 | -78685.5 | 49 | 40 | 181.669 | 44775.3
6979 | 189054 | 0 | 47 | 38 | 117.874 | 32078.1
6980 | 169455 | 0 | 44 | 36 | 103.211 | 28489.3
6981 | 155935 | -5089.2 | 42 | 36 | 98.7313 | 17536.1
6982 | 144631 | 0 | 42 | 36 | 83.4339 | 9501.3
6983 | 139727 | -12262.5 | 41 | 35 | 87.9406 | 8285.76
6984 | 138011 | 0 | 41 | 35 | 79.0555 | 8287.88
6985 | 137019 | -16508.8 | 39 | 34 | 87.8523 | 8289.66
6986 | 136018 | -3993.89 | 38 | 33 | 83.3933 | 8291.59
6987 | 137256 | -10621 | 38 | 33 | 85.2048 | 8293.34
6988 | 137763 | -8897.75 | 39 | 34 | 88.8555 | 9192.86
6989 | 189763 | -11584.3 | 39 | 34 | 129.462 | 22080.2
6990 | 328919 | -237538 | 38 | 33 | 239.226 | 65098.6
6991 | 399211 | -237962 | 38 | 33 | 272.823 | 79025.9
6992 | 420614 | -214555 | 38 | 33 | 270.987 | 109335
6993 | 446952 | -208908 | 40 | 34 | 268.123 | 128622
6994 | 464330 | -194165 | 43 | 36 | 261.673 | 131374
6995 | 481746 | -171260 | 45 | 37 | 250.197 | 131374
6996 | 403170 | -149148 | 44 | 36 | 243.376 | 131374
6997 | 463956 | -163303 | 43 | 35 | 266.274 | 131373
6998 | 499862 | -151929 | 44 | 36 | 274.287 | 129678
6999 | 477590 | -144499 | 43 | 35 | 274.161 | 117904
7000 | 476885 | -165497 | 42 | 35 | 270.161 | 96269.8
7001 | 411423 | -190350 | 40 | 33 | 252.587 | 72233.1
7002 | 322896 | -242281 | 39 | 34 | 185.855 | 44780.8
7003 | 187353 | 0 | 39 | 34 | 117.781 | 32083.8
7004 | 167993 | -11776 | 39 | 33 | 112.398 | 28494.7
7005 | 154383 | 0 | 39 | 32 | 91.8704 | 17543.8
7006 | 143194 | -19788 | 37 | 31 | 92.779 | 9510.06
7007 | 138361 | -7000.83 | 37 | 31 | 84.2468 | 8295.35
7008 | 139403 | -14621.4 | 37 | 31 | 86.5414 | 8297.84
7009 | 135663 | -12405.6 | 36 | 30 | 85.8975 | 8300.33
7010 | 134794 | -14424.1 | 35 | 30 | 85.9969 | 8302.61
7011 | 133891 | -15202.4 | 35 | 30 | 86.0989 | 8304.77
7012 | 147981 | -25619.9 | 34 | 29 | 93.3907 | 9204.47
7013 | 206367 | -20186 | 34 | 30 | 134.496 | 22092.2
7014 | 327634 | -389702 | 34 | 29 | 239.729 | 65111.2
7015 | 389571 | -370927 | 34 | 30 | 272.074 | 79039.1
7016 | 407851 | -305348 | 35 | 30 | 270.625 | 109346
7017 | 409007 | -291055 | 36 | 30 | 284.544 | 128633
7018 | 431736 | -279654 | 40 | 33 | 278.105 | 131384
7019 | 438483 | -241731 | 43 | 36 | 265.497 | 131384
7020 | 409924 | -199414 | 45 | 37 | 262.758 | 131383
7021 | 451937 | -136803 | 49 | 38 | 265.281 | 131381
7022 | 478047 | -93021.5 | 52 | 40 | 275.277 | 129685
7023 | 479153 | -63021.5 | 53 | 42 | 273.639 | 117910
7024 | 478189 | -53093.5 | 54 | 43 | 266.862 | 96274.9
7025 | 434025 | -62318.5 | 54 | 43 | 255.669 | 72237.2
7026 | 343065 | -102223 | 53 | 43 | 182.959 | 44783.8
7027 | 188096 | 0 | 52 | 43 | 117.83 | 32086.2
7028 | 168415 | 0 | 52 | 43 | 103.163 | 28496.9
7029 | 155057 | 0 | 52 | 43 | 91.901 | 17545.6
7030 | 143983 | -6383.37 | 51 | 43 | 90.1899 | 9510.92
7031 | 138991 | 0 | 49 | 42 | 79.7 | 8295.42
7032 | 137184 | -1598.12 | 46 | 41 | 79.5134 | 8297.09
7033 | 136083 | 0 | 45 | 40 | 75.0341 | 8298.7
7034 | 135525 | -12529.3 | 48 | 43 | 82.9069 | 8300.75
7035 | 134458 | 0 | 50 | 43 | 74.9604 | 8302.64
7036 | 133698 | -2931.04 | 47 | 41 | 79.3545 | 8304.31
7037 | 132923 | 0 | 47 | 40 | 74.8906 | 8305.55
7038 | 132182 | -15002.6 | 46 | 39 | 80.5666 | 8307.04
7039 | 144543 | -294709 | 44 | 37 | 87.8599 | 8308.59
7040 | 207685 | -327676 | 44 | 37 | 90.2547 | 8310.01
7041 | 196013 | -285070 | 45 | 38 | 88.9388 | 8312.52
7042 | 201938 | -294062 | 46 | 39 | 90.8624 | 8312.53
7043 | 198216 | -277696 | 46 | 39 | 89.2704 | 8313.62
7044 | 199002 | -265218 | 47 | 40 | 88.1833 | 8314.37
7045 | 198151 | -259256 | 48 | 40 | 88.4314 | 8315.21
7046 | 127635 | 0 | 48 | 40 | 71.5261 | 8315.89
7047 | 127273 | -8274.22 | 47 | 40 | 76.8588 | 8316.72
7048 | 126891 | 0 | 46 | 39 | 73.0946 | 8317.05
7049 | 126573 | -13928 | 46 | 39 | 84.4185 | 8318.04
7050 | 126203 | 0 | 45 | 39 | 79.3933 | 8319.1
7051 | 125844 | -16516.3 | 45 | 39 | 87.8752 | 8320.35
7052 | 125508 | -5564.43 | 45 | 38 | 83.7991 | 8321.8
7053 | 127702 | -11015.8 | 44 | 38 | 83.8964 | 8323.18
7054 | 124810 | -9520.17 | 40 | 36 | 82.9695 | 8324.71
7055 | 124385 | -11801.7 | 38 | 35 | 84.0672 | 8326.22
7056 | 133982 | -22515.2 | 35 | 33 | 83.1858 | 3260.52
7057 | 128520 | -16325.9 | 35 | 33 | 80.9445 | 3262.29
7058 | 149685 | -26472.3 | 33 | 31 | 86.0956 | 3264.77
7059 | 147157 | -41100.5 | 32 | 31 | 87.4178 | 3267.02
7060 | 145132 | -48350.5 | 30 | 30 | 87.2785 | 3268.86
7061 | 143608 | -58136.7 | 31 | 30 | 87.6693 | 3271.7
7062 | 142646 | -68950.5 | 31 | 30 | 85.1473 | 3274.1
7063 | 141749 | -72081.3 | 30 | 29 | 83.3863 | 3276.62
7064 | 147284 | -64820.2 | 33 | 32 | 82.8483 | 3279.02
7065 | 141423 | -48834.2 | 36 | 34 | 81.7061 | 3281.24
7066 | 141416 | -42796.7 | 38 | 35 | 81.0259 | 3283.26
7067 | 142621 | -41379.5 | 40 | 37 | 81.6165 | 3284.56
7068 | 128166 | -29966.4 | 42 | 38 | 78.0979 | 3285.95
7069 | 143192 | -30134.3 | 44 | 38 | 80.9241 | 3287.47
7070 | 134202 | -17535.3 | 44 | 38 | 77.528 | 3288.8
7071 | 127757 | -24735.4 | 43 | 37 | 77.4823 | 3290.02
7072 | 144913 | -27038.9 | 44 | 37 | 82.3674 | 3290.9
7073 | 120207 | -13061 | 44 | 37 | 80.3929 | 3291.98
7074 | 140996 | -35199.2 | 42 | 37 | 89.9554 | 3293.24
7075 | 139313 | -40507.3 | 41 | 36 | 89.7478 | 3294.21
7076 | 138767 | -45990.6 | 41 | 36 | 90.076 | 3295.8
7077 | 139856 | -48655.7 | 41 | 36 | 90.321 | 3297.35
7078 | 137560 | -44111.3 | 40 | 36 | 88.295 | 3298.88
7079 | 142753 | -57417.9 | 39 | 35 | 89.2009 | 3300.32
7080 | 137020 | -46894.2 | 40 | 36 | 90.3962 | 8368.69
7081 | 139231 | -62383.7 | 39 | 36 | 92.1666 | 8370.13
7082 | 136635 | -60213.9 | 39 | 36 | 91.3923 | 8370.29
7083 | 141243 | -73251.5 | 36 | 32 | 92.4828 | 8371.45
7084 | 139099 | -69861.3 | 34 | 32 | 94.5451 | 9270.09
7085 | 204086 | -70081.9 | 32 | 30 | 138.967 | 22156.8
7086 | 314893 | -633360 | 30 | 29 | 250.058 | 65174.1
7087 | 377441 | -603431 | 30 | 29 | 277.417 | 79101.3
7088 | 396671 | -417203 | 34 | 32 | 265.544 | 109394
7089 | 424443 | -331230 | 39 | 35 | 285.787 | 128678
7090 | 448068 | -300186 | 43 | 37 | 279.402 | 131427
7091 | 437689 | -275278 | 44 | 37 | 246.243 | 131424
7092 | 393938 | -204102 | 48 | 39 | 243.534 | 131420
7093 | 462354 | -208250 | 46 | 37 | 265.263 | 131417
7094 | 479222 | -167733 | 48 | 39 | 273.978 | 129720
7095 | 464590 | -142469 | 48 | 39 | 274.249 | 117943
7096 | 450348 | -129024 | 50 | 41 | 271.018 | 96306.2
7097 | 416838 | -179978 | 47 | 40 | 250.456 | 72266.8
7098 | 342023 | -266147 | 44 | 38 | 184.315 | 44811.4
7099 | 180637 | 0 | 41 | 36 | 117.489 | 32112.5
7100 | 161562 | -8841 | 39 | 36 | 110.844 | 28522.7
7101 | 148357 | 0 | 39 | 36 | 91.5949 | 17576.2
7102 | 137448 | -19638 | 39 | 36 | 92.3183 | 9543.19
7103 | 132772 | -9407.45 | 38 | 35 | 83.9931 | 8329.37
7104 | 132842 | -15728.6 | 37 | 35 | 86.0126 | 8332.06
7105 | 130488 | -14551 | 37 | 34 | 85.4669 | 8334.59
7106 | 138658 | -26374.1 | 37 | 34 | 89.1136 | 8336.76
7107 | 145658 | -20879.1 | 37 | 34 | 89.1228 | 8338.86
7108 | 153693 | -34012.1 | 36 | 33 | 96.5294 | 9238.81
7109 | 193415 | -24185.8 | 35 | 33 | 134.382 | 22126.4
7110 | 323504 | -453881 | 36 | 33 | 239.981 | 65145
7111 | 385829 | -427998 | 37 | 34 | 271.404 | 79072.4
7112 | 414964 | -319873 | 39 | 35 | 286.08 | 109373
7113 | 459762 | -262732 | 44 | 38 | 289.199 | 128658
7114 | 440955 | -203011 | 48 | 41 | 261.419 | 131408
7115 | 426244 | -134958 | 54 | 44 | 248.826 | 131405
7116 | 428235 | -82632.3 | 58 | 46 | 249.275 | 131403
7117 | 507089 | -40026.3 | 61 | 49 | 266.531 | 131399
7118 | 605332 | -23814 | 65 | 51 | 280.543 | 129702
7119 | 665416 | -21462.5 | 66 | 53 | 281.86 | 117926
7120 | 651226 | -15976.5 | 67 | 54 | 276.342 | 96290
7121 | 501694 | -11831.5 | 63 | 52 | 248.05 | 72251.6
7122 | 325320 | -18690.2 | 58 | 50 | 178.342 | 44797.3
7123 | 187005 | 0 | 57 | 50 | 117.767 | 32098.8
7124 | 167212 | 0 | 55 | 49 | 103.108 | 28508.9
7125 | 153883 | 0 | 56 | 49 | 91.8473 | 17558.5
7126 | 142983 | 0 | 55 | 49 | 83.3586 | 9523.7
7127 | 138050 | 0 | 53 | 48 | 79.6572 | 8308.11
7128 | 136603 | 0 | 55 | 49 | 79.1103 | 8309.48
7129 | 135866 | 0 | 55 | 50 | 79.0763 | 8310.62
7130 | 134832 | 0 | 55 | 49 | 79.0297 | 8311.42
7131 | 134536 | -5713.98 | 59 | 50 | 85.3208 | 8312.32
7132 | 137480 | 0 | 60 | 50 | 82.6119 | 9210.62
7133 | 184615 | 0 | 60 | 51 | 122.382 | 22096.8
7134 | 354339 | -49910.1 | 59 | 49 | 245.755 | 65113.9
7135 | 452295 | -31644.3 | 60 | 50 | 267.379 | 79039.7
7136 | 498722 | -21132.8 | 61 | 50 | 272.354 | 109345
7137 | 545854 | -15827.3 | 62 | 51 | 272.27 | 128632
7138 | 619927 | -29666.4 | 63 | 52 | 267.204 | 131382
7139 | 669549 | -31532.5 | 66 | 54 | 256.905 | 131381
7140 | 792335 | -51329.9 | 70 | 56 | 284.324 | 131380
7141 | 882070 | -34502.4 | 73 | 56 | 305.968 | 131380
7142 | 913177 | -25706.1 | 73 | 56 | 312.39 | 129686
7143 | 938899 | -30127.6 | 72 | 56 | 314.47 | 117913
7144 | 861736 | -12746.6 | 71 | 56 | 305.664 | 96278.2
7145 | 684098 | -6048.21 | 68 | 55 | 277.693 | 72240.5
7146 | 434966 | -5798.87 | 65 | 54 | 180.793 | 44786.5
7147 | 190545 | 0 | 62 | 53 | 117.328 | 32087.1
7148 | 170335 | 0 | 59 | 51 | 102.736 | 28497.5
7149 | 157105 | 0 | 58 | 51 | 91.9946 | 17543.5
7150 | 146006 | 0 | 60 | 52 | 83.4964 | 9507.62
7151 | 140897 | 0 | 60 | 51 | 79.7867 | 8291.04
7152 | 139494 | 0 | 59 | 51 | 79.1226 | 8291.9
7153 | 138385 | 0 | 58 | 50 | 79.072 | 8292.51
7154 | 137679 | 0 | 56 | 50 | 79.0397 | 8293.01
7155 | 136652 | 0 | 55 | 49 | 78.9933 | 8293.44
7156 | 139638 | 0 | 53 | 48 | 82.7099 | 9191.55
7157 | 186088 | 0 | 51 | 47 | 122.45 | 22077.7
7158 | 336951 | -41553.1 | 48 | 45 | 242.148 | 65094.9
7159 | 437985 | -71525 | 48 | 45 | 272.774 | 79021.2
7160 | 487202 | -86852.9 | 50 | 46 | 276.323 | 109333
7161 | 502086 | -63381.5 | 53 | 48 | 271.185 | 128621
7162 | 518849 | -33510.7 | 56 | 50 | 261.389 | 131372
7163 | 588991 | -23585.9 | 61 | 53 | 262.031 | 131372
7164 | 692153 | -34252.1 | 66 | 55 | 276.348 | 131372
7165 | 726298 | -8756.02 | 68 | 55 | 294.552 | 131372
7166 | 846703 | -8493.74 | 68 | 57 | 307.428 | 129677
7167 | 931433 | -9030.03 | 70 | 58 | 314.133 | 117904
7168 | 774557 | -7459.06 | 68 | 56 | 300.374 | 96269.6
7169 | 635085 | -6503.86 | 65 | 54 | 278.807 | 72232.4
7170 | 407062 | -6297.94 | 62 | 53 | 179.152 | 44777.9
7171 | 190895 | 0 | 58 | 51 | 117.487 | 32080.3
7172 | 171156 | 0 | 56 | 51 | 103.289 | 28491
7173 | 157353 | 0 | 54 | 49 | 92.0064 | 17536.2
7174 | 146360 | 0 | 54 | 49 | 83.5125 | 9500.18
7175 | 141477 | 0 | 53 | 49 | 79.8129 | 8283.28
7176 | 139769 | 0 | 53 | 49 | 79.2543 | 8284.44
7177 | 138794 | 0 | 52 | 49 | 79.2095 | 8285.33
7178 | 137854 | 0 | 51 | 49 | 79.1667 | 8286.24
7179 | 136968 | 0 | 51 | 49 | 79.1264 | 8287.05
7180 | 139838 | 0 | 52 | 49 | 82.7191 | 9185.5
7181 | 193513 | -5238.51 | 52 | 49 | 130.105 | 22071.9
7182 | 353295 | -27652.1 | 52 | 48 | 239.25 | 65089.3
7183 | 468244 | -79226.5 | 51 | 48 | 278.408 | 79015.7
7184 | 499156 | -69356.1 | 52 | 48 | 276.229 | 109329
7185 | 512887 | -52858.8 | 54 | 50 | 271.704 | 128617
7186 | 507989 | -30346.5 | 56 | 52 | 260.915 | 131368
7187 | 482656 | -26863.6 | 57 | 52 | 262.095 | 131368
7188 | 525226 | -12289.3 | 61 | 54 | 263.446 | 131368
7189 | 690528 | -10029.9 | 62 | 56 | 290.78 | 131368
7190 | 736051 | -9373.63 | 64 | 57 | 300.22 | 129674
7191 | 774837 | -11015.5 | 65 | 56 | 303.683 | 117900
7192 | 748158 | -10966.2 | 64 | 56 | 296.765 | 96265.2
7193 | 626917 | -10291.1 | 62 | 55 | 275.225 | 72228
7194 | 372521 | -11401.7 | 59 | 53 | 177.735 | 44774.9
7195 | 190974 | 0 | 58 | 53 | 117.984 | 32077.6
7196 | 170994 | 0 | 56 | 52 | 103.282 | 28488.6
7197 | 157602 | 0 | 55 | 52 | 92.0175 | 17533.7
7198 | 146302 | 0 | 54 | 51 | 83.51 | 9498.17
7199 | 141425 | 0 | 54 | 51 | 79.8105 | 8281.66
7200 | 139475 | 0 | 52 | 50 | 75.1888 | 8282.79
7201 | 138368 | 0 | 51 | 49 | 75.1378 | 8283.82
7202 | 137467 | 0 | 49 | 48 | 75.0968 | 8285.45
7203 | 136461 | -6573.09 | 47 | 46 | 81.7294 | 8286.74
7204 | 135422 | 0 | 43 | 43 | 75.0041 | 8288.12
7205 | 134976 | 0 | 45 | 45 | 74.9834 | 8289.55
7206 | 133908 | -11452.9 | 44 | 43 | 80.0131 | 8291.07
7207 | 187050 | -148438 | 42 | 40 | 88.0024 | 8292.29
7208 | 213140 | -247916 | 45 | 40 | 88.4086 | 8293.9
7209 | 208398 | -219336 | 46 | 40 | 94.9648 | 8298.7
7210 | 207321 | -193864 | 48 | 42 | 95.2204 | 8299.92
7211 | 212792 | -160361 | 51 | 43 | 97.2592 | 8301.56
7212 | 214031 | -131783 | 53 | 43 | 90.2017 | 8302.51
7213 | 217329 | -122590 | 53 | 43 | 89.6915 | 8303.51
7214 | 129176 | 0 | 53 | 44 | 71.929 | 8303.98
7215 | 128637 | 0 | 52 | 42 | 71.8189 | 8304.59
7216 | 128446 | 0 | 51 | 42 | 73.6401 | 8302.88
7217 | 128052 | -6852.73 | 50 | 41 | 83.1499 | 8302.92
7218 | 127676 | 0 | 48 | 40 | 79.4683 | 8303.29
7219 | 127212 | -1599.32 | 45 | 37 | 83.8762 | 8304.14
7220 | 127074 | 0 | 41 | 38 | 79.4409 | 8305.26
7221 | 126498 | -16154.4 | 39 | 38 | 87.8116 | 8306.49
7222 | 125893 | -5889.34 | 37 | 36 | 83.0167 | 8308.06
7223 | 127877 | -13295 | 37 | 36 | 84.9909 | 8309.76
7224 | 125064 | -11451.4 | 37 | 36 | 77.689 | 3244.5
7225 | 125301 | -15221.9 | 37 | 36 | 80.3652 | 3246.53
7226 | 124215 | -15023.6 | 36 | 35 | 80.1768 | 3248.77
7227 | 134993 | -24060.4 | 36 | 35 | 83.6746 | 3250.94
7228 | 123469 | -18585.9 | 35 | 34 | 80.6286 | 3253.09
7229 | 153051 | -31495.4 | 33 | 32 | 87.4305 | 3255.62
7230 | 149832 | -38704.8 | 31 | 30 | 85.1203 | 3258.03
7231 | 148308 | -43339.4 | 32 | 31 | 83.5272 | 3260.43
7232 | 148555 | -45662 | 32 | 31 | 82.3549 | 3263.23
7233 | 148579 | -39246.8 | 35 | 33 | 81.9912 | 3265.72
7234 | 135072 | -33834.9 | 36 | 34 | 78.8457 | 3268.25
7235 | 152734 | -30524.8 | 41 | 37 | 81.3889 | 3269.99
7236 | 126039 | -16984.9 | 44 | 39 | 74.8344 | 3271.08
7237 | 121389 | -11420.6 | 46 | 39 | 71.7703 | 3272.15
7238 | 122761 | -11136.1 | 46 | 39 | 71.8294 | 3272.4
7239 | 121453 | -9398.23 | 48 | 42 | 73.3992 | 3272.08
7240 | 123597 | -9130.77 | 49 | 41 | 74.7597 | 3271.95
7241 | 121077 | -7734.29 | 46 | 38 | 79.5351 | 3272.08
7242 | 134798 | -17402.1 | 43 | 37 | 86.2823 | 3272.42
7243 | 133343 | -20046.9 | 40 | 36 | 86.1488 | 3273.03
7244 | 150977 | -25351.3 | 39 | 35 | 90.1179 | 3274.63
7245 | 147420 | -31109.2 | 37 | 34 | 90.1531 | 3276.85
7246 | 151159 | -34755.5 | 36 | 33 | 90.1174 | 3278.72
7247 | 144255 | -32094.7 | 37 | 35 | 87.9554 | 3280.75
7248 | 145061 | -40296.6 | 38 | 36 | 92.3434 | 8349.86
7249 | 142919 | -40949.9 | 37 | 36 | 91.8091 | 8351.25
7250 | 142039 | -44235.3 | 37 | 36 | 92.1719 | 8352.41
7251 | 141280 | -44525.1 | 37 | 35 | 92.0782 | 8353.77
7252 | 149257 | -47355.8 | 37 | 36 | 96.6148 | 9252.82
7253 | 192535 | -37538.1 | 37 | 35 | 135.491 | 22139.8
7254 | 316034 | -479331 | 37 | 35 | 242.534 | 65157.8
7255 | 382465 | -431788 | 38 | 35 | 272.751 | 79084.7
7256 | 413973 | -328536 | 40 | 37 | 267.628 | 109380
7257 | 451454 | -276195 | 44 | 39 | 270.458 | 128665
7258 | 435923 | -237206 | 46 | 40 | 260.175 | 131415
7259 | 424730 | -162885 | 52 | 43 | 247.948 | 131412
7260 | 401155 | -113754 | 55 | 45 | 246.706 | 131410
7261 | 467682 | -70308.4 | 58 | 47 | 265.27 | 131406
7262 | 497026 | -30429.6 | 60 | 49 | 270.527 | 129709
7263 | 530440 | -21197.7 | 61 | 49 | 274.189 | 117932
7264 | 469511 | -17878 | 59 | 48 | 274.888 | 96294.5
7265 | 426319 | -19244.6 | 59 | 48 | 251.6 | 72255.8
7266 | 317122 | -101201 | 53 | 46 | 180.098 | 44801.4
7267 | 182692 | 0 | 56 | 47 | 117.564 | 32102.8
7268 | 163226 | 0 | 55 | 46 | 102.924 | 28512.7
7269 | 149984 | 0 | 52 | 44 | 91.6691 | 17563.8
7270 | 139341 | 0 | 53 | 45 | 83.1928 | 9529.29
7271 | 134526 | -6242.16 | 53 | 44 | 86.1858 | 8313.9
7272 | 133231 | 0 | 51 | 43 | 78.5323 | 8315.49
7273 | 132803 | -1313.44 | 50 | 45 | 82.9411 | 8316.85
7274 | 131805 | 0 | 51 | 45 | 78.4675 | 8318.04
7275 | 131241 | -2009.85 | 50 | 44 | 82.8704 | 8318.98
7276 | 134147 | 0 | 49 | 42 | 82.4607 | 9217.68
7277 | 180914 | -11693.9 | 48 | 41 | 130.632 | 22104.1
7278 | 326289 | -172596 | 48 | 40 | 240.417 | 65121.7
7279 | 440786 | -186615 | 48 | 40 | 278.542 | 79048.2
7280 | 456330 | -136548 | 50 | 42 | 281.668 | 109353
7281 | 464951 | -132053 | 51 | 42 | 274.933 | 128638
7282 | 443140 | -102460 | 53 | 43 | 263.532 | 131388
7283 | 437146 | -86230 | 55 | 44 | 248.025 | 131387
7284 | 431999 | -46235.1 | 59 | 46 | 244.787 | 131385
7285 | 484485 | -30954.7 | 60 | 46 | 263.823 | 131385
7286 | 514324 | -16030.2 | 61 | 48 | 270.066 | 129690
7287 | 529797 | -13694 | 61 | 47 | 287.946 | 117916
7288 | 528998 | -11792.5 | 61 | 47 | 273.628 | 96280.3
7289 | 458741 | -10712.4 | 60 | 46 | 255.96 | 72242.4
7290 | 337259 | -13595.7 | 59 | 46 | 181.145 | 44788.9
7291 | 187939 | 0 | 57 | 45 | 117.818 | 32090.9
7292 | 168188 | 0 | 55 | 44 | 103.152 | 28501.3
7293 | 154727 | 0 | 52 | 42 | 91.886 | 17549.8
7294 | 143548 | 0 | 50 | 41 | 83.3846 | 9514.71
7295 | 138673 | 0 | 48 | 40 | 79.6854 | 8298.99
7296 | 137114 | -6972.88 | 46 | 38 | 85.9372 | 8300.53
7297 | 135722 | 0 | 42 | 36 | 79.0703 | 8998.43
7298 | 134814 | -12879.4 | 40 | 34 | 86.9491 | 8999.98
7299 | 133906 | 0 | 38 | 33 | 78.9876 | 9001.68
7300 | 136459 | -19451.7 | 36 | 31 | 91.8175 | 9987.36
7301 | 182355 | -8852.15 | 33 | 29 | 126.854 | 24114.5
7302 | 327149 | -292366 | 30 | 27 | 240.014 | 71271.5
7303 | 389095 | -401107 | 29 | 26 | 291.454 | 86539.4
7304 | 407477 | -368824 | 29 | 26 | 291.657 | 119762
7305 | 405263 | -371844 | 30 | 27 | 284.611 | 140907
7306 | 402672 | -387372 | 31 | 27 | 275.411 | 143924
7307 | 387931 | -342018 | 32 | 28 | 260.128 | 143924
7308 | 361359 | -332109 | 33 | 28 | 257.533 | 143924
7309 | 392877 | -295160 | 33 | 28 | 277.202 | 143923
7310 | 410949 | -281891 | 32 | 27 | 283.905 | 142064
7311 | 413440 | -295560 | 32 | 26 | 285.252 | 129157
7312 | 409170 | -336746 | 30 | 25 | 283.334 | 105442
7313 | 398494 | -441815 | 27 | 24 | 271.391 | 79092.5
7314 | 319360 | -501928 | 25 | 22 | 188.797 | 48998.9
7315 | 184610 | -13692.7 | 24 | 21 | 128.052 | 35079.9
7316 | 165452 | -19887.9 | 23 | 20 | 112.498 | 31145
7317 | 163327 | -33411.9 | 22 | 19 | 104.344 | 19143.2
7318 | 169813 | -42973.2 | 21 | 19 | 98.8154 | 10338.8
7319 | 160170 | -53194.4 | 21 | 18 | 94.6035 | 9009.06
7320 | 156722 | -72881.2 | 20 | 18 | 93.5106 | 9013.66
7321 | 154478 | -90496.6 | 20 | 18 | 93.2779 | 9017.47
7322 | 152658 | -102153 | 20 | 18 | 93.0725 | 9021.06
7323 | 151030 | -113898 | 20 | 18 | 92.8957 | 9024.23
7324 | 152635 | -128628 | 19 | 18 | 96.704 | 10011.2
7325 | 199709 | -113479 | 19 | 18 | 137.578 | 24139.3
7326 | 324794 | -807372 | 18 | 17 | 260.793 | 71297.2
7327 | 385727 | -767493 | 19 | 18 | 288.565 | 86566.1
7328 | 404753 | -636044 | 21 | 19 | 272.856 | 119782
7329 | 402398 | -569411 | 22 | 19 | 267.709 | 140926
7330 | 392222 | -528200 | 25 | 22 | 258.617 | 143942
7331 | 381617 | -433928 | 28 | 24 | 260.762 | 143942
7332 | 357437 | -379836 | 31 | 25 | 258.025 | 143942
7333 | 390780 | -329272 | 32 | 26 | 276.177 | 143940
7334 | 409045 | -298104 | 33 | 26 | 283.757 | 142081
7335 | 411593 | -301283 | 34 | 26 | 285.133 | 129174
7336 | 407074 | -363081 | 31 | 25 | 283.304 | 105457
7337 | 397063 | -467236 | 28 | 23 | 272.324 | 79107
7338 | 317809 | -543087 | 25 | 21 | 191.664 | 49012.9
7339 | 183254 | -15208.8 | 24 | 20 | 127.961 | 35093.3
7340 | 164188 | -22940.6 | 23 | 20 | 112.587 | 31158
7341 | 178839 | -40643.8 | 22 | 19 | 107.401 | 19157
7342 | 162636 | -57531.2 | 21 | 19 | 98.192 | 10352.9
7343 | 155459 | -78561.5 | 20 | 18 | 94.1141 | 9023.09
7344 | 152301 | -99896.6 | 19 | 17 | 93.1661 | 9027.58
7345 | 150396 | -114882 | 19 | 17 | 92.9494 | 9031.15
7346 | 148613 | -127267 | 18 | 17 | 92.774 | 9034.49
7347 | 147071 | -140575 | 18 | 16 | 92.6218 | 9037.47
7348 | 148834 | -150800 | 18 | 16 | 96.3273 | 10024.3
7349 | 195865 | -133527 | 18 | 16 | 137.206 | 24152.1
7350 | 323574 | -863543 | 18 | 16 | 264.545 | 71309.8
7351 | 385019 | -789775 | 20 | 18 | 289.977 | 86578.4
7352 | 403934 | -660618 | 21 | 19 | 274.364 | 119791
7353 | 401638 | -602957 | 23 | 20 | 269.509 | 140933
7354 | 394945 | -600926 | 25 | 22 | 262.851 | 143949
7355 | 375554 | -505804 | 27 | 23 | 243.023 | 143949
7356 | 356517 | -474136 | 29 | 24 | 239.905 | 143948
7357 | 390003 | -398953 | 30 | 25 | 276.068 | 143947
7358 | 408305 | -379483 | 31 | 25 | 283.642 | 142088
7359 | 410953 | -387531 | 32 | 25 | 285.321 | 129180
7360 | 404560 | -396759 | 31 | 25 | 283.061 | 105464
7361 | 394596 | -481967 | 29 | 23 | 272.08 | 79114
7362 | 310019 | -527483 | 28 | 22 | 190.019 | 49019.4
7363 | 182777 | -15407.2 | 27 | 22 | 127.916 | 35099.5
7364 | 163656 | -22376.9 | 26 | 21 | 112.583 | 31163.9
7365 | 159694 | -35582.7 | 25 | 21 | 104.029 | 19163.4
7366 | 163060 | -50018.6 | 26 | 22 | 98.3215 | 10359.2
7367 | 154837 | -59813.6 | 27 | 23 | 94.2475 | 9029.21
7368 | 151470 | -74742.6 | 28 | 23 | 89.2944 | 9033.38
7369 | 149727 | -88301 | 27 | 23 | 89.1492 | 9036.55
7370 | 147780 | -96269.5 | 27 | 23 | 88.9841 | 9040.1
7371 | 146891 | -108622 | 26 | 22 | 88.9034 | 9042.87
7372 | 145030 | -113580 | 26 | 22 | 88.7554 | 9045.48
7373 | 144736 | -121557 | 25 | 22 | 88.7286 | 9047.92
7374 | 142753 | -123271 | 25 | 21 | 87.0577 | 9050.24
7375 | 126812 | -846834 | 27 | 24 | 125.739 | 9052.5
7376 | 133405 | -720641 | 30 | 26 | 116.983 | 9054.37
7377 | 141553 | -566464 | 32 | 28 | 105.331 | 9046.21
7378 | 144183 | -497655 | 34 | 30 | 100.857 | 9042.54
7379 | 148736 | -467370 | 36 | 31 | 98.6463 | 9041.23
7380 | 162996 | -473783 | 38 | 32 | 99.2106 | 9040.38
7381 | 162559 | -469782 | 38 | 33 | 98.5929 | 9040.01
7382 | 124469 | -10498.9 | 39 | 33 | 77.3927 | 9039.89
7383 | 123252 | -13624.4 | 39 | 33 | 76.937 | 9040.04
7384 | 123332 | -17699.9 | 37 | 32 | 79.822 | 9042.51
7385 | 131567 | -26805.8 | 35 | 31 | 88.3993 | 9045.45
7386 | 144532 | -32743.3 | 33 | 29 | 93.6878 | 9047.34
7387 | 142647 | -43516.6 | 32 | 29 | 93.734 | 9049.92
7388 | 139291 | -49063.7 | 30 | 28 | 92.3964 | 9052.38
7389 | 137975 | -72738.1 | 29 | 27 | 93.3991 | 9054.7
7390 | 137041 | -81378.3 | 29 | 27 | 92.4317 | 9056.45
7391 | 136708 | -93278.8 | 30 | 28 | 91.5372 | 9058.56
7392 | 135259 | -100298 | 30 | 28 | 86.9051 | 3505.85
7393 | 134826 | -109009 | 31 | 29 | 86.8325 | 3507.89
7394 | 134013 | -111464 | 32 | 29 | 86.7801 | 3509.99
7395 | 133606 | -113480 | 33 | 30 | 86.7549 | 3511.94
7396 | 133137 | -114677 | 33 | 30 | 86.7334 | 3513.83
7397 | 132531 | -119093 | 32 | 30 | 86.6985 | 3515.62
7398 | 132166 | -122087 | 32 | 29 | 86.6737 | 3517.36
7399 | 132064 | -123156 | 33 | 30 | 85.0795 | 3519.02
7400 | 131526 | -114608 | 34 | 31 | 82.1931 | 3520.64
7401 | 132097 | -111049 | 35 | 31 | 81.4742 | 3522.2
7402 | 131265 | -99709.1 | 35 | 32 | 81.7249 | 3523.69
7403 | 131191 | -86519.3 | 36 | 32 | 81.3718 | 3525.07
7404 | 131826 | -82910 | 36 | 32 | 81.4796 | 3526.44
7405 | 131246 | -62221.4 | 37 | 33 | 80.9442 | 3527.7
7406 | 133664 | -54991.1 | 37 | 33 | 81.1557 | 3528.89
7407 | 133129 | -48901.4 | 38 | 32 | 81.1288 | 3530.08
7408 | 135109 | -51140.2 | 35 | 31 | 81.4178 | 3531
7409 | 132090 | -55690.2 | 33 | 29 | 84.3741 | 3531.51
7410 | 130603 | -71776.1 | 30 | 27 | 89.8856 | 3532.39
7411 | 129569 | -98405.4 | 30 | 27 | 90.5037 | 3533.25
7412 | 129211 | -127848 | 29 | 27 | 90.3951 | 3534.7
7413 | 128647 | -137361 | 29 | 27 | 90.3268 | 3536.21
7414 | 128344 | -145885 | 29 | 27 | 90.2672 | 3537.83
7415 | 128050 | -147215 | 30 | 27 | 89.4375 | 3539.31
7416 | 128285 | -151515 | 30 | 27 | 88.667 | 3540.76
7417 | 128011 | -145329 | 32 | 29 | 91.6233 | 9096.9
7418 | 128673 | -147834 | 33 | 31 | 91.6755 | 9098.21
7419 | 127954 | -143577 | 35 | 32 | 91.6434 | 9098.62
7420 | 129031 | -144901 | 35 | 33 | 91.7501 | 9099.47
7421 | 131308 | -137425 | 36 | 33 | 95.5439 | 10084.2
7422 | 183007 | -107445 | 36 | 34 | 136.997 | 24210.2
7423 | 313164 | -741108 | 37 | 35 | 259.816 | 71366.1
7424 | 403156 | -659362 | 38 | 36 | 278.369 | 86632.8
7425 | 421975 | -515502 | 39 | 36 | 270.01 | 119835
7426 | 434514 | -462495 | 41 | 38 | 268.458 | 140972
7427 | 421815 | -426535 | 42 | 39 | 258.667 | 143984
7428 | 422983 | -383566 | 44 | 40 | 245.458 | 143982
7429 | 388428 | -336952 | 45 | 41 | 242.176 | 143979
7430 | 449439 | -313720 | 45 | 41 | 264.545 | 143976
7431 | 464326 | -288565 | 46 | 42 | 272.399 | 142115
7432 | 455121 | -276241 | 46 | 42 | 275.179 | 129205
7433 | 457427 | -278946 | 46 | 42 | 284.217 | 105486
7434 | 428326 | -293870 | 46 | 43 | 263.653 | 79134
7435 | 358369 | -372939 | 45 | 43 | 185.562 | 49037.6
7436 | 179360 | 0 | 44 | 43 | 117.444 | 35116.2
7437 | 160181 | -11277.6 | 43 | 43 | 111.634 | 31181.1
7438 | 146943 | 0 | 43 | 43 | 91.5304 | 19182.9
7439 | 136083 | -18398.9 | 44 | 43 | 92.2669 | 10377.5
7440 | 131561 | -8540.79 | 44 | 43 | 83.9381 | 9046.52
7441 | 132113 | -13187.9 | 44 | 43 | 85.5463 | 9049.08
7442 | 129541 | -11450.6 | 44 | 43 | 85.0329 | 9051.16
7443 | 142884 | -14893.1 | 44 | 44 | 88.1401 | 9052.86
7444 | 128273 | -14078.5 | 44 | 43 | 85.1904 | 9054.35
7445 | 151827 | -22807.4 | 43 | 43 | 95.4118 | 10039.7
7446 | 190898 | -17153.5 | 43 | 43 | 132.909 | 24166.2
7447 | 323672 | -404502 | 44 | 44 | 241.32 | 71322.8
7448 | 468031 | -416916 | 44 | 44 | 273.675 | 86589.9
7449 | 476959 | -323708 | 45 | 45 | 274.165 | 119805
7450 | 484401 | -289888 | 46 | 46 | 273.166 | 140943
7451 | 462344 | -264192 | 47 | 47 | 263.43 | 143956
7452 | 448517 | -252206 | 48 | 48 | 249.591 | 143953
7453 | 416686 | -211497 | 49 | 49 | 245.548 | 143951
7454 | 467292 | -193151 | 49 | 49 | 267.688 | 143948
7455 | 490433 | -174987 | 50 | 50 | 279.538 | 142088
7456 | 490134 | -170241 | 49 | 49 | 281.961 | 129179
7457 | 495501 | -197920 | 47 | 47 | 288.144 | 105461
7458 | 463353 | -228980 | 46 | 46 | 266.341 | 79109.9
7459 | 353952 | -295725 | 46 | 45 | 185.65 | 49014.8
7460 | 184612 | 0 | 45 | 45 | 117.68 | 35094.5
7461 | 165031 | -7866.88 | 45 | 44 | 110.625 | 31158.4
7462 | 151716 | 0 | 44 | 43 | 91.7483 | 19159
7463 | 140583 | -14864.4 | 44 | 42 | 92.0246 | 10353
7464 | 135970 | 0 | 43 | 42 | 79.5625 | 9021.9
7465 | 134116 | -18352.2 | 41 | 39 | 88.0189 | 9024.45
7466 | 133278 | -8900 | 39 | 37 | 83.3878 | 9026.77
7467 | 132955 | -15513.5 | 37 | 35 | 86.4109 | 9028.73
7468 | 147604 | -19266.2 | 36 | 34 | 89.2609 | 9030.76
7469 | 155997 | -33431 | 34 | 33 | 96.8217 | 10016.8
7470 | 203366 | -32773.2 | 33 | 31 | 137.739 | 24144.1
7471 | 325486 | -536457 | 32 | 30 | 244.153 | 71301.7
7472 | 387209 | -535657 | 31 | 29 | 269.384 | 86570.4
7473 | 405551 | -469360 | 30 | 28 | 265.291 | 119788
7474 | 403756 | -425725 | 32 | 29 | 264.613 | 140929
7475 | 399679 | -435016 | 33 | 31 | 274.537 | 143945
7476 | 381636 | -365987 | 35 | 31 | 259.097 | 143944
7477 | 358796 | -342080 | 36 | 32 | 257.265 | 143943
7478 | 391785 | -290145 | 36 | 33 | 276.273 | 143941
7479 | 420427 | -283611 | 37 | 33 | 284.864 | 142082
7480 | 421904 | -300010 | 37 | 33 | 291.166 | 129174
7481 | 407645 | -316326 | 36 | 33 | 297.066 | 105457
7482 | 390472 | -357011 | 36 | 33 | 277.867 | 79107
7483 | 313368 | -406037 | 36 | 33 | 181.984 | 49012.2
7484 | 185668 | -8670.89 | 36 | 33 | 126.008 | 35092.2
7485 | 165266 | -11473.3 | 36 | 33 | 110.519 | 31156.7
7486 | 151799 | -15685 | 36 | 33 | 99.8492 | 19156.4
7487 | 140580 | -16429.4 | 35 | 33 | 91.2185 | 10351.3
7488 | 135725 | -18158.8 | 35 | 32 | 87.7512 | 9020.44
7489 | 150996 | -24483.8 | 35 | 33 | 90.2911 | 9023.68
7490 | 155569 | -35855.5 | 34 | 33 | 93.33 | 9026.42
7491 | 146318 | -31749.8 | 34 | 33 | 90.2712 | 9028.98
7492 | 150887 | -50371.4 | 34 | 33 | 93.3768 | 9031.67
7493 | 153469 | -56477.3 | 33 | 33 | 97.3518 | 10017.9
7494 | 201048 | -47694.7 | 33 | 33 | 138.515 | 24145.6
7495 | 325411 | -554621 | 33 | 33 | 245.137 | 71303.1
7496 | 387350 | -531879 | 33 | 33 | 271.018 | 86571.4
7497 | 405713 | -434697 | 33 | 32 | 272.836 | 119788
7498 | 403727 | -424730 | 33 | 32 | 265.098 | 140930
7499 | 399517 | -441837 | 33 | 32 | 275.604 | 143945
7500 | 384058 | -409167 | 33 | 32 | 260.098 | 143944
7501 | 358548 | -401997 | 33 | 33 | 257.335 | 143942
7502 | 391716 | -349981 | 34 | 32 | 277.522 | 143941
7503 | 409984 | -336856 | 34 | 33 | 284.988 | 142082
7504 | 412640 | -339299 | 34 | 33 | 290.313 | 129174
7505 | 406212 | -363352 | 33 | 33 | 297.338 | 105458
7506 | 391190 | -406630 | 33 | 33 | 277.875 | 79107.6
7507 | 302493 | -438319 | 33 | 33 | 184.144 | 49013.1
7508 | 184392 | -9598.3 | 33 | 33 | 126.257 | 35093
7509 | 165094 | -13068.9 | 33 | 33 | 110.879 | 31157.5
7510 | 153916 | -15455.2 | 33 | 33 | 99.85 | 19156.9
7511 | 140400 | -13611.9 | 34 | 33 | 90.4971 | 10351.8
7512 | 152424 | -23996.7 | 34 | 33 | 91.1704 | 9020.72
7513 | 155902 | -35772.8 | 34 | 32 | 87.9472 | 3468.93
7514 | 153430 | -47118.1 | 33 | 32 | 88.4455 | 3471.74
7515 | 151020 | -56017.2 | 33 | 31 | 88.2228 | 3475.55
7516 | 149310 | -68016.1 | 32 | 30 | 88.0505 | 3478.76
7517 | 147860 | -76302.6 | 32 | 30 | 87.9008 | 3481.72
7518 | 146565 | -86759.8 | 31 | 29 | 87.7604 | 3484.45
7519 | 145415 | -94354.3 | 31 | 29 | 86.0344 | 3486.98
7520 | 144476 | -101438 | 30 | 29 | 83.1122 | 3489.44
7521 | 143366 | -96443.3 | 30 | 28 | 81.832 | 3491.82
7522 | 143289 | -86175.6 | 31 | 29 | 82.3074 | 3494.16
7523 | 142126 | -77445.1 | 32 | 30 | 82.1568 | 3496.38
7524 | 141560 | -70410.8 | 33 | 30 | 82.0582 | 3498.5
7525 | 141008 | -68972.1 | 34 | 31 | 81.6027 | 3500.45
7526 | 140425 | -59358.1 | 34 | 31 | 81.5762 | 3502.29
7527 | 140092 | -52098.2 | 35 | 32 | 81.5745 | 3504.02
7528 | 140050 | -58121.1 | 34 | 31 | 81.7298 | 3505.78
7529 | 138468 | -79413.3 | 32 | 30 | 85.7672 | 3507.34
7530 | 137354 | -98983.2 | 31 | 29 | 90.2487 | 3508.9
7531 | 136636 | -109958 | 32 | 30 | 90.9614 | 3510.65
7532 | 136523 | -114741 | 33 | 31 | 90.9502 | 3512.45
7533 | 135381 | -113171 | 34 | 31 | 90.8876 | 3514.32
7534 | 135438 | -115529 | 34 | 31 | 90.9102 | 3516.11
7535 | 134384 | -115970 | 34 | 31 | 90.0409 | 3517.8
7536 | 133895 | -118916 | 34 | 31 | 89.1964 | 3519.4
7537 | 133491 | -121362 | 34 | 32 | 88.067 | 9075.66
7538 | 133313 | -126869 | 34 | 32 | 88.0423 | 9077.19
7539 | 132730 | -130009 | 34 | 32 | 88.0069 | 9078.5
7540 | 132410 | -132189 | 34 | 32 | 87.9853 | 9079.91
7541 | 132070 | -131702 | 35 | 32 | 87.9608 | 9081.29
7542 | 132375 | -132412 | 35 | 32 | 88.0021 | 9082.63
7543 | 131469 | -131462 | 35 | 33 | 86.3505 | 9083.96
7544 | 123997 | -923000 | 35 | 33 | 131.258 | 9085.26
7545 | 134562 | -783506 | 35 | 33 | 119.885 | 9086.31
7546 | 154966 | -659897 | 36 | 33 | 110.457 | 9068.13
7547 | 161317 | -594416 | 38 | 34 | 106.338 | 9065.34
7548 | 171446 | -571803 | 39 | 34 | 105.059 | 9063.09
7549 | 167693 | -561116 | 37 | 34 | 104.11 | 9061.81
7550 | 157269 | -554815 | 36 | 34 | 103.847 | 9060.86
7551 | 118377 | -9470.54 | 34 | 33 | 76.5271 | 9060.12
7552 | 118187 | -16309.1 | 32 | 31 | 78.1336 | 9059.69
7553 | 124994 | -34190.6 | 31 | 30 | 85.3357 | 9063.46
7554 | 135373 | -69412.7 | 29 | 28 | 92.2492 | 9067.1
7555 | 132777 | -91586.4 | 28 | 27 | 92.7839 | 9070.18
7556 | 131559 | -116287 | 26 | 25 | 92.628 | 9073.29
7557 | 130743 | -131455 | 25 | 24 | 92.503 | 9075.86
7558 | 130156 | -145891 | 24 | 23 | 92.397 | 9078.31
7559 | 129646 | -153875 | 24 | 22 | 91.5157 | 9080.45
7560 | 129135 | -163970 | 23 | 21 | 90.6495 | 9082.56
7561 | 128410 | -174267 | 22 | 20 | 86.0617 | 3529.84
7562 | 127818 | -193048 | 20 | 19 | 86.6288 | 3531.81
7563 | 127284 | -203518 | 19 | 17 | 87.3124 | 3533.89
7564 | 126841 | -217374 | 18 | 17 | 88.0512 | 3535.87
7565 | 126319 | -226422 | 16 | 15 | 88.7003 | 3537.85
7566 | 125801 | -240932 | 15 | 14 | 89.4812 | 3539.85
7567 | 125512 | -245665 | 17 | 16 | 88.3457 | 3541.81
7568 | 125485 | -215987 | 18 | 17 | 83.5241 | 3543.71
7569 | 125844 | -172529 | 20 | 18 | 79.9637 | 3545.59
7570 | 128782 | -147030 | 22 | 20 | 80.1962 | 3547.38
7571 | 127872 | -130343 | 24 | 22 | 80.1485 | 3548.87
7572 | 130655 | -126682 | 26 | 23 | 80.3888 | 3549.9
7573 | 129660 | -117566 | 28 | 25 | 80.399 | 3550.73
7574 | 129966 | -111329 | 29 | 26 | 80.5197 | 3551.37
7575 | 129932 | -102817 | 31 | 26 | 80.6191 | 3552
7576 | 130986 | -103471 | 30 | 26 | 80.7903 | 3552.49
7577 | 127812 | -109204 | 28 | 25 | 84.9263 | 3553.23
7578 | 126124 | -131845 | 27 | 24 | 89.2296 | 3554.05
7579 | 125339 | -152564 | 27 | 25 | 89.9445 | 3555.19
7580 | 125264 | -167993 | 28 | 25 | 89.9214 | 3556.64
7581 | 124972 | -175055 | 28 | 25 | 90.029 | 3558.09
7582 | 125035 | -176350 | 30 | 27 | 90.1144 | 3559.21
7583 | 125592 | -176525 | 31 | 28 | 89.368 | 3560.12
7584 | 124862 | -171554 | 33 | 28 | 88.3372 | 3560.96
7585 | 125591 | -167420 | 33 | 29 | 91.3901 | 9116.46
7586 | 125313 | -168404 | 33 | 29 | 91.3822 | 9117.19
7587 | 125524 | -171640 | 33 | 29 | 91.4036 | 9117.38
7588 | 125350 | -172847 | 33 | 29 | 91.394 | 9117.9
7589 | 128716 | -173022 | 33 | 30 | 95.2473 | 10102.4
7590 | 176366 | -134663 | 33 | 29 | 136.36 | 24228.2
7591 | 311760 | -845897 | 34 | 31 | 266.672 | 71383.9
7592 | 389352 | -720125 | 36 | 32 | 279.782 | 86650.4
7593 | 401642 | -537094 | 37 | 33 | 265.99 | 119846
7594 | 416693 | -438731 | 40 | 35 | 265.49 | 140985
7595 | 420284 | -375223 | 43 | 36 | 257.925 | 143997
7596 | 423112 | -315775 | 46 | 37 | 245.37 | 143994
7597 | 382347 | -256956 | 47 | 38 | 242.284 | 143991
7598 | 439840 | -229490 | 48 | 39 | 263.865 | 143988
7599 | 453757 | -212392 | 49 | 40 | 271.829 | 142126
7600 | 457486 | -236899 | 46 | 39 | 273.321 | 129215
7601 | 456222 | -285210 | 43 | 38 | 282.538 | 105496
7602 | 395311 | -331179 | 40 | 36 | 259.695 | 79144.4
7603 | 322537 | -421252 | 38 | 35 | 182.595 | 49048.5
7604 | 178041 | 0 | 37 | 34 | 121.514 | 35128.2
7605 | 158979 | -11201.8 | 35 | 33 | 110.154 | 31193.2
7606 | 145740 | -16978.6 | 33 | 31 | 99.8203 | 19194.9
7607 | 134618 | -21039.2 | 30 | 30 | 91.6191 | 10390.2
7608 | 149496 | -46173.7 | 28 | 28 | 94.158 | 9059.67
7609 | 152254 | -57735.6 | 29 | 28 | 93.4752 | 9063.09
7610 | 144054 | -56298.2 | 29 | 29 | 91.4564 | 9066.23
7611 | 143066 | -78813.4 | 30 | 29 | 92.4792 | 9068.79
7612 | 141011 | -92067.7 | 28 | 27 | 92.2724 | 9070.45
7613 | 143088 | -106976 | 27 | 25 | 96.3826 | 10056.6
7614 | 190255 | -100709 | 25 | 23 | 137.41 | 24183.8
7615 | 320469 | -800249 | 26 | 24 | 261.171 | 71340.8
7616 | 382656 | -711905 | 28 | 25 | 278.303 | 86608.7
7617 | 401320 | -545958 | 29 | 25 | 266.345 | 119820
7618 | 399767 | -464296 | 31 | 27 | 263.63 | 140960
7619 | 393012 | -418488 | 34 | 29 | 255.849 | 143974
7620 | 379436 | -352844 | 36 | 30 | 259.983 | 143972
7621 | 355362 | -321378 | 37 | 31 | 257.184 | 143970
7622 | 398992 | -283625 | 38 | 31 | 277.091 | 143967
7623 | 428217 | -279454 | 39 | 32 | 285.793 | 142106
7624 | 409856 | -305938 | 36 | 31 | 285.715 | 129196
7625 | 405066 | -369641 | 33 | 29 | 296.491 | 105479
7626 | 393496 | -467968 | 30 | 27 | 277.978 | 79128.9
7627 | 306946 | -500578 | 30 | 27 | 188.42 | 49034.1
7628 | 181682 | -12316.4 | 29 | 27 | 127.375 | 35114.3
7629 | 162618 | -17356.3 | 29 | 26 | 111.868 | 31178.5
7630 | 149233 | -22697 | 29 | 26 | 100.962 | 19179.8
7631 | 160902 | -38573.4 | 29 | 26 | 98.3038 | 10375.4
7632 | 153020 | -53630.3 | 29 | 26 | 94.2298 | 9045.09
7633 | 149968 | -63470.6 | 30 | 27 | 93.3305 | 9049.12
7634 | 148049 | -72121.2 | 31 | 28 | 93.1642 | 9052.35
7635 | 146595 | -78932.2 | 32 | 29 | 93.0577 | 9055.13
7636 | 145457 | -82227 | 33 | 30 | 92.9803 | 9057.53
7637 | 147897 | -83121.8 | 34 | 31 | 96.7825 | 10043.7
7638 | 198834 | -65032.6 | 35 | 32 | 138.224 | 24170.8
7639 | 323763 | -587510 | 36 | 33 | 248.397 | 71327.7
7640 | 398052 | -524787 | 38 | 35 | 268.961 | 86595.4
7641 | 417036 | -373703 | 39 | 36 | 266.395 | 119807
7642 | 432146 | -330225 | 41 | 37 | 266.867 | 140947
7643 | 440649 | -318528 | 44 | 39 | 278.637 | 143961
7644 | 434865 | -285411 | 46 | 41 | 246.256 | 143957
7645 | 394312 | -207806 | 48 | 42 | 243.354 | 143955
7646 | 441708 | -192140 | 49 | 43 | 264.282 | 143952
7647 | 459825 | -153912 | 51 | 44 | 273.011 | 142092
7648 | 458522 | -152696 | 50 | 44 | 274.489 | 129183
7649 | 463558 | -179078 | 48 | 43 | 286.958 | 105464
7650 | 436126 | -217482 | 47 | 43 | 264.755 | 79112.2
7651 | 360369 | -306065 | 45 | 41 | 185.767 | 49016.6
7652 | 184841 | 0 | 42 | 40 | 117.695 | 35096
7653 | 165396 | -10221.2 | 40 | 39 | 111.617 | 31160.7
7654 | 151920 | 0 | 40 | 39 | 91.7577 | 19161.3
7655 | 140795 | -19466 | 40 | 39 | 92.5751 | 10355.6
7656 | 135969 | -8784.4 | 40 | 39 | 84.1382 | 9024.76
7657 | 136395 | -14448 | 40 | 39 | 86.4349 | 9027.56
7658 | 133436 | -12684.1 | 40 | 39 | 85.8316 | 9030.04
7659 | 148916 | -16287.9 | 40 | 39 | 89.244 | 9032.14
7660 | 131712 | -15823.2 | 40 | 38 | 86.0805 | 9034.08
7661 | 157638 | -26248.3 | 39 | 38 | 96.2813 | 10019.9
7662 | 195566 | -19275 | 39 | 38 | 133.643 | 24146.8
7663 | 326100 | -395155 | 39 | 38 | 241.178 | 71304
7664 | 419613 | -405835 | 40 | 39 | 268.081 | 86571.4
7665 | 434413 | -301714 | 40 | 39 | 268.029 | 119788
7666 | 479641 | -247243 | 45 | 42 | 271.936 | 140929
7667 | 443856 | -185733 | 49 | 44 | 262.128 | 143943
7668 | 426546 | -129733 | 54 | 46 | 248.93 | 143940
7669 | 411900 | -98660.5 | 55 | 47 | 246.176 | 143937
7670 | 473583 | -70710.6 | 57 | 47 | 264.119 | 143934
7671 | 497419 | -46338.4 | 58 | 48 | 270.048 | 142074
7672 | 455791 | -56027.3 | 53 | 46 | 287.589 | 129166
7673 | 460684 | -107147 | 48 | 43 | 299.439 | 105449
7674 | 428150 | -180174 | 43 | 40 | 280.136 | 79098
7675 | 350324 | -238223 | 43 | 40 | 184.942 | 49003.5
7676 | 186366 | 0 | 42 | 40 | 117.757 | 35084.4
7677 | 166843 | 0 | 42 | 40 | 103.09 | 31149.2
7678 | 153370 | -7939.85 | 42 | 40 | 99.3045 | 19146.9
7679 | 142162 | 0 | 41 | 40 | 83.3215 | 10340.3
7680 | 137261 | -15617.4 | 41 | 40 | 88.372 | 9008.72
7681 | 135536 | -6438.61 | 41 | 39 | 83.4909 | 9011.28
7682 | 136333 | -11863.9 | 40 | 39 | 83.5252 | 9013.42
7683 | 133719 | -10499.1 | 40 | 39 | 83.4092 | 9015.53
7684 | 132853 | -12725 | 39 | 38 | 85.7046 | 9017.4
7685 | 153606 | -14235.2 | 39 | 38 | 92.6969 | 10003.2
7686 | 202476 | -16580.2 | 38 | 38 | 133.742 | 24130.2
7687 | 326933 | -330581 | 39 | 38 | 240.893 | 71287.1
7688 | 409343 | -354133 | 40 | 39 | 272.114 | 86554.6
7689 | 438216 | -289453 | 41 | 40 | 270.352 | 119774
7690 | 473052 | -252901 | 45 | 42 | 271.275 | 140916
7691 | 439308 | -181536 | 49 | 45 | 261.558 | 143931
7692 | 421800 | -129540 | 53 | 48 | 247.924 | 143929
7693 | 398376 | -140241 | 49 | 45 | 244.374 | 143927
7694 | 466701 | -167555 | 46 | 43 | 265.591 | 143925
7695 | 472928 | -194122 | 42 | 40 | 276.378 | 142066
7696 | 475625 | -200176 | 42 | 40 | 282.323 | 129159
7697 | 467217 | -218237 | 42 | 40 | 286.396 | 105443
7698 | 422108 | -235578 | 42 | 40 | 262.257 | 79093.9
7699 | 331506 | -310906 | 40 | 38 | 182.625 | 48999.8
7700 | 185845 | 0 | 39 | 36 | 117.718 | 35080.4
7701 | 166610 | -13158.8 | 37 | 34 | 112.769 | 31145
7702 | 153019 | 0 | 36 | 33 | 91.808 | 19143.2
7703 | 141785 | -23689.4 | 35 | 33 | 92.4394 | 10337.3
7704 | 136847 | -11522.6 | 34 | 31 | 84.1781 | 9006.3
7705 | 136448 | -19668 | 32 | 30 | 83.4958 | 9009.4
7706 | 160723 | -31779.6 | 31 | 28 | 89.3223 | 9012.35
7707 | 156606 | -39432.9 | 29 | 26 | 89.9395 | 9015.72
7708 | 153975 | -46532.4 | 28 | 25 | 89.652 | 9019.19
7709 | 151642 | -70744.1 | 26 | 24 | 89.3825 | 9022.6
7710 | 149851 | -85577.2 | 25 | 23 | 89.1665 | 9025.77
7711 | 148373 | -97672.8 | 25 | 22 | 87.3732 | 9028.85
7712 | 129024 | -768364 | 25 | 22 | 118.899 | 9031.81
7713 | 129574 | -674025 | 25 | 22 | 112.473 | 9034.44
7714 | 127063 | -557612 | 26 | 23 | 104.166 | 9031.78
7715 | 126356 | -501634 | 27 | 23 | 100.734 | 9029.19
7716 | 125761 | -462953 | 28 | 23 | 98.0842 | 9028.98
7717 | 125310 | -440910 | 29 | 24 | 96.716 | 9028.92
7718 | 124733 | -435856 | 29 | 24 | 96.1518 | 9029.15
7719 | 125607 | -16526.2 | 30 | 24 | 77.3327 | 9029.3
7720 | 123892 | -21398.1 | 28 | 24 | 77.4041 | 9029.83
7721 | 134035 | -37839.9 | 27 | 23 | 85.5508 | 9032.6
7722 | 148342 | -47579.9 | 25 | 21 | 93.0732 | 9035.34
7723 | 143978 | -67405.8 | 24 | 21 | 93.4725 | 9038.4
7724 | 141556 | -86036.7 | 22 | 20 | 93.2285 | 9042.01
7725 | 139575 | -100894 | 21 | 19 | 93.0298 | 9044.97
7726 | 138505 | -118080 | 20 | 18 | 92.9217 | 9047.97
7727 | 137142 | -126405 | 20 | 18 | 92.0329 | 9050.77
7728 | 137143 | -134222 | 19 | 17 | 91.258 | 9053.49
7729 | 137562 | -139926 | 19 | 17 | 86.9339 | 3501.27
7730 | 134139 | -136513 | 18 | 17 | 86.8041 | 3503.63
7731 | 135380 | -144096 | 18 | 17 | 86.9451 | 3506.02
7732 | 132664 | -148314 | 17 | 16 | 86.7988 | 3507.84
7733 | 132020 | -161977 | 17 | 16 | 86.561 | 3509.7
7734 | 131349 | -186090 | 16 | 15 | 86.2943 | 3511.41
7735 | 130837 | -185003 | 18 | 17 | 84.7351 | 3513.06
7736 | 131774 | -177745 | 20 | 18 | 81.4879 | 3515.31
7737 | 130854 | -135741 | 22 | 20 | 80.1457 | 3517.55
7738 | 133918 | -112517 | 25 | 23 | 80.6853 | 3519.84
7739 | 132890 | -95641.8 | 29 | 25 | 80.6609 | 3521.79
7740 | 136317 | -91360.2 | 32 | 27 | 80.9872 | 3523.1
7741 | 133932 | -80452.8 | 33 | 28 | 80.9237 | 3524.24
7742 | 133452 | -77492.4 | 33 | 28 | 80.9559 | 3525.05
7743 | 132110 | -77677 | 34 | 28 | 81.7702 | 3526.09
7744 | 131687 | -89974.6 | 33 | 28 | 81.4461 | 3526.98
7745 | 129995 | -99235.2 | 31 | 27 | 85.3279 | 3528.35
7746 | 129207 | -120472 | 30 | 26 | 89.5296 | 3530.02
7747 | 128804 | -134727 | 31 | 27 | 90.2657 | 3531.51
7748 | 128758 | -136392 | 33 | 28 | 90.2644 | 3533.14
7749 | 128322 | -134785 | 34 | 29 | 90.2704 | 3534.73
7750 | 128152 | -133138 | 34 | 29 | 90.2951 | 3536.25
7751 | 128026 | -132423 | 35 | 30 | 89.4998 | 3537.63
7752 | 128439 | -132859 | 35 | 30 | 88.7479 | 3538.87
7753 | 128049 | -127439 | 35 | 30 | 91.6912 | 9094.79
7754 | 128562 | -127516 | 36 | 30 | 91.7223 | 9095.96
7755 | 128077 | -128078 | 36 | 30 | 91.7133 | 9096.24
7756 | 128025 | -130688 | 35 | 31 | 91.726 | 9097.02
7757 | 131328 | -132614 | 35 | 31 | 95.5784 | 10081.7
7758 | 179247 | -108924 | 34 | 30 | 136.687 | 24207.7
7759 | 313019 | -760346 | 35 | 31 | 261.027 | 71363.6
7760 | 375360 | -672888 | 35 | 32 | 277.92 | 86630.4
7761 | 394392 | -491139 | 36 | 32 | 264.651 | 119832
7762 | 401185 | -410871 | 38 | 34 | 264.14 | 140970
7763 | 408014 | -376230 | 40 | 35 | 256.492 | 143983
7764 | 410234 | -331023 | 42 | 36 | 243.399 | 143980
7765 | 390166 | -292495 | 43 | 37 | 241.644 | 143978
7766 | 443637 | -261823 | 44 | 37 | 262.882 | 143975
7767 | 464585 | -246337 | 45 | 38 | 271.372 | 142113
7768 | 452582 | -266485 | 42 | 36 | 271.771 | 129204
7769 | 417686 | -308908 | 38 | 34 | 279.467 | 105485
7770 | 385472 | -388324 | 35 | 32 | 258.553 | 79133.7
7771 | 297367 | -441638 | 34 | 32 | 184.238 | 49038.7
7772 | 178230 | -9783.54 | 34 | 31 | 126.067 | 35118.6
7773 | 159200 | -13989.8 | 33 | 31 | 110.795 | 31183.3
7774 | 146058 | -19282.5 | 33 | 31 | 100.359 | 19184.8
7775 | 158409 | -30292.4 | 33 | 31 | 97.9852 | 10380.2
7776 | 150362 | -38429.3 | 33 | 31 | 94.1906 | 9049.65
7777 | 147269 | -49433.8 | 32 | 30 | 92.864 | 9053.38
7778 | 145049 | -64216.4 | 30 | 29 | 92.6485 | 9056.41
7779 | 143408 | -76721.2 | 29 | 28 | 92.4595 | 9058.93
7780 | 142296 | -84845.8 | 31 | 29 | 92.3164 | 9061.23
7781 | 144752 | -89808.4 | 32 | 31 | 96.5251 | 10047.3
7782 | 192667 | -70121.8 | 34 | 32 | 137.7 | 24174.5
7783 | 321663 | -613186 | 35 | 33 | 250.126 | 71331.4
7784 | 383812 | -552092 | 36 | 34 | 274.375 | 86599.2
7785 | 406067 | -440153 | 37 | 34 | 267.471 | 119811
7786 | 420550 | -391431 | 39 | 36 | 265.736 | 140950
7787 | 420006 | -361892 | 41 | 37 | 257.384 | 143964
7788 | 422592 | -294697 | 43 | 39 | 263.511 | 143962
7789 | 398187 | -268796 | 44 | 40 | 261.378 | 143959
7790 | 447821 | -241444 | 46 | 41 | 263.622 | 143956
7791 | 467107 | -226491 | 47 | 41 | 272.898 | 142096
7792 | 460697 | -212484 | 47 | 41 | 280.044 | 129187
7793 | 462682 | -223435 | 47 | 41 | 287.418 | 105469
7794 | 431757 | -241034 | 47 | 41 | 264.32 | 79117.1
7795 | 341784 | -288109 | 48 | 42 | 185.084 | 49021.1
7796 | 183805 | 0 | 48 | 42 | 117.633 | 35100.2
7797 | 164489 | -8643.7 | 49 | 43 | 110.987 | 31164.4
7798 | 151089 | 0 | 49 | 43 | 91.7197 | 19165.2
7799 | 140123 | -13093.1 | 48 | 43 | 91.6823 | 10359.1
7800 | 135330 | 0 | 48 | 43 | 79.5336 | 9027.71
7801 | 134026 | -14827.8 | 48 | 44 | 87.3948 | 9029.88
7802 | 133154 | 0 | 49 | 45 | 78.9535 | 9031.77
7803 | 132384 | -15452.4 | 49 | 45 | 87.3276 | 9033.26
7804 | 131824 | 0 | 49 | 46 | 78.893 | 9034.65
7805 | 134844 | -15465.5 | 50 | 47 | 90.9959 | 10019.8
7806 | 181603 | -5931.58 | 50 | 48 | 126.818 | 24146.1
7807 | 327133 | -220665 | 50 | 49 | 241.666 | 71302.2
7808 | 431166 | -235615 | 51 | 49 | 277.479 | 86569
7809 | 462690 | -180743 | 51 | 50 | 279.288 | 119786
7810 | 474649 | -158929 | 52 | 51 | 275.125 | 140926
7811 | 452093 | -137724 | 53 | 51 | 265.202 | 143939
7812 | 437850 | -120973 | 54 | 52 | 249.509 | 143936
7813 | 433673 | -99952.5 | 55 | 53 | 247.489 | 143934
7814 | 475806 | -80711.8 | 56 | 54 | 266.949 | 143932
7815 | 516401 | -66570.7 | 57 | 55 | 274.842 | 142074
7816 | 504950 | -56734.2 | 56 | 54 | 278.407 | 129166
7817 | 502983 | -68203 | 54 | 53 | 283.944 | 105449
7818 | 451879 | -83596.9 | 53 | 52 | 261.835 | 79098.4
7819 | 343861 | -143171 | 52 | 51 | 183.769 | 49003.3
7820 | 186872 | 0 | 51 | 50 | 117.775 | 35083.4
7821 | 167258 | 0 | 50 | 49 | 103.11 | 31148.2
7822 | 154085 | 0 | 50 | 50 | 91.8564 | 19146.2
7823 | 142890 | -6221.13 | 50 | 50 | 90.0904 | 10339.1
7824 | 138002 | 0 | 50 | 50 | 79.655 | 9007.1
7825 | 138119 | -869.778 | 50 | 50 | 78.2781 | 3454.22
7826 | 135147 | 0 | 50 | 50 | 73.7167 | 3455.82
7827 | 134312 | 0 | 50 | 50 | 73.6772 | 3457.82
7828 | 133464 | 0 | 49 | 49 | 73.6388 | 3459.22
7829 | 135143 | -7600.02 | 49 | 49 | 79.9907 | 3460.46
7830 | 132007 | 0 | 48 | 48 | 73.5745 | 3461.53
7831 | 131399 | 0 | 48 | 48 | 71.9451 | 3462.65
7832 | 135383 | -6127.32 | 49 | 49 | 75.8313 | 3463.75
7833 | 130205 | 0 | 49 | 49 | 68.5104 | 3464.76
7834 | 138482 | -3199.51 | 49 | 49 | 73.227 | 3465.73
7835 | 129183 | 0 | 50 | 50 | 68.3052 | 3466.68
7836 | 128644 | -3322.98 | 50 | 50 | 72.8969 | 3467.45
7837 | 135643 | -3514.18 | 50 | 50 | 72.9535 | 3467.92
7838 | 127705 | 0 | 50 | 50 | 68.2558 | 3468.65
7839 | 127328 | -10016.9 | 50 | 50 | 75.2573 | 3469.66
7840 | 130345 | -3779.3 | 49 | 49 | 73.5312 | 3470.39
7841 | 127962 | -6566.75 | 48 | 48 | 78.561 | 3471.26
7842 | 126020 | -6242.17 | 47 | 47 | 82.5604 | 3472.46
7843 | 143979 | -8690.26 | 47 | 47 | 87.211 | 3473.61
7844 | 125369 | -8118.55 | 47 | 47 | 81.6726 | 3474.99
7845 | 142036 | -9830.86 | 47 | 47 | 86.9746 | 3476.42
7846 | 124707 | -8854 | 47 | 47 | 81.6417 | 3477.86
7847 | 140837 | -10515.6 | 48 | 48 | 86.0766 | 3479.27
7848 | 124138 | -9044.63 | 48 | 48 | 80.0156 | 3480.63
7849 | 139862 | -10411.4 | 47 | 47 | 88.1709 | 9036.71
7850 | 147947 | -16406.4 | 46 | 46 | 91.1113 | 9037.99
7851 | 123569 | -10313.2 | 45 | 45 | 84.7755 | 9038.42
7852 | 138638 | -13145.2 | 46 | 46 | 88.084 | 9039.65
7853 | 149175 | -20912.3 | 46 | 46 | 94.7913 | 10024.8
7854 | 173876 | -11448.6 | 47 | 47 | 128.869 | 24150.9
7855 | 319385 | -340163 | 46 | 46 | 241.713 | 71307.5
7856 | 466375 | -346403 | 46 | 46 | 277.919 | 86574.4
7857 | 480947 | -297150 | 45 | 45 | 274.726 | 119791
7858 | 491687 | -288708 | 45 | 45 | 273.78 | 140930
7859 | 466588 | -287215 | 44 | 44 | 263.008 | 143944
7860 | 443973 | -269892 | 44 | 44 | 247.286 | 143942
7861 | 403249 | -255169 | 44 | 43 | 243.058 | 143940
7862 | 449942 | -243403 | 43 | 43 | 264.465 | 143938
7863 | 479241 | -242654 | 43 | 43 | 276.768 | 142078
7864 | 491375 | -237364 | 43 | 43 | 280.806 | 129170
7865 | 477375 | -246571 | 42 | 42 | 286.879 | 105453
7866 | 425325 | -260314 | 42 | 42 | 262.637 | 79102.6
7867 | 352303 | -321356 | 42 | 42 | 184.825 | 49007.8
7868 | 182167 | 0 | 42 | 42 | 117.567 | 35087.7
7869 | 162979 | 0 | 42 | 42 | 102.913 | 31151.6
7870 | 149713 | -12428.5 | 42 | 42 | 99.8089 | 19150.6
7871 | 138573 | 0 | 42 | 41 | 83.1583 | 10344.3
7872 | 134056 | -17683.9 | 42 | 41 | 88.49 | 9012.98
7873 | 132288 | -7890.83 | 41 | 40 | 79.2913 | 9015.68
7874 | 132643 | -13545.4 | 40 | 39 | 81.9605 | 9017.93
7875 | 148208 | -14894.7 | 39 | 38 | 84.7679 | 9020.75
7876 | 145245 | -17506.9 | 39 | 37 | 85.0099 | 9023.04
7877 | 152390 | -27505.9 | 38 | 37 | 88.0804 | 9025.34
7878 | 142658 | -21663.3 | 38 | 36 | 85.1636 | 9027.57
7879 | 148736 | -34977.4 | 38 | 37 | 86.6165 | 9030.13
7880 | 133298 | -576473 | 39 | 37 | 107.33 | 9032.31
7881 | 185508 | -566285 | 39 | 37 | 106.065 | 9034.45
7882 | 167971 | -472848 | 39 | 38 | 99.8106 | 9033.99
7883 | 183467 | -447192 | 40 | 37 | 97.8913 | 9031.74
7884 | 180527 | -426320 | 40 | 38 | 96.8367 | 9031.76
7885 | 179404 | -365370 | 41 | 38 | 92.8746 | 9031.71
7886 | 186708 | -368102 | 42 | 39 | 93.1884 | 9031.9
7887 | 126910 | -7250.43 | 43 | 39 | 75.6063 | 9032.13
7888 | 124089 | -7477.22 | 41 | 38 | 73.4617 | 9032.47
7889 | 123756 | -11739.1 | 40 | 37 | 80.864 | 9033.69
7890 | 123488 | -13551.1 | 38 | 36 | 85.3862 | 9035.33
7891 | 123206 | -15575.2 | 37 | 36 | 86.5245 | 9036.91
7892 | 147332 | -28158.6 | 36 | 35 | 93.0081 | 9039
7893 | 144539 | -32198.4 | 35 | 34 | 93.138 | 9041.04
7894 | 142881 | -38032.4 | 36 | 35 | 93.2314 | 9043.47
7895 | 141706 | -45153.2 | 36 | 35 | 92.5494 | 9045.93
7896 | 140499 | -47163.6 | 37 | 36 | 91.5625 | 9048.19
7897 | 139310 | -55634 | 37 | 36 | 87.0578 | 3495.6
7898 | 138511 | -62394.6 | 37 | 36 | 87.0945 | 3497.56
7899 | 137975 | -67777.7 | 37 | 37 | 87.1154 | 3499.61
7900 | 137245 | -72054.1 | 37 | 37 | 87.1174 | 3501.51
7901 | 136646 | -73689.5 | 38 | 37 | 87.0645 | 3503.35
7902 | 136885 | -76680.7 | 38 | 38 | 87.1737 | 3505.12
7903 | 135746 | -75474.1 | 39 | 38 | 85.3208 | 3506.85
7904 | 136101 | -73672.6 | 39 | 39 | 82.7256 | 3508.53
7905 | 135321 | -68639.1 | 40 | 40 | 81.7179 | 3510.13
7906 | 136419 | -60059.7 | 41 | 41 | 81.8706 | 3511.7
7907 | 135302 | -49473.3 | 43 | 43 | 81.2377 | 3513.14
7908 | 136972 | -41376.3 | 44 | 44 | 81.0784 | 3514.54
7909 | 129401 | -25182.5 | 45 | 45 | 77.784 | 3515.8
7910 | 135601 | -35476.9 | 45 | 45 | 80.5509 | 3516.9
7911 | 135188 | -32640.1 | 46 | 45 | 80.517 | 3517.63
7912 | 130062 | -24795.3 | 46 | 45 | 78.5817 | 3518.85
7913 | 133422 | -42410.5 | 46 | 45 | 84.5002 | 3519.76
7914 | 134398 | -46432.2 | 46 | 45 | 88.6974 | 3520.61
7915 | 133779 | -47747.9 | 46 | 45 | 89.4318 | 3521.91
7916 | 133590 | -50499.7 | 45 | 45 | 89.4126 | 3522.96
7917 | 133266 | -52102.9 | 45 | 45 | 89.3878 | 3524.06
7918 | 133243 | -53630.8 | 45 | 45 | 89.4454 | 3525.05
7919 | 132786 | -56811.7 | 44 | 44 | 88.6354 | 3526.05
7920 | 132631 | -58462.2 | 44 | 44 | 87.8285 | 3527.04
7921 | 132752 | -58934.5 | 44 | 44 | 90.9259 | 9082.74
7922 | 132777 | -60467.8 | 44 | 44 | 90.9961 | 9083.71
7923 | 132646 | -62534.4 | 44 | 44 | 91.0867 | 9083.89
7924 | 132208 | -68420.8 | 42 | 41 | 91.1664 | 9084.53
7925 | 135565 | -74813.1 | 40 | 39 | 95.0993 | 10069.2
7926 | 183564 | -63633.6 | 38 | 36 | 136.337 | 24195.1
7927 | 314865 | -622726 | 37 | 35 | 251.323 | 71351.1
7928 | 384845 | -575665 | 37 | 35 | 275.562 | 86618
7929 | 396042 | -471762 | 36 | 34 | 273.245 | 119824
7930 | 398820 | -451116 | 36 | 34 | 264.797 | 140963
7931 | 387774 | -451723 | 36 | 33 | 255.909 | 143976
7932 | 371272 | -417226 | 36 | 33 | 240.49 | 143974
7933 | 350927 | -410668 | 36 | 33 | 237.862 | 143973
7934 | 384226 | -388742 | 35 | 32 | 258.2 | 143969
7935 | 402792 | -376160 | 35 | 32 | 265.7 | 142109
7936 | 405873 | -389509 | 34 | 31 | 272.908 | 129200
7937 | 399277 | -402820 | 34 | 31 | 279.536 | 105484
7938 | 385489 | -462050 | 33 | 30 | 258.911 | 79133.4
7939 | 298622 | -506400 | 32 | 29 | 188.473 | 49037.9
7940 | 178545 | -11927.6 | 30 | 27 | 126.885 | 35117.5
7941 | 159639 | -18403.4 | 29 | 26 | 111.794 | 31182
7942 | 155334 | -32621.2 | 28 | 26 | 103.81 | 19183.4
7943 | 156849 | -59363.4 | 28 | 25 | 97.9026 | 10379.4
7944 | 148975 | -78088.5 | 27 | 24 | 93.8205 | 9049.62
7945 | 146185 | -96168.5 | 26 | 24 | 92.4963 | 9053.73
7946 | 144372 | -110415 | 25 | 22 | 92.3007 | 9056.91
7947 | 142838 | -126161 | 24 | 21 | 92.1291 | 9059.83
7948 | 141699 | -141183 | 23 | 21 | 91.99 | 9062.3
7949 | 143801 | -151723 | 23 | 20 | 96.1462 | 10048.7
7950 | 190941 | -135500 | 22 | 19 | 137.024 | 24176.1
7951 | 321027 | -866570 | 23 | 20 | 265.72 | 71333.4
7952 | 382778 | -789343 | 23 | 20 | 287.105 | 86601.4
7953 | 401557 | -628196 | 24 | 20 | 271.394 | 119812
7954 | 399943 | -532724 | 27 | 23 | 265.51 | 140952
7955 | 389704 | -501120 | 29 | 24 | 256.97 | 143967
7956 | 376572 | -412593 | 32 | 26 | 241.327 | 143966
7957 | 355377 | -381154 | 33 | 27 | 257.692 | 143964
7958 | 388531 | -327681 | 34 | 27 | 276.102 | 143961
7959 | 406957 | -310235 | 35 | 28 | 284.057 | 142101
7960 | 409792 | -349333 | 33 | 27 | 286.478 | 129193
7961 | 403600 | -418311 | 30 | 25 | 297.719 | 105476
7962 | 395953 | -513958 | 28 | 23 | 261.229 | 79125.3
7963 | 310084 | -559854 | 27 | 23 | 192.55 | 49030.8
7964 | 181494 | -15801.9 | 26 | 22 | 127.797 | 35110.8
7965 | 162419 | -23392.7 | 25 | 21 | 112.433 | 31175.1
7966 | 173856 | -41367.4 | 24 | 21 | 107.04 | 19176.3
7967 | 158078 | -70177.6 | 24 | 21 | 97.8286 | 10372.5
7968 | 151214 | -88180 | 23 | 20 | 93.8087 | 9042.92
7969 | 148354 | -106766 | 23 | 20 | 92.9015 | 9047.19
7970 | 146552 | -120363 | 23 | 20 | 92.7208 | 9050.57
7971 | 145018 | -130649 | 23 | 20 | 92.5797 | 9053.61
7972 | 143728 | -141483 | 23 | 20 | 92.4607 | 9056.25
7973 | 145807 | -149125 | 23 | 20 | 96.199 | 10042.7
7974 | 192986 | -129633 | 23 | 20 | 137.128 | 24170.2
7975 | 322819 | -845743 | 24 | 21 | 264.601 | 71327.5
7976 | 384332 | -757546 | 24 | 21 | 285.271 | 86595.6
7977 | 403101 | -587800 | 25 | 22 | 269.671 | 119806
7978 | 401391 | -492035 | 29 | 25 | 264.57 | 140947
7979 | 393476 | -436279 | 33 | 27 | 256.301 | 143962
7980 | 378778 | -342059 | 37 | 29 | 260.056 | 143960
7981 | 356902 | -313477 | 38 | 30 | 257.323 | 143958
7982 | 403365 | -293367 | 39 | 30 | 277.47 | 143956
7983 | 433590 | -285360 | 40 | 30 | 286.362 | 142096
7984 | 425071 | -299755 | 38 | 30 | 289.456 | 129187
7985 | 405302 | -332571 | 36 | 30 | 297.892 | 105470
7986 | 390900 | -411796 | 34 | 28 | 277.854 | 79119.3
7987 | 302041 | -459105 | 33 | 28 | 185.455 | 49024.2
7988 | 182987 | -11951.2 | 33 | 28 | 127.234 | 35104.1
7989 | 163734 | -16514.3 | 32 | 26 | 111.793 | 31168.3
7990 | 150494 | -20826.1 | 32 | 28 | 101.01 | 19169.1
7991 | 139258 | -21129.9 | 33 | 28 | 92.1854 | 10364.5
7992 | 157285 | -37976.1 | 33 | 29 | 94.6422 | 9033.92
7993 | 153319 | -44193.3 | 33 | 29 | 93.6434 | 9037.38
7994 | 150979 | -52490.4 | 34 | 29 | 93.4196 | 9040.52
7995 | 149156 | -61733.3 | 34 | 28 | 93.2558 | 9043.3
7996 | 147946 | -67948.9 | 34 | 29 | 93.1464 | 9045.67
7997 | 150231 | -72281.1 | 35 | 29 | 97.0258 | 10031.9
7998 | 201647 | -58452.2 | 35 | 29 | 138.501 | 24159.1
7999 | 324231 | -635641 | 31 | 27 | 250.278 | 71316.2
8000 | 385599 | -654608 | 27 | 23 | 279.917 | 86584.1
8001 | 404251 | -584204 | 23 | 20 | 269.273 | 119798
8002 | 402311 | -547531 | 24 | 20 | 266.276 | 140940
8003 | 389963 | -546648 | 24 | 20 | 258.899 | 143956
8004 | 378214 | -483558 | 25 | 20 | 241.556 | 143955
8005 | 356895 | -515424 | 24 | 19 | 242.45 | 143954
8006 | 389554 | -498250 | 22 | 18 | 257.251 | 143952
8007 | 408055 | -533775 | 21 | 17 | 267.646 | 142093
8008 | 410973 | -572465 | 20 | 16 | 276.508 | 129186
8009 | 402718 | -637556 | 18 | 15 | 287.47 | 105471
8010 | 392182 | -716548 | 17 | 14 | 273.567 | 79122.5
8011 | 309589 | -727806 | 17 | 14 | 203.822 | 49028.9
8012 | 181796 | -19525.9 | 17 | 14 | 127.276 | 35108.5
8013 | 171437 | -40659.1 | 17 | 15 | 115.067 | 31172.3
8014 | 172274 | -74992 | 19 | 16 | 106.469 | 19173.2
8015 | 157131 | -106835 | 20 | 17 | 97.376 | 10370.6
8016 | 150911 | -119778 | 21 | 19 | 93.5 | 9041.06
8017 | 148613 | -129530 | 24 | 22 | 92.7196 | 9844.31
8018 | 146654 | -130932 | 26 | 23 | 92.6335 | 9847.56
8019 | 145047 | -129516 | 27 | 25 | 92.5875 | 9850.46
8020 | 143998 | -127790 | 29 | 27 | 92.563 | 9852.99
8021 | 146443 | -126749 | 30 | 28 | 96.3895 | 10938.2
8022 | 194284 | -95681 | 32 | 29 | 137.594 | 26487.7
8023 | 323473 | -675225 | 34 | 32 | 255.161 | 78393
8024 | 385156 | -602498 | 34 | 32 | 279.39 | 95198.5
8025 | 403583 | -480803 | 35 | 32 | 270.158 | 131754
8026 | 401922 | -449942 | 35 | 33 | 267.219 | 155024
8027 | 394536 | -438076 | 36 | 33 | 256.968 | 158342
8028 | 380044 | -406205 | 36 | 33 | 241.778 | 158341
8029 | 357054 | -402056 | 36 | 33 | 238.637 | 158339
8030 | 390262 | -368754 | 35 | 34 | 258.576 | 158338
8031 | 408556 | -355881 | 35 | 34 | 285.623 | 156291
8032 | 411144 | -352535 | 35 | 34 | 293.197 | 142083
8033 | 404080 | -377104 | 34 | 33 | 298.9 | 115978
8034 | 388999 | -421222 | 34 | 33 | 278.269 | 86973.9
8035 | 302031 | -459168 | 34 | 33 | 185.829 | 53848.5
8036 | 182958 | -11201.2 | 33 | 33 | 126.94 | 38526.6
8037 | 163745 | -15959.7 | 33 | 32 | 111.639 | 34194.5
8038 | 150267 | -20324 | 33 | 32 | 100.892 | 20986.5
8039 | 155338 | -23551.8 | 33 | 32 | 95.4122 | 11294.9
8040 | 155431 | -38737.1 | 33 | 32 | 94.5457 | 9830.04
8041 | 152147 | -49253.8 | 33 | 32 | 89.5914 | 9833.51
8042 | 149733 | -58215.7 | 33 | 33 | 89.387 | 9836.69
8043 | 148056 | -66149.6 | 33 | 33 | 89.2519 | 9840.22
8044 | 146533 | -73726.2 | 33 | 33 | 89.1305 | 9842.93
8045 | 145307 | -78951.2 | 33 | 33 | 89.0249 | 9845.5
8046 | 144460 | -85308.3 | 33 | 33 | 88.9665 | 9847.74
8047 | 143129 | -89123.8 | 33 | 33 | 87.2719 | 9849.88
8048 | 130039 | -774514 | 34 | 33 | 120.113 | 9851.91
8049 | 154255 | -705970 | 34 | 33 | 115.756 | 9853.63
8050 | 159236 | -596370 | 35 | 34 | 107.706 | 9846.95
8051 | 155283 | -556721 | 35 | 34 | 104.792 | 9843.41
8052 | 155051 | -519923 | 36 | 35 | 102.204 | 9842.34
8053 | 152082 | -505877 | 36 | 35 | 101.234 | 9841.68
8054 | 149364 | -492722 | 36 | 35 | 100.381 | 9841.4
8055 | 124120 | -11267.9 | 36 | 35 | 77.7759 | 9841.23
8056 | 123202 | -15045.9 | 36 | 35 | 78.4581 | 9841.34
8057 | 123123 | -19434 | 36 | 35 | 82.606 | 9843.89
8058 | 143731 | -37347.4 | 36 | 36 | 92.7142 | 9847.28
8059 | 140872 | -45753.2 | 36 | 35 | 93.6397 | 9849.52
8060 | 139277 | -51620.8 | 36 | 35 | 93.5042 | 9852.37
8061 | 138156 | -61306.4 | 36 | 36 | 93.4026 | 9854.81
8062 | 137085 | -68895.2 | 36 | 35 | 93.312 | 9857.01
8063 | 136469 | -74617.9 | 36 | 35 | 92.4505 | 9859.06
8064 | 135826 | -79404.6 | 36 | 35 | 91.5862 | 9860.94
8065 | 134932 | -85305.4 | 36 | 35 | 86.9966 | 3748.7
8066 | 134522 | -91682.9 | 36 | 35 | 86.9471 | 3750.43
8067 | 133788 | -94355.4 | 36 | 35 | 86.8914 | 3752.28
8068 | 133425 | -97824.4 | 36 | 35 | 86.8606 | 3754.01
8069 | 132790 | -100273 | 36 | 34 | 86.8172 | 3755.7
8070 | 132407 | -103693 | 36 | 34 | 86.7871 | 3757.34
8071 | 132239 | -107432 | 36 | 34 | 85.1782 | 3758.93
8072 | 131549 | -110649 | 35 | 34 | 82.611 | 3760.48
8073 | 131311 | -106553 | 35 | 33 | 81.493 | 3762.01
8074 | 131619 | -96620.1 | 36 | 34 | 81.7346 | 3763.49
8075 | 131050 | -90542.5 | 36 | 34 | 81.6039 | 3764.93
8076 | 130884 | -81995.3 | 37 | 34 | 81.4553 | 3766.36
8077 | 131361 | -80541.6 | 37 | 34 | 81.5184 | 3767.65
8078 | 130510 | -84567.8 | 36 | 34 | 81.5812 | 3768.93
8079 | 130157 | -92182.1 | 36 | 33 | 81.7138 | 3770.15
8080 | 129976 | -103511 | 36 | 33 | 82.444 | 3771.37
8081 | 129406 | -114727 | 35 | 33 | 85.6552 | 3772.64
8082 | 129115 | -121998 | 35 | 33 | 89.6736 | 3773.97
8083 | 128858 | -126690 | 35 | 33 | 90.4376 | 3775.32
8084 | 128612 | -128806 | 35 | 33 | 90.4185 | 3776.61
8085 | 128386 | -131195 | 35 | 33 | 90.3997 | 3777.91
8086 | 128238 | -133264 | 35 | 33 | 90.3875 | 3779.16
8087 | 127920 | -137024 | 34 | 32 | 89.5622 | 3780.38
8088 | 127666 | -139463 | 34 | 32 | 88.7291 | 3781.59
8089 | 127795 | -141291 | 33 | 31 | 91.6863 | 9896.79
8090 | 127738 | -146842 | 33 | 31 | 91.6601 | 9897.96
8091 | 127852 | -153305 | 32 | 30 | 91.6639 | 9898.32
8092 | 127361 | -161484 | 30 | 29 | 91.6158 | 9899.18
8093 | 130346 | -172413 | 28 | 27 | 95.3889 | 10983.1
8094 | 177773 | -151749 | 26 | 25 | 136.396 | 26531.5
8095 | 312320 | -935579 | 27 | 26 | 271.118 | 78436
8096 | 374733 | -810962 | 27 | 27 | 292.01 | 95240.7
8097 | 393875 | -663496 | 28 | 27 | 281.678 | 131788
8098 | 392472 | -613799 | 30 | 28 | 272.866 | 155056
8099 | 382950 | -599893 | 31 | 29 | 264.288 | 158373
8100 | 364759 | -527982 | 33 | 30 | 245.437 | 158371
8101 | 348934 | -507589 | 34 | 31 | 242.738 | 158369
8102 | 382686 | -428568 | 36 | 32 | 259.291 | 158366
8103 | 412264 | -402889 | 37 | 32 | 270.551 | 156319
8104 | 414512 | -376229 | 38 | 34 | 275.209 | 142110
8105 | 414287 | -374214 | 39 | 35 | 281.349 | 116004
8106 | 386272 | -383191 | 40 | 36 | 259.098 | 86998.7
8107 | 322761 | -474929 | 38 | 34 | 186.416 | 53871.8
8108 | 177403 | -9020.24 | 35 | 31 | 125.565 | 38548.8
8109 | 158373 | -15389.6 | 33 | 28 | 111.065 | 34217.4
8110 | 145302 | -21029.9 | 31 | 28 | 100.58 | 21010.8
8111 | 154292 | -55608.5 | 30 | 26 | 97.7937 | 11319.7
8112 | 146723 | -75569.7 | 28 | 24 | 93.7174 | 9855.2
8113 | 143846 | -92382.6 | 27 | 24 | 92.3386 | 9859.31
8114 | 141990 | -113379 | 25 | 23 | 92.1247 | 9862.48
8115 | 140644 | -130533 | 24 | 21 | 91.9488 | 9865.4
8116 | 139525 | -148845 | 23 | 20 | 91.7969 | 9867.93
8117 | 141641 | -163619 | 21 | 19 | 95.9237 | 10953.3
8118 | 188574 | -150503 | 20 | 17 | 136.793 | 26503
8119 | 319653 | -935244 | 20 | 17 | 269.573 | 78408.6
8120 | 381641 | -846037 | 20 | 17 | 291.421 | 95214.4
8121 | 400522 | -724247 | 20 | 17 | 277.992 | 131770
8122 | 398597 | -681751 | 21 | 18 | 274.566 | 155040
8123 | 387371 | -694764 | 22 | 19 | 268.119 | 158359
8124 | 366282 | -604235 | 23 | 19 | 249.477 | 158358
8125 | 353606 | -582876 | 23 | 19 | 246.65 | 158356
8126 | 386628 | -554757 | 22 | 19 | 260.245 | 158353
8127 | 405102 | -539078 | 22 | 19 | 266.475 | 156307
8128 | 408068 | -571698 | 21 | 18 | 270.976 | 142100
8129 | 402253 | -633456 | 20 | 17 | 286.507 | 115996
8130 | 389466 | -711602 | 19 | 16 | 273.543 | 86993.3
8131 | 307715 | -742631 | 18 | 16 | 204.81 | 53868.4
8132 | 179515 | -19328.3 | 18 | 15 | 127.122 | 38546.4
8133 | 184412 | -51907.3 | 17 | 14 | 118.053 | 34213.7
8134 | 166244 | -94728.4 | 16 | 14 | 105.999 | 21007
8135 | 152295 | -135080 | 16 | 14 | 96.9753 | 11317.7
8136 | 146127 | -156272 | 15 | 13 | 93.009 | 9853.97
8137 | 143800 | -177940 | 15 | 13 | 92.173 | 9858.36
8138 | 142216 | -194107 | 14 | 13 | 92.0336 | 9861.73
8139 | 140925 | -205142 | 14 | 12 | 92.5141 | 9864.73
8140 | 139780 | -216337 | 14 | 12 | 93.1326 | 9867.42
8141 | 141689 | -228706 | 13 | 12 | 97.7407 | 10953
8142 | 188288 | -207721 | 13 | 12 | 136.271 | 26502.9
8143 | 319939 | -1081220 | 14 | 13 | 278.57 | 78408.7
8144 | 382006 | -965776 | 15 | 13 | 297.65 | 95214.6
8145 | 400979 | -790816 | 16 | 14 | 282.467 | 131768
8146 | 399009 | -703798 | 18 | 16 | 275.872 | 155038
8147 | 380532 | -652303 | 21 | 18 | 265.053 | 158356
8148 | 368544 | -564846 | 23 | 19 | 247.75 | 158356
8149 | 354014 | -551980 | 23 | 20 | 245.663 | 158354
8150 | 387138 | -493080 | 24 | 20 | 276.509 | 158351
8151 | 405586 | -495878 | 24 | 20 | 283.556 | 156304
8152 | 408607 | -526208 | 23 | 20 | 268.061 | 142097
8153 | 402045 | -607537 | 21 | 19 | 285.213 | 115993
8154 | 392153 | -692399 | 20 | 17 | 272.479 | 86990.3
8155 | 309742 | -726408 | 19 | 17 | 203.798 | 53865.6
8156 | 179907 | -19527.7 | 18 | 16 | 127.178 | 38543.7
8157 | 185444 | -47663.6 | 17 | 15 | 118.109 | 34211.1
8158 | 166989 | -93285.3 | 16 | 15 | 106.047 | 21004.3
8159 | 152857 | -130546 | 15 | 14 | 97.0201 | 11314.9
8160 | 146533 | -157070 | 14 | 13 | 93.0418 | 9851.17
8161 | 144233 | -178973 | 14 | 13 | 92.0493 | 9855.56
8162 | 142675 | -193068 | 14 | 13 | 91.9178 | 9859.04
8163 | 141349 | -201767 | 14 | 13 | 92.2643 | 9862.1
8164 | 140327 | -211992 | 14 | 13 | 92.8274 | 9864.86
8165 | 142106 | -217575 | 15 | 14 | 97.0037 | 10950.5
8166 | 188858 | -196325 | 15 | 14 | 136.342 | 26500.3
8167 | 320209 | -1048080 | 16 | 15 | 276.734 | 78406.1
8168 | 382257 | -926930 | 18 | 16 | 297.116 | 95212
8169 | 401303 | -789389 | 19 | 17 | 284.205 | 131765
8170 | 399270 | -717385 | 20 | 18 | 277.254 | 155035
8171 | 380556 | -707717 | 20 | 18 | 268.215 | 158354
8172 | 364405 | -609612 | 21 | 18 | 249.955 | 158353
8173 | 354092 | -583490 | 22 | 19 | 247.446 | 158351
8174 | 387043 | -533729 | 22 | 19 | 259.537 | 158349
8175 | 405632 | -509844 | 23 | 20 | 284.117 | 156302
8176 | 408651 | -548147 | 22 | 19 | 269.51 | 142096
8177 | 401788 | -633799 | 20 | 18 | 286.449 | 115992
8178 | 392343 | -719693 | 19 | 17 | 273.908 | 86989
8179 | 309886 | -753434 | 18 | 16 | 205.394 | 53864.4
8180 | 179755 | -19725.8 | 16 | 15 | 127.106 | 38542.4
8181 | 184900 | -52497.4 | 15 | 14 | 117.997 | 34209.7
8182 | 166592 | -101885 | 14 | 13 | 105.956 | 21002.9
8183 | 152461 | -143874 | 12 | 12 | 96.9439 | 11313.7
8184 | 146228 | -167726 | 11 | 10 | 92.9432 | 9850.05
8185 | 143903 | -194094 | 10 | 9 | 92.1026 | 9854.5
8186 | 142240 | -207152 | 10 | 9 | 92.5726 | 9857.97
8187 | 141507 | -222839 | 9 | 8 | 93.5114 | 9861.12
8188 | 139563 | -229059 | 9 | 8 | 93.9947 | 9863.91
8189 | 143528 | -242778 | 9 | 8 | 98.5087 | 10949.6
8190 | 187891 | -211279 | 9 | 8 | 136.294 | 26499.6
8191 | 319479 | -1119880 | 10 | 10 | 279.725 | 78405.5
8192 | 381538 | -984383 | 12 | 11 | 297.446 | 95211.3
8193 | 400810 | -804492 | 13 | 12 | 282.558 | 131765
8194 | 398706 | -709063 | 16 | 14 | 275.821 | 155035
8195 | 380064 | -690521 | 18 | 17 | 266.69 | 158354
8196 | 366660 | -584626 | 21 | 18 | 248.776 | 158353
8197 | 353658 | -562135 | 22 | 19 | 246.682 | 158351
8198 | 386757 | -486527 | 24 | 20 | 277.043 | 158348
8199 | 405340 | -462052 | 25 | 21 | 284.386 | 156302
8200 | 408351 | -501635 | 23 | 20 | 287.117 | 142095
8201 | 401611 | -571667 | 21 | 18 | 281.944 | 115991
8202 | 396925 | -678616 | 19 | 17 | 271.075 | 86988
8203 | 311640 | -707888 | 19 | 17 | 202.788 | 53863.4
8204 | 179766 | -19726.2 | 19 | 17 | 127.279 | 38541.6
8205 | 186289 | -41037 | 19 | 17 | 118.31 | 34208.7
8206 | 167785 | -76192 | 20 | 18 | 106.23 | 21001.5
8207 | 153681 | -103551 | 21 | 19 | 97.1971 | 11311.8
8208 | 147319 | -119642 | 22 | 19 | 93.2742 | 9847.83
8209 | 144578 | -134419 | 22 | 19 | 88.4032 | 9851.98
8210 | 142889 | -145630 | 23 | 20 | 88.2746 | 9855.25
8211 | 142277 | -156075 | 23 | 20 | 88.2358 | 9858.67
8212 | 140528 | -161627 | 23 | 20 | 88.1162 | 9861.39
8213 | 139740 | -167163 | 24 | 20 | 88.0506 | 9863.93
8214 | 138578 | -171460 | 24 | 20 | 87.9843 | 9866.22
8215 | 137724 | -175209 | 24 | 21 | 86.3314 | 9868.43
8216 | 124479 | -1014070 | 25 | 21 | 139.31 | 9870.55
8217 | 129357 | -883113 | 25 | 21 | 129.124 | 9872.31
8218 | 126214 | -769135 | 26 | 22 | 119.814 | 9859.29
8219 | 125449 | -717715 | 27 | 23 | 115.703 | 9855.54
8220 | 124725 | -676058 | 28 | 23 | 112.432 | 9853.57
8221 | 124498 | -647065 | 29 | 24 | 110.567 | 9852.53
8222 | 123671 | -630663 | 29 | 24 | 109.376 | 9851.87
8223 | 121207 | -17050.7 | 30 | 24 | 78.4717 | 9851.38
8224 | 129201 | -38774.9 | 30 | 25 | 82.2335 | 9851.21
8225 | 139962 | -62886.2 | 30 | 25 | 88.3631 | 9855.57
8226 | 136222 | -85637.6 | 30 | 25 | 92.1685 | 9860.46
8227 | 134951 | -101854 | 30 | 25 | 92.862 | 9863.72
8228 | 133731 | -111258 | 30 | 25 | 92.7638 | 9866.79
8229 | 132992 | -119894 | 30 | 25 | 92.6937 | 9869.19
8230 | 132489 | -125480 | 30 | 26 | 92.6456 | 9871.4
8231 | 132079 | -129763 | 30 | 26 | 91.8123 | 9873.43
8232 | 131431 | -132718 | 30 | 25 | 90.9698 | 9875.33
8233 | 130828 | -138377 | 30 | 26 | 86.4267 | 3763.12
8234 | 130329 | -144961 | 29 | 25 | 86.3818 | 3764.85
8235 | 129793 | -152384 | 29 | 25 | 86.329 | 3766.7
8236 | 129606 | -157325 | 29 | 25 | 86.3043 | 3768.39
8237 | 128984 | -163094 | 28 | 25 | 86.2641 | 3770.06
8238 | 128568 | -166732 | 28 | 25 | 86.2222 | 3771.72
8239 | 128898 | -169581 | 29 | 25 | 84.6458 | 3773.33
8240 | 127954 | -169615 | 29 | 26 | 82.1306 | 3774.88
8241 | 127953 | -164520 | 30 | 26 | 81.2477 | 3776.44
8242 | 127764 | -131796 | 31 | 27 | 80.5134 | 3777.91
8243 | 128948 | -111143 | 33 | 29 | 80.5514 | 3779.34
8244 | 128321 | -94118.4 | 34 | 29 | 80.5536 | 3780.7
8245 | 128423 | -96102.4 | 34 | 30 | 80.6172 | 3781.82
8246 | 128112 | -93186 | 35 | 30 | 80.6017 | 3782.77
8247 | 128410 | -104280 | 35 | 30 | 80.8413 | 3783.59
8248 | 127320 | -112107 | 34 | 29 | 81.4627 | 3784.68
8249 | 126925 | -135767 | 33 | 29 | 85.3263 | 3785.71
8250 | 126611 | -150651 | 32 | 28 | 89.3812 | 3786.92
8251 | 126444 | -158194 | 32 | 28 | 90.1423 | 3788.12
8252 | 126250 | -163330 | 32 | 28 | 90.1141 | 3789.33
8253 | 126036 | -166350 | 32 | 28 | 90.0921 | 3790.5
8254 | 125920 | -171223 | 31 | 28 | 90.0767 | 3791.67
8255 | 125718 | -174844 | 31 | 27 | 89.2455 | 3792.8
8256 | 125526 | -180640 | 30 | 27 | 88.788 | 3793.91
8257 | 125697 | -185019 | 29 | 26 | 91.9814 | 9909.03
8258 | 125620 | -191628 | 28 | 26 | 92.3195 | 9910.14
8259 | 125446 | -197291 | 27 | 25 | 92.7052 | 9910.41
8260 | 125356 | -201073 | 28 | 26 | 92.8468 | 9911.21
8261 | 128571 | -203697 | 28 | 27 | 96.7778 | 10995
8262 | 176101 | -163534 | 29 | 27 | 136.137 | 26543.4
8263 | 311527 | -916525 | 31 | 29 | 271.141 | 78447.7
8264 | 374206 | -758082 | 32 | 30 | 288.048 | 95252.2
8265 | 393067 | -557926 | 34 | 32 | 269.632 | 131795
8266 | 391940 | -457223 | 37 | 34 | 264.562 | 155064
8267 | 401334 | -412195 | 40 | 36 | 256.818 | 158380
8268 | 411122 | -374599 | 43 | 38 | 243.582 | 158377
8269 | 386878 | -340068 | 44 | 39 | 241.589 | 158374
8270 | 438420 | -288385 | 46 | 40 | 262.857 | 158371
8271 | 456958 | -279240 | 47 | 41 | 272.718 | 156323
8272 | 450051 | -285895 | 46 | 40 | 275.282 | 142113
8273 | 457542 | -311167 | 44 | 40 | 285.119 | 116005
8274 | 413573 | -338488 | 43 | 39 | 261.66 | 86999.3
8275 | 347371 | -415662 | 43 | 40 | 184.304 | 53872.5
8276 | 178118 | 0 | 44 | 41 | 121.536 | 38549.9
8277 | 159068 | -8290.85 | 44 | 42 | 109.452 | 34218.4
8278 | 145840 | -11512.2 | 45 | 43 | 98.6643 | 21012.2
8279 | 135010 | -11765.7 | 47 | 44 | 90.051 | 11320.1
8280 | 130549 | -12400.4 | 48 | 45 | 86.4127 | 9854.82
8281 | 129292 | -11749.5 | 48 | 46 | 85.1321 | 9857.4
8282 | 141377 | -13373.6 | 49 | 46 | 87.8854 | 9859.25
8283 | 137739 | -12681.4 | 49 | 46 | 88.141 | 9860.73
8284 | 139414 | -13227.6 | 49 | 46 | 87.6737 | 9861.93
8285 | 141577 | -13782.6 | 49 | 46 | 91.8808 | 10946.3
8286 | 187026 | -12634.3 | 49 | 46 | 132.458 | 26494.8
8287 | 323333 | -370558 | 50 | 47 | 241.979 | 78399.1
8288 | 433631 | -330134 | 50 | 47 | 278.701 | 95204.1
8289 | 448556 | -240784 | 51 | 48 | 281.903 | 131764
8290 | 446857 | -203042 | 52 | 49 | 272.183 | 155030
8291 | 425257 | -149349 | 54 | 50 | 262.253 | 158346
8292 | 406463 | -128345 | 55 | 51 | 247.434 | 158342
8293 | 399813 | -116332 | 55 | 51 | 246.014 | 158339
8294 | 442661 | -101428 | 55 | 52 | 264.493 | 158336
8295 | 466433 | -96369.9 | 55 | 52 | 278.932 | 156288
8296 | 480426 | -97060.1 | 54 | 52 | 282.622 | 142079
8297 | 469067 | -97384.4 | 54 | 51 | 285.925 | 115973
8298 | 434761 | -116365 | 53 | 51 | 263.532 | 86968
8299 | 322434 | -186507 | 51 | 48 | 184.316 | 53842
8300 | 184152 | 0 | 48 | 44 | 117.634 | 38519.9
8301 | 164726 | 0 | 46 | 41 | 102.993 | 34188
8302 | 151302 | -9159.3 | 40 | 36 | 99.5662 | 20980.3
8303 | 140024 | 0 | 34 | 31 | 83.2243 | 11287.2
8304 | 135011 | -21262.2 | 28 | 26 | 88.5196 | 9821.94
8305 | 149713 | -17152.9 | 25 | 23 | 86.1714 | 9824.98
8306 | 153411 | -51350.4 | 23 | 21 | 93.6101 | 9827.98
8307 | 151078 | -65845.5 | 20 | 18 | 93.3303 | 9831.23
8308 | 148630 | -85186.8 | 20 | 18 | 92.9824 | 9834.87
8309 | 149946 | -109154 | 20 | 18 | 96.5654 | 10921.3
8310 | 196789 | -101125 | 20 | 18 | 137.429 | 26472
8311 | 324398 | -785177 | 20 | 19 | 259.623 | 78378.7
8312 | 385360 | -735922 | 21 | 19 | 286.925 | 95185.3
8313 | 404145 | -640713 | 21 | 20 | 277.252 | 131748
8314 | 401837 | -637709 | 21 | 20 | 274.782 | 155019
8315 | 391195 | -649347 | 22 | 20 | 267.809 | 158339
8316 | 376120 | -604206 | 22 | 20 | 249.964 | 158339
8317 | 356073 | -600778 | 21 | 19 | 247.476 | 158337
8318 | 388976 | -570929 | 20 | 18 | 261.1 | 158335
8319 | 407370 | -555000 | 19 | 17 | 266.931 | 156289
8320 | 410328 | -623867 | 17 | 15 | 274.211 | 142083
8321 | 400435 | -670582 | 16 | 14 | 289.236 | 115980
8322 | 392337 | -771173 | 14 | 12 | 276.309 | 86978.2
8323 | 309859 | -790038 | 13 | 11 | 207.27 | 53854
8324 | 180937 | -19460.2 | 12 | 10 | 127.005 | 38532.5
8325 | 186142 | -69663.5 | 11 | 9 | 117.888 | 34200
8326 | 168383 | -111532 | 10 | 9 | 105.901 | 20993
8327 | 154600 | -157701 | 10 | 8 | 96.9229 | 11304.2
8328 | 148229 | -184535 | 9 | 8 | 92.9497 | 9840.72
8329 | 145750 | -202295 | 9 | 7 | 91.9725 | 9845.42
8330 | 143971 | -218398 | 8 | 7 | 92.9979 | 9849.21
8331 | 142455 | -229091 | 8 | 7 | 93.6775 | 9852.62
8332 | 141333 | -241463 | 8 | 7 | 94.3188 | 9855.73
8333 | 142845 | -251115 | 8 | 7 | 98.689 | 10941.7
8334 | 189292 | -231216 | 8 | 7 | 136.317 | 26492
8335 | 320090 | -1160720 | 8 | 7 | 282.145 | 78398.2
8336 | 382054 | -1081910 | 8 | 7 | 304.006 | 95204.4
8337 | 401243 | -925673 | 8 | 7 | 290.424 | 131758
8338 | 399081 | -870074 | 9 | 8 | 286.86 | 155030
8339 | 380203 | -821411 | 11 | 9 | 273.994 | 158349
8340 | 358965 | -729279 | 12 | 10 | 255.547 | 158349
8341 | 353574 | -707252 | 13 | 11 | 253.435 | 158347
8342 | 386413 | -646997 | 14 | 12 | 264.825 | 158344
8343 | 405183 | -632321 | 15 | 12 | 271.285 | 156298
8344 | 408227 | -688241 | 13 | 11 | 276.552 | 142092
8345 | 398288 | -763632 | 12 | 10 | 292.194 | 115989
8346 | 390921 | -874159 | 10 | 8 | 281.361 | 86986.4
8347 | 309499 | -893883 | 9 | 7 | 213.256 | 53861.8
8348 | 213982 | -19723.6 | 7 | 6 | 133.587 | 38539.8
8349 | 180900 | -95742.5 | 6 | 5 | 117.266 | 34206.8
8350 | 164403 | -153360 | 5 | 4 | 105.36 | 21001.4
8351 | 150674 | -197062 | 4 | 3 | 96.4055 | 11312.7
8352 | 144773 | -225633 | 3 | 2 | 94.0629 | 9849.21
8353 | 142423 | -245725 | 3 | 2 | 94.5887 | 9853.88
8354 | 140831 | -257656 | 3 | 2 | 95.4969 | 9857.58
8355 | 139419 | -270503 | 3 | 2 | 96.4551 | 9860.98
8356 | 138581 | -280489 | 3 | 2 | 97.003 | 9864.05
8357 | 139859 | -287846 | 4 | 3 | 101.251 | 10950
8358 | 186156 | -264936 | 4 | 3 | 137.766 | 26500.1
8359 | 318489 | -1239250 | 6 | 5 | 286.043 | 78406.3
8360 | 380625 | -1122410 | 7 | 6 | 305.93 | 95212.3
8361 | 399955 | -942477 | 9 | 8 | 298.216 | 131764
8362 | 397861 | -867465 | 11 | 10 | 302.069 | 155035
8363 | 379251 | -811834 | 14 | 12 | 273.785 | 158353
8364 | 367607 | -739430 | 16 | 14 | 257.406 | 158353
8365 | 352753 | -731924 | 17 | 15 | 256.254 | 158351
8366 | 385881 | -654084 | 19 | 16 | 266.944 | 158348
8367 | 404615 | -633037 | 20 | 17 | 275.797 | 156301
8368 | 407663 | -633645 | 20 | 18 | 282.47 | 142095
8369 | 398077 | -665111 | 20 | 18 | 289.925 | 115991
8370 | 386339 | -715892 | 20 | 18 | 274.01 | 86987.9
8371 | 304967 | -728463 | 20 | 18 | 204.125 | 53863
8372 | 179299 | -19594.3 | 20 | 18 | 127.232 | 38540.7
8373 | 185222 | -43752.6 | 20 | 18 | 118.273 | 34208
8374 | 166681 | -82302.1 | 19 | 17 | 106.212 | 21001
8375 | 152553 | -117095 | 18 | 16 | 97.1941 | 11311.4
8376 | 146310 | -141384 | 17 | 15 | 93.1787 | 9847.53
8377 | 143616 | -167352 | 16 | 15 | 88.2449 | 9851.7
8378 | 141900 | -183859 | 15 | 14 | 88.0751 | 9854.98
8379 | 140475 | -199469 | 14 | 13 | 88.1456 | 9858.6
8380 | 139225 | -213072 | 13 | 12 | 88.9648 | 9861.48
8381 | 138018 | -226456 | 12 | 11 | 89.8944 | 9864.26
8382 | 136852 | -238268 | 11 | 10 | 90.4841 | 9866.87
8383 | 135919 | -242099 | 13 | 12 | 89.0327 | 9869.42
8384 | 123547 | -1156120 | 15 | 14 | 148.666 | 9871.88
8385 | 122858 | -963534 | 17 | 16 | 134.622 | 9873.99
8386 | 122363 | -787601 | 19 | 18 | 120.443 | 9859.91
8387 | 121902 | -688599 | 22 | 20 | 113.386 | 9856.11
8388 | 121417 | -622306 | 24 | 21 | 108.899 | 9853.89
8389 | 121072 | -581018 | 25 | 22 | 105.802 | 9852.71
8390 | 120682 | -548089 | 27 | 23 | 103.436 | 9851.95
8391 | 121159 | -19396.1 | 28 | 24 | 76.8947 | 9851.38
8392 | 131472 | -38655 | 25 | 22 | 80.3593 | 9851.14
8393 | 142097 | -52471.6 | 23 | 20 | 88.3001 | 9855.83
8394 | 137178 | -85293.1 | 20 | 18 | 92.1383 | 9859.32
8395 | 137877 | -103199 | 18 | 17 | 93.1065 | 9862.86
8396 | 132515 | -113025 | 17 | 16 | 92.8402 | 9865.93
8397 | 133554 | -133880 | 15 | 14 | 92.9601 | 9868.69
8398 | 130606 | -148308 | 13 | 13 | 92.7883 | 9870.83
8399 | 131049 | -161413 | 12 | 11 | 92.0366 | 9872.79
8400 | 129212 | -170537 | 10 | 10 | 91.1276 | 9874.45
8401 | 128457 | -178995 | 11 | 11 | 86.5781 | 3761.99
8402 | 128138 | -183560 | 12 | 11 | 86.8273 | 3763.45
8403 | 127414 | -188942 | 13 | 12 | 87.164 | 3765
8404 | 126975 | -195427 | 13 | 13 | 87.5533 | 3766.39
8405 | 126555 | -200845 | 14 | 13 | 87.5061 | 3767.75
8406 | 126129 | -222841 | 14 | 13 | 88.4048 | 3769.03
8407 | 125753 | -234323 | 15 | 14 | 87.5494 | 3770.27
8408 | 125386 | -240532 | 15 | 14 | 85.4693 | 3772.08
8409 | 125132 | -226232 | 16 | 15 | 83.245 | 3774.16
8410 | 125165 | -198739 | 19 | 17 | 81.7184 | 3776.23
8411 | 126603 | -183221 | 21 | 20 | 80.7742 | 3778.18
8412 | 125382 | -141645 | 24 | 22 | 80.0749 | 3780.02
8413 | 125742 | -138097 | 26 | 23 | 80.2638 | 3781.68
8414 | 125467 | -126732 | 27 | 24 | 80.3678 | 3783.13
8415 | 127327 | -130094 | 29 | 25 | 80.6508 | 3783.9
8416 | 125145 | -142086 | 28 | 25 | 82.0012 | 3784.93
8417 | 125896 | -156933 | 27 | 25 | 85.4843 | 3785.79
8418 | 124715 | -160332 | 26 | 24 | 89.4623 | 3786.76
8419 | 124626 | -167988 | 25 | 23 | 90.2853 | 3787.71
8420 | 124327 | -173379 | 24 | 22 | 90.1147 | 3788.57
8421 | 124119 | -197494 | 23 | 21 | 90.8379 | 3789.39
8422 | 123924 | -198162 | 22 | 20 | 91.4762 | 3790.18
8423 | 125501 | -219945 | 21 | 19 | 91.7513 | 3791.54
8424 | 123476 | -220516 | 20 | 18 | 91.1111 | 3792.86
8425 | 130571 | -231378 | 19 | 18 | 94.8764 | 9908.37
8426 | 123559 | -214646 | 19 | 18 | 93.9433 | 9909.69
8427 | 125779 | -248893 | 18 | 17 | 95.288 | 9910.12
8428 | 123179 | -246406 | 18 | 17 | 95.3824 | 9910.54
8429 | 129996 | -264037 | 18 | 17 | 99.779 | 10994.7
8430 | 173384 | -213542 | 18 | 17 | 135.716 | 26543.2
8431 | 309127 | -1112070 | 19 | 18 | 281.34 | 78448
8432 | 371730 | -950076 | 20 | 19 | 299.421 | 95252.5
8433 | 391141 | -804821 | 21 | 20 | 290.868 | 131795
8434 | 389669 | -752970 | 23 | 21 | 281.387 | 155065
8435 | 374339 | -744609 | 24 | 23 | 272.872 | 158382
8436 | 357884 | -667909 | 26 | 23 | 255.266 | 158380
8437 | 346239 | -658640 | 26 | 24 | 251.974 | 158377
8438 | 379679 | -587692 | 27 | 25 | 264.392 | 158374
8439 | 398461 | -570389 | 27 | 26 | 268.909 | 156327
8440 | 401808 | -546662 | 28 | 27 | 276.657 | 142119
8441 | 393025 | -533028 | 30 | 28 | 282.198 | 116014
8442 | 379679 | -558691 | 31 | 29 | 265.154 | 87010.1
8443 | 292975 | -591821 | 31 | 29 | 194.847 | 53883.9
8444 | 175251 | -14366.4 | 32 | 30 | 127.386 | 38561.3
8445 | 156361 | -23210 | 32 | 30 | 112.095 | 34228.7
8446 | 164355 | -42485 | 31 | 30 | 106.471 | 21022.2
8447 | 149227 | -69777 | 31 | 30 | 97.359 | 11331.4
8448 | 142803 | -83559.8 | 30 | 29 | 93.3533 | 9867.07
8449 | 140468 | -100774 | 30 | 30 | 92.0767 | 9870.75
8450 | 139270 | -109023 | 31 | 30 | 91.9554 | 9873.58
8451 | 138338 | -117997 | 31 | 30 | 91.8948 | 9876.03
8452 | 137534 | -123837 | 31 | 30 | 91.8412 | 9878.1
8453 | 140209 | -126563 | 32 | 30 | 96.0603 | 10963
8454 | 187757 | -100803 | 32 | 30 | 137.135 | 26512.1
8455 | 319638 | -735749 | 32 | 30 | 258.499 | 78417.2
8456 | 381534 | -668683 | 31 | 30 | 282.979 | 95222.4
8457 | 400396 | -554760 | 31 | 31 | 275.964 | 131776
8458 | 398345 | -529505 | 31 | 30 | 266.356 | 155045
8459 | 389959 | -541199 | 30 | 30 | 260.414 | 158362
8460 | 374379 | -497463 | 30 | 30 | 242.832 | 158361
8461 | 353716 | -502349 | 30 | 30 | 241.521 | 158359
8462 | 386873 | -456649 | 30 | 29 | 257.896 | 158357
8463 | 405227 | -451768 | 30 | 29 | 265.519 | 156309
8464 | 408234 | -455431 | 30 | 28 | 272.56 | 142101
8465 | 400854 | -487636 | 29 | 28 | 279.63 | 115997
8466 | 388005 | -537050 | 29 | 27 | 263.179 | 86992.8
8467 | 301302 | -565488 | 29 | 28 | 192.621 | 53867.5
8468 | 180345 | -14824 | 30 | 28 | 127.725 | 38545.2
8469 | 161240 | -22810.4 | 30 | 28 | 112.437 | 34213.2
8470 | 171705 | -35145.3 | 30 | 28 | 106.988 | 21006.3
8471 | 156002 | -59587.7 | 30 | 28 | 97.8366 | 11315.5
8472 | 149208 | -69412.3 | 30 | 28 | 93.8166 | 9851.32
8473 | 146323 | -88106.8 | 28 | 26 | 92.9446 | 9855.26
8474 | 144511 | -105608 | 26 | 24 | 92.7478 | 9858.28
8475 | 142991 | -125727 | 24 | 22 | 92.552 | 9861.04
8476 | 141805 | -141662 | 23 | 22 | 92.3862 | 9863.39
8477 | 143956 | -153791 | 23 | 21 | 96.0947 | 10948.8
8478 | 190967 | -135505 | 22 | 20 | 137.033 | 26498.4
8479 | 321416 | -894293 | 22 | 20 | 267.142 | 78404.1
8480 | 383172 | -826547 | 21 | 20 | 292.446 | 95209.9
8481 | 402053 | -719255 | 21 | 19 | 282.993 | 131766
8482 | 400079 | -683901 | 22 | 20 | 276.904 | 155036
8483 | 385614 | -670300 | 23 | 21 | 267.746 | 158355
8484 | 371942 | -601508 | 24 | 21 | 249.264 | 158354
8485 | 354821 | -628846 | 23 | 21 | 249.611 | 158352
8486 | 387765 | -585080 | 23 | 21 | 263.876 | 158349
8487 | 406227 | -583664 | 22 | 20 | 269.392 | 156303
8488 | 409137 | -596306 | 21 | 19 | 280.096 | 142096
8489 | 399567 | -627071 | 21 | 19 | 287.517 | 115993
8490 | 390063 | -697648 | 20 | 18 | 272.937 | 86990
8491 | 306661 | -709523 | 20 | 18 | 202.913 | 53865.1
8492 | 180482 | -19052.6 | 20 | 18 | 127.387 | 38543.2
8493 | 187064 | -40474.4 | 20 | 18 | 118.489 | 34210.5
8494 | 168328 | -75720.8 | 19 | 18 | 106.415 | 21003.4
8495 | 154114 | -104949 | 18 | 17 | 97.3704 | 11313.7
8496 | 147734 | -129993 | 17 | 16 | 93.3919 | 9849.75
8497 | 145265 | -146882 | 17 | 16 | 92.4288 | 9853.92
8498 | 143726 | -161855 | 17 | 16 | 92.2944 | 9857.17
8499 | 142428 | -170806 | 17 | 16 | 92.1668 | 9860.01
8500 | 141254 | -182550 | 16 | 15 | 92.0509 | 9862.5
8501 | 143184 | -188583 | 16 | 15 | 95.9105 | 10947.9
8502 | 198477 | -167604 | 15 | 14 | 137.475 | 26497.6
8503 | 320722 | -980412 | 16 | 15 | 271.641 | 78403.3
8504 | 382751 | -878923 | 17 | 16 | 294.397 | 95209
8505 | 401808 | -744576 | 18 | 17 | 304.334 | 131764
8506 | 399747 | -704641 | 19 | 18 | 295.681 | 155034
8507 | 386385 | -689471 | 21 | 19 | 287.424 | 158353
8508 | 369692 | -599915 | 22 | 20 | 251.816 | 158352
8509 | 354558 | -586369 | 22 | 20 | 247.098 | 158350
8510 | 387504 | -570910 | 22 | 20 | 263.312 | 158347
8511 | 406127 | -563456 | 22 | 20 | 269.353 | 156299
8512 | 409098 | -571038 | 22 | 20 | 276.549 | 142092
8513 | 400640 | -600696 | 22 | 20 | 286.186 | 115989
8514 | 390154 | -659280 | 22 | 20 | 271.062 | 86985.7
8515 | 306291 | -674132 | 22 | 20 | 200.942 | 53860.8
8516 | 180608 | -17353.5 | 22 | 21 | 127.536 | 38538.5
8517 | 178620 | -30182 | 22 | 21 | 115.536 | 34206.1
8518 | 168404 | -64460.6 | 22 | 21 | 106.57 | 20998.9
8519 | 154856 | -87456.6 | 23 | 22 | 97.5392 | 11308.5
8520 | 148475 | -111127 | 23 | 22 | 93.5461 | 9844.64
8521 | 145940 | -120951 | 23 | 23 | 92.6734 | 9848.79
8522 | 144732 | -133781 | 24 | 23 | 92.5589 | 9852.08
8523 | 143177 | -141182 | 24 | 23 | 92.4583 | 9854.95
8524 | 142267 | -146700 | 25 | 24 | 92.4002 | 9857.51
8525 | 144524 | -149314 | 26 | 25 | 96.1811 | 10942.9
8526 | 191869 | -122920 | 27 | 26 | 137.137 | 26492.4
8527 | 322338 | -787048 | 29 | 28 | 261.893 | 78397.9
8528 | 384405 | -680013 | 30 | 30 | 284.269 | 95203.6
8529 | 403129 | -542067 | 32 | 31 | 275.115 | 131759
8530 | 401053 | -511772 | 32 | 32 | 272.883 | 155029
8531 | 391506 | -496959 | 33 | 32 | 272.079 | 158347
8532 | 378315 | -453163 | 33 | 33 | 241.665 | 158345
8533 | 356178 | -429876 | 34 | 33 | 238.536 | 158344
8534 | 389689 | -377999 | 34 | 34 | 258.018 | 158342
8535 | 407596 | -357681 | 35 | 34 | 265.768 | 156295
8536 | 410594 | -369610 | 34 | 34 | 271.561 | 142087
8537 | 403125 | -380417 | 34 | 33 | 279.422 | 115982
8538 | 388904 | -439988 | 33 | 33 | 259.168 | 86977.6
8539 | 298895 | -475876 | 33 | 32 | 186.594 | 53851.9
8540 | 182357 | -12139.2 | 33 | 32 | 127.134 | 38529.9
8541 | 163147 | -17697.3 | 33 | 32 | 111.98 | 34197.7
8542 | 149623 | -22081.3 | 31 | 30 | 101.001 | 20990.3
8543 | 161385 | -38847.5 | 30 | 28 | 98.3175 | 11299
8544 | 153103 | -62369.4 | 28 | 27 | 94.1869 | 9834.38
8545 | 149473 | -79137.8 | 27 | 26 | 89.131 | 9838.47
8546 | 147060 | -98208.3 | 26 | 25 | 88.8665 | 9841.89
8547 | 145304 | -113573 | 25 | 24 | 88.671 | 9845.58
8548 | 143713 | -130127 | 24 | 22 | 88.4923 | 9848.66
8549 | 142366 | -147758 | 22 | 21 | 88.3426 | 9851.5
8550 | 141169 | -161407 | 21 | 19 | 88.1867 | 9854.19
8551 | 140075 | -175253 | 20 | 19 | 86.4471 | 9856.77
8552 | 125758 | -1010420 | 20 | 18 | 138.902 | 9859.27
8553 | 126429 | -907071 | 19 | 17 | 129.574 | 9861.5
8554 | 124362 | -747489 | 19 | 18 | 116.785 | 9852.43
8555 | 123751 | -710095 | 20 | 18 | 113.646 | 9848.6
8556 | 123141 | -678237 | 20 | 18 | 111.437 | 9847.2
8557 | 122608 | -654955 | 20 | 18 | 109.869 | 9846.35
8558 | 122092 | -612338 | 20 | 18 | 106.85 | 9846.01
8559 | 122562 | -19394.8 | 20 | 17 | 76.7073 | 9845.78
8560 | 145745 | -48629.9 | 18 | 16 | 83.0602 | 9845.92
8561 | 140501 | -74819.3 | 15 | 14 | 87.722 | 9850.55
8562 | 136565 | -116799 | 13 | 11 | 91.675 | 9855.13
8563 | 133992 | -156100 | 12 | 11 | 92.1952 | 9858.93
8564 | 132648 | -184987 | 12 | 10 | 92.0417 | 9862.64
8565 | 131838 | -208284 | 11 | 10 | 93.1827 | 9866.14
8566 | 130760 | -221247 | 10 | 9 | 94.0321 | 9869.25
8567 | 129838 | -238026 | 8 | 7 | 94.2439 | 9872.13
8568 | 128995 | -251342 | 7 | 6 | 94.2594 | 9874.87
8569 | 127927 | -281243 | 5 | 4 | 91.2915 | 3763.52
8570 | 127069 | -295210 | 4 | 3 | 92.3674 | 3766.16
8571 | 126357 | -320372 | 2 | 1 | 94.0789 | 3768.97
8572 | 125700 | -334037 | 2 | 1 | 95.1133 | 3771.62
8573 | 126083 | -352467 | 1 | 0 | 96.0412 | 3774.27
8574 | 124536 | -359079 | 1 | 0 | 96.5168 | 3776.86
8575 | 125221 | -373148 | 1 | 0 | 96.0141 | 3779.43
8576 | 123621 | -372692 | 0 | -1 | 93.4086 | 3781.3
8577 | 123319 | -360226 | 0 | -1 | 91.2412 | 3782.96
8578 | 123284 | -336132 | 1 | 0 | 89.5735 | 3784.48
8579 | 123045 | -294831 | 3 | 1 | 87.2803 | 3785.89
8580 | 125878 | -326660 | 4 | 2 | 88.692 | 3787.21
8581 | 122558 | -332543 | 4 | 2 | 89.8482 | 3788.44
8582 | 123427 | -341385 | 4 | 2 | 90.2699 | 3789.62
8583 | 121910 | -352153 | 4 | 2 | 91.2642 | 3790.87
8584 | 121804 | -356519 | 1 | 0 | 91.1975 | 3792.06
8585 | 121071 | -376123 | -2 | -3 | 96.6891 | 3793.25
8586 | 120532 | -411508 | -5 | -6 | 103.192 | 3794.44
8587 | 119952 | -430763 | -8 | -8 | 105.466 | 3795.6
8588 | 119401 | -452622 | -10 | -11 | 106.953 | 3796.78
8589 | 118866 | -470489 | -13 | -13 | 108.326 | 3797.94
8590 | 118415 | -483861 | -13 | -13 | 109.237 | 3799.08
8591 | 118070 | -491212 | -12 | -13 | 108.955 | 3800.17
8592 | 117724 | -497756 | -12 | -13 | 108.64 | 3801.21
8593 | 117593 | -516819 | -13 | -13 | 107.507 | 3802.21
8594 | 116905 | -521881 | -13 | -14 | 108.008 | 3803.19
8595 | 116928 | -530063 | -14 | -15 | 108.562 | 3804.12
8596 | 116499 | -536328 | -15 | -15 | 109.078 | 3805.04
8597 | 115907 | -539290 | -16 | -16 | 109.315 | 3805.92
8598 | 115986 | -549687 | -17 | -17 | 110.049 | 3806.79
8599 | 115323 | -548090 | -16 | -16 | 108.396 | 3807.64
8600 | 118862 | -548918 | -15 | -15 | 106.015 | 3808.45
8601 | 115093 | -523487 | -14 | -15 | 103.945 | 3809.23
8602 | 123166 | -500258 | -12 | -13 | 102.197 | 3809.98
8603 | 115244 | -448200 | -10 | -11 | 98.7385 | 3810.67
8604 | 120208 | -439481 | -8 | -9 | 97.5684 | 3811.27
8605 | 115581 | -413131 | -6 | -6 | 96.0049 | 3811.77
8606 | 119110 | -402515 | -3 | -4 | 94.936 | 3812.24
8607 | 115840 | -387026 | -1 | -2 | 94.1508 | 3812.7
8608 | 118589 | -394753 | 0 | -1 | 95.1227 | 3813.16
8609 | 115806 | -391753 | 1 | 0 | 98.2101 | 3813.62
8610 | 115752 | -420554 | 2 | 0 | 103.703 | 3814.08
8611 | 115769 | -410014 | 3 | 1 | 104.131 | 3814.55
8612 | 118540 | -436036 | 3 | 2 | 105.367 | 3815.14
8613 | 115756 | -426260 | 4 | 3 | 104.914 | 3815.74
8614 | 118482 | -434799 | 5 | 4 | 105.211 | 3816.28
8615 | 115906 | -421019 | 7 | 5 | 103.627 | 3816.82
8616 | 118682 | -424207 | 8 | 7 | 102.8 | 3817.3
8617 | 116451 | -414203 | 9 | 7 | 104.659 | 9931.79
8618 | 118823 | -417104 | 9 | 8 | 104.73 | 9932.23
8619 | 116749 | -405273 | 10 | 8 | 104.053 | 9932.14
8620 | 118963 | -405762 | 11 | 10 | 103.916 | 9932.35
8621 | 120082 | -396279 | 12 | 11 | 107.66 | 11015.7
8622 | 167158 | -348017 | 13 | 12 | 142.465 | 26563.4
8623 | 304946 | -1331510 | 14 | 13 | 313.049 | 78467.3
8624 | 367755 | -1150070 | 15 | 14 | 330.252 | 95272.5
8625 | 387481 | -969894 | 16 | 15 | 304.342 | 131810
8626 | 385986 | -920754 | 17 | 16 | 293.317 | 155080
8627 | 368262 | -888923 | 19 | 18 | 282.401 | 158397
8628 | 347556 | -812476 | 20 | 19 | 263.992 | 158395
8629 | 342869 | -779545 | 21 | 20 | 260.242 | 158392
8630 | 376431 | -712381 | 22 | 21 | 271.974 | 158389
8631 | 395383 | -679368 | 23 | 21 | 274.795 | 156341
8632 | 398840 | -670778 | 23 | 22 | 281.311 | 142133
8633 | 389883 | -681649 | 23 | 22 | 290.925 | 116028
8634 | 374674 | -728941 | 23 | 21 | 275.304 | 87024.1
8635 | 292562 | -749883 | 23 | 22 | 205.983 | 53898.1
8636 | 172303 | -19266.5 | 23 | 22 | 126.794 | 38575.2
8637 | 174330 | -58736.8 | 23 | 22 | 117.53 | 34242.2
8638 | 156548 | -95866.8 | 23 | 22 | 105.517 | 21036.7
8639 | 143231 | -132578 | 23 | 22 | 96.537 | 11347.2
8640 | 137748 | -151509 | 23 | 22 | 92.6321 | 9883.11
8641 | 135917 | -169014 | 23 | 23 | 91.8476 | 9886.99
8642 | 134867 | -176867 | 24 | 23 | 91.7688 | 9889.75
8643 | 134047 | -183146 | 24 | 23 | 91.7229 | 9892.13
8644 | 133460 | -186831 | 25 | 25 | 91.8875 | 9894.17
8645 | 136197 | -187249 | 27 | 26 | 95.57 | 10979
8646 | 186949 | -153185 | 28 | 28 | 136.749 | 26528.1
8647 | 317016 | -905623 | 28 | 28 | 275.587 | 78433.2
8648 | 379074 | -784579 | 28 | 27 | 291.939 | 95238.3
8649 | 398011 | -663392 | 28 | 27 | 297.057 | 131788
8650 | 396269 | -627853 | 28 | 27 | 290.9 | 155057
8651 | 385160 | -612154 | 29 | 27 | 283.347 | 158374
8652 | 369851 | -557361 | 29 | 27 | 265.639 | 158372
8653 | 351961 | -547272 | 29 | 27 | 258.063 | 158370
8654 | 385111 | -516371 | 28 | 27 | 278.294 | 158367
8655 | 403596 | -502374 | 28 | 27 | 265.254 | 156321
8656 | 406691 | -508477 | 28 | 27 | 270.41 | 142113
8657 | 397388 | -527427 | 28 | 27 | 299.428 | 116009
8658 | 386773 | -575827 | 28 | 27 | 284.805 | 87004.7
8659 | 300082 | -602844 | 28 | 27 | 214.242 | 53879.1
8660 | 178912 | -16301.8 | 28 | 27 | 127.54 | 38556.8
8661 | 159926 | -25697.4 | 28 | 27 | 112.203 | 34224.4
8662 | 167840 | -49777.3 | 27 | 27 | 106.605 | 21017.6
8663 | 152546 | -76780.2 | 27 | 26 | 97.4303 | 11327
8664 | 146071 | -96694.6 | 26 | 25 | 93.4436 | 9862.95
8665 | 143522 | -114697 | 25 | 24 | 92.4555 | 9866.87
8666 | 142038 | -132705 | 24 | 23 | 92.2997 | 9869.94
8667 | 140770 | -147068 | 23 | 22 | 92.1645 | 9872.61
8668 | 139748 | -157960 | 23 | 22 | 92.0471 | 9874.91
8669 | 141973 | -166883 | 23 | 22 | 95.9079 | 10960.1
8670 | 189064 | -144756 | 23 | 22 | 136.791 | 26509.6
8671 | 320681 | -900196 | 24 | 23 | 269.266 | 78415.1
8672 | 382566 | -796011 | 24 | 24 | 291.834 | 95220.6
8673 | 401489 | -671680 | 25 | 24 | 297.995 | 131774
8674 | 399307 | -647804 | 25 | 24 | 292.291 | 155044
8675 | 389364 | -665672 | 24 | 24 | 286.984 | 158362
8676 | 371393 | -609791 | 24 | 23 | 268.821 | 158360
8677 | 354222 | -603148 | 24 | 23 | 247.591 | 158359
8678 | 387295 | -560041 | 24 | 23 | 261.539 | 158356
8679 | 405820 | -555696 | 24 | 23 | 267.84 | 156310
8680 | 408674 | -561936 | 24 | 23 | 273.902 | 142102
8681 | 399156 | -597126 | 23 | 22 | 284.67 | 115999
8682 | 388274 | -651869 | 23 | 22 | 270.983 | 86995.5
8683 | 305702 | -686593 | 22 | 21 | 201.764 | 53870.5
8684 | 180040 | -19199.4 | 21 | 19 | 127.323 | 38548.4
8685 | 185799 | -42990 | 20 | 18 | 118.328 | 34215.9
8686 | 166882 | -88398.3 | 16 | 14 | 106.171 | 21009.2
8687 | 152533 | -131534 | 12 | 11 | 97.0245 | 11319.7
8688 | 146047 | -170897 | 8 | 7 | 92.9395 | 9855.92
8689 | 143574 | -203531 | 7 | 6 | 91.9979 | 9860.38
8690 | 141837 | -226579 | 6 | 6 | 93.6404 | 9863.93
8691 | 140357 | -240306 | 5 | 5 | 94.4652 | 9867.23
8692 | 139497 | -259875 | 3 | 3 | 95.4533 | 9870.28
8693 | 140430 | -275922 | 2 | 1 | 100.199 | 10956.2
8694 | 186405 | -261938 | 0 | -1 | 137.477 | 26506.3
8695 | 318614 | -1284870 | 0 | -1 | 292.742 | 78412.4
8696 | 380614 | -1192050 | 0 | -1 | 314.581 | 95218.5
8697 | 400005 | -1012240 | 0 | -1 | 312.252 | 131771
8698 | 397805 | -912766 | 3 | 2 | 304.528 | 155042
8699 | 382560 | -923992 | 6 | 5 | 297.145 | 158361
8700 | 356304 | -789317 | 9 | 7 | 265.468 | 158361
8701 | 352364 | -767115 | 10 | 9 | 256.6 | 158359
8702 | 385322 | -703001 | 12 | 10 | 267.709 | 158355
8703 | 404225 | -639323 | 13 | 11 | 271.01 | 156309
8704 | 407317 | -692164 | 13 | 11 | 275.549 | 142102
8705 | 397455 | -733107 | 12 | 11 | 289.423 | 115998
8706 | 386208 | -795938 | 12 | 11 | 277.154 | 86995.3
8707 | 306282 | -776021 | 13 | 12 | 206.3 | 53870.4
8708 | 178711 | -12783.1 | 14 | 13 | 127.219 | 38547.8
8709 | 183245 | -57674.3 | 15 | 14 | 118.347 | 34214.4
8710 | 165288 | -96295.3 | 15 | 14 | 106.169 | 21006.3
8711 | 151349 | -120908 | 16 | 14 | 97.1164 | 11316.6
8712 | 147122 | -141955 | 16 | 15 | 93.4238 | 9852.62
8713 | 142864 | -151064 | 16 | 15 | 88.6372 | 9856.91
8714 | 141277 | -158166 | 16 | 15 | 88.426 | 9860.12
8715 | 140739 | -177747 | 16 | 15 | 88.2126 | 9863.22
8716 | 138861 | -191158 | 16 | 15 | 87.9867 | 9865.29
8717 | 138838 | -207014 | 16 | 15 | 88.6703 | 9867.91
8718 | 136731 | -210626 | 16 | 15 | 89.1309 | 9870.29
8719 | 136398 | -218689 | 16 | 15 | 87.8837 | 9872.76
8720 | 123424 | -1120550 | 16 | 15 | 146.231 | 9875.08
8721 | 122776 | -988291 | 16 | 15 | 155.539 | 9877.06
8722 | 122235 | -869389 | 16 | 15 | 145.134 | 9862.43
8723 | 121700 | -810488 | 17 | 16 | 140.23 | 9859.7
8724 | 121201 | -797663 | 17 | 16 | 121.044 | 9857.67
8725 | 120752 | -781769 | 17 | 16 | 118.749 | 9856.62
8726 | 120283 | -780677 | 17 | 16 | 118.624 | 9856
8727 | 135743 | -19329.2 | 17 | 16 | 81.2164 | 9855.55
8728 | 138518 | -81336.3 | 15 | 14 | 83.7828 | 9855.49
8729 | 134217 | -129039 | 14 | 12 | 87.3619 | 9861.14
8730 | 132133 | -182918 | 12 | 11 | 91.2934 | 9867.32
8731 | 130666 | -212402 | 7 | 5 | 93.3391 | 9871.02
8732 | 129362 | -247722 | 1 | 0 | 95.3212 | 9874.68
8733 | 128095 | -283269 | -4 | -5 | 97.7568 | 9877.74
8734 | 127070 | -315450 | -7 | -8 | 99.9886 | 9880.74
8735 | 126044 | -347827 | -10 | -11 | 101.414 | 9883.78
8736 | 124994 | -378411 | -13 | -14 | 102.792 | 9886.91
8737 | 123884 | -415410 | -13 | -14 | 100.641 | 3776.08
8738 | 123085 | -442612 | -13 | -14 | 102.641 | 3779.19
8739 | 122387 | -464501 | -13 | -14 | 104.03 | 3782.5
8740 | 121764 | -480268 | -13 | -14 | 104.794 | 3784.64
8741 | 121580 | -493336 | -13 | -14 | 105.677 | 3786.43
8742 | 120660 | -502638 | -13 | -14 | 106.412 | 3788.04
8743 | 120674 | -511647 | -13 | -14 | 105.327 | 3789.54
8744 | 119793 | -507830 | -13 | -14 | 102.693 | 3790.95
8745 | 119711 | -453708 | -13 | -14 | 97.8413 | 3792.31
8746 | 119822 | -403455 | -12 | -13 | 94.9907 | 3793.61
8747 | 119829 | -378574 | -10 | -11 | 93.2143 | 3794.82
8748 | 119794 | -370061 | -9 | -10 | 92.6386 | 3795.85
8749 | 119366 | -365132 | -9 | -10 | 92.24 | 3796.89
8750 | 118973 | -354811 | -10 | -11 | 91.5942 | 3797.89
8751 | 118707 | -363822 | -10 | -11 | 91.954 | 3798.96
8752 | 120129 | -398883 | -10 | -11 | 94.2489 | 3800
8753 | 118086 | -448931 | -11 | -12 | 101.533 | 3800.99
8754 | 117818 | -492264 | -11 | -12 | 108.854 | 3802.02
8755 | 117369 | -510097 | -11 | -12 | 110.827 | 3803.04
8756 | 116661 | -516635 | -10 | -11 | 111.267 | 3804.05
8757 | 117599 | -523432 | -10 | -11 | 111.726 | 3805.03
8758 | 116124 | -522792 | -10 | -11 | 111.747 | 3805.95
8759 | 116840 | -531342 | -11 | -11 | 111.488 | 3806.83
8760 | 115591 | -531711 | -11 | -12 | 110.855 | 3807.69
Note on K14: shackel: Peak cooling for the building. This is the same peak value we always publish in our program reports. This value is simply carried through TRNSYS and into the final report.
Note on L14: shackel: Take the maximum value from the hourly building cooling loads in 'eQUEST Output' (alternatively, take from SS-D report)
Note on K15: shackel: Peak cooling for the building. This is the same peak value we always publish in our program reports. This value is simply carried through TRNSYS and into the final report.
Note on L15: shackel: Take the maximum value from the hourly building heating loads in 'eQUEST Output' (alternatively, take from SS-D report)
Note on K16: shackel: The gas rate/cost per therm for the customer (default $0.70/therm)
Note on K17: shackel: The electric rate/cost per kWh for the customer (default $0.10/kWh)
Note on K18: shackel: The peak CHW (cooling) load on the heat recovery chiller, used to size other items in the model.
Note on K19: shackel: The peak HW (heating) load on the heat recovery chiller, used to size other items in the model.
Note on K20: shackel: The size of the hybrid equipment (boiler and/or chiller) as a percentage of maximum load on the system.
Note on K21: shackel: The total length of the ground heat exchanger, in feet. As in eQUEST, there is no autosize feature. A good first guess is 125 ft for every ton of capacity; the loop temperature should then be plotted and GHX size adjusted until temps are reasonable.
Note on K22: shackel: Ground conductivity, as measured by a thermal conductivity test; a reasonable default is 1.5; in WI and parts of northern IL these values are often a bit higher (close to 2 in some cases).
Note on K23: shackel: Initial ground temperature. Can be measured with a conductivity test. Ranges from high 40s in northern WI to 55 in central IL.
Note on K24: shackel: Ground diffusivity, as measured by a thermal conductivity test. 1.1 is a reasonable default.

## eQUEST Output
C:\Users\shackel\Documents\eQUEST 3-64 Projects\Organic Valley\For Central Geo\Organic Valley v7.2 CGEO no econ - 8
Simulated: 2013-Jul-24 16:48:02
CSV Written: 2013-Jul-24 16:48:38
eQUEST 3.64.7130
|  |  |  | Hourly Report | [25 empty] | Hourly Report 2
|  |  |  | EM1 Hourly Report Block | [12 empty] | FM1 Hourly Report Block | [12 empty] | CHW Loads | HW Loads | Weather
|  |  |  | ELEC-METER | [12 empty] | FUEL-METER | [12 empty] | CIRCULATION-LOOP | CIRCULATION-LOOP | Global |  | Building HVAC
|  |  |  | EM1 | [12 empty] | FM1 | [12 empty] | Chilled Water Loop - Geo | Hot Water Loop - Geo
|  |  | Day | Var 1 | Var 2 | Var 3 | Var 4 | Var 5 | Var 6 | Var 7 | Var 8 | Var 9 | Var 10 | Var 11 | Var 12 | Var 20 | Var 1 | Var 2 | Var 3 | Var 4 | Var 5 | Var 6 | Var 7 | Var 8 | Var 9 | Var 10 | Var 11 | Var 12 | Var 20 | Var 7 | Var 6 | Var 3 | Var 4 | Var 7 | Var 6
Month | Day | Hour | Type | Lighting end-use energy | Task lighting end-use energy | Miscellaneous equipment end-use energy | Heating end-use energy | Cooling end-use energy | Heat rejection end-use energy | Auxiliary end-use energy (pumps) | Vent fan end-use energy | Refrigeration systems end-use energy | Supplemental heat pump end-use energy | Domestic hot water end-use energy | Exterior to the building end-use energy | Total end-use energy | Lighting end-use energy | Task lighting end-use energy | Miscellaneous equipment end-use energy | Heating end-use energy | Cooling end-use energy | Heat rejection end-use energy | Auxiliary end-use energy (pumps) | Vent fan end-use energy | Refrigeration systems end-use energy | Supplemental heat pump end-use energy | Domestic hot water end-use energy | Exterior to the building end-use energy | Total end-use energy | Cooling coil load on loop | Heating coil load on loop | Outside wet-bulb temp (F) | Outside dry-bulb temp (F) | Building cool load (coils+losses&gains) (Btu/hr) | Building heat load (coils+losses&gains) (Btu/hr)
1 | 1 | 1 | 7 | 5.1054 | 0 | 42.7453 | 32.9581 | 0 | 0 | 25.2905 | 17.3638 | 0 | 0 | 0 | 4.8 | 128.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4051.92 | 0 | 4051.92 | 120563 | -215622 | 25 | 27 | 120563 | -1215622
1 | 1 | 2 | 7 | 5.1054 | 0 | 42.7453 | 12.9393 | 0 | 0 | 9.4984 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4051.91 | 0 | 4051.91 | 120336 | -221116 | 24 | 26 | 120336 | -1221116
1 | 1 | 3 | 7 | 5.1054 | 0 | 42.7453 | 13.7811 | 0 | 0 | 10.2631 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4051.93 | 0 | 4051.93 | 120171 | -228892 | 22 | 24 | 120171 | -1228892
1 | 1 | 4 | 7 | 5.1054 | 0 | 42.7453 | 14.0513 | 0 | 0 | 10.5359 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.6017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4051.99 | 0 | 4051.99 | 119955 | -232156 | 22 | 23 | 119955 | -1232156
1 | 1 | 5 | 7 | 5.1054 | 0 | 42.7453 | 14.2586 | 0 | 0 | 10.7536 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.08 | 0 | 4052.08 | 119798 | -235136 | 21 | 22 | 119798 | -1235136
1 | 1 | 6 | 7 | 5.1054 | 0 | 42.7453 | 14.4418 | 0 | 0 | 10.9386 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.16 | 0 | 4052.16 | 119759 | -238247 | 20 | 21 | 119759 | -1238247
1 | 1 | 7 | 7 | 5.1054 | 0 | 42.7453 | 14.6017 | 0 | 0 | 11.1501 | 17.3638 | 0 | 0 | 0 | 3.2 | 94.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.23 | 0 | 4052.23 | 119679 | -240070 | 20 | 21 | 119679 | -1240070
1 | 1 | 8 | 7 | 5.046 | 0 | 42.7453 | 14.2078 | 0 | 0 | 10.8322 | 17.3638 | 0 | 0 | 0 | 0.8 | 90.9951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.29 | 0 | 4052.29 | 119627 | -240466 | 20 | 21 | 119627 | -1240466
1 | 1 | 9 | 7 | 4.2171 | 0 | 42.7453 | 14.1375 | 0 | 0 | 11.0363 | 17.3638 | 0 | 0 | 0 | 0 | 89.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.35 | 0 | 4052.35 | 119646 | -243073 | 20 | 21 | 119646 | -1243073
1 | 1 | 10 | 7 | 4.1777 | 0 | 42.7453 | 12.3847 | 0 | 0 | 9.3979 | 17.3638 | 0 | 0 | 0 | 0 | 86.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.4 | 0 | 4052.4 | 119859 | -210747 | 22 | 23 | 119859 | -1210747
1 | 1 | 11 | 7 | 4.1502 | 0 | 42.7453 | 11.0842 | 0 | 0 | 8.3681 | 17.3638 | 0 | 0 | 0 | 0 | 83.7116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.54 | 0 | 4052.54 | 121852 | -191191 | 24 | 26 | 121852 | -1191191
1 | 1 | 12 | 7 | 4.1502 | 0 | 42.7453 | 10.7054 | 0 | 0 | 8.1424 | 17.3638 | 0 | 0 | 0 | 0 | 83.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.61 | 0 | 4052.61 | 120263 | -180512 | 26 | 28 | 120263 | -1180512
1 | 1 | 13 | 7 | 4.1494 | 0 | 42.7453 | 10.1223 | 0 | 0 | 7.7697 | 17.3638 | 0 | 0 | 0 | 0 | 82.1504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.63 | 0 | 4052.63 | 122189 | -170105 | 27 | 29 | 122189 | -1170105
1 | 1 | 14 | 7 | 4.1498 | 0 | 42.7453 | 0 | 9.7438 | 0 | 5.8815 | 17.3638 | 0 | 0 | 0 | 0 | 79.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.62 | 0 | 4052.62 | 120431 | -157738 | 28 | 31 | 120431 | -1157738
1 | 1 | 15 | 7 | 4.6547 | 0 | 42.7453 | 10.823 | 0 | 0 | 8.1654 | 17.3638 | 0 | 0 | 0 | 0 | 83.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.62 | 0 | 4052.62 | 122184 | -184884 | 28 | 32 | 122184 | -1184884
1 | 1 | 16 | 7 | 4.7981 | 0 | 42.7453 | 11.2066 | 0 | 0 | 8.4779 | 17.3638 | 0 | 0 | 0 | 0 | 84.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.6 | 0 | 4052.6 | 120581 | -188223 | 28 | 30 | 120581 | -1188223
1 | 1 | 17 | 7 | 6.4251 | 0 | 42.7453 | 12.303 | 0 | 0 | 9.2939 | 17.3638 | 0 | 0 | 0 | 2.4 | 90.5311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.62 | 0 | 4052.62 | 120544 | -210854 | 26 | 29 | 120544 | -1210854
1 | 1 | 18 | 7 | 6.6633 | 0 | 42.7453 | 13.3603 | 0 | 0 | 10.3557 | 17.3638 | 0 | 0 | 0 | 6.4 | 96.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.71 | 0 | 4052.71 | 120419 | -226934 | 25 | 27 | 120419 | -1226934
1 | 1 | 19 | 7 | 6.6633 | 0 | 42.7453 | 14.0003 | 0 | 0 | 10.9677 | 17.3638 | 0 | 0 | 0 | 7.2 | 98.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.8 | 0 | 4052.8 | 120322 | -238841 | 23 | 25 | 120322 | -1238841
1 | 1 | 20 | 7 | 6.6633 | 0 | 42.7453 | 14.8251 | 0 | 0 | 12.044 | 17.3638 | 0 | 0 | 0 | 7.2 | 100.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.93 | 0 | 4052.93 | 120212 | -252066 | 21 | 22 | 120212 | -1252066
1 | 1 | 21 | 7 | 6.6633 | 0 | 42.7453 | 15.2903 | 0 | 0 | 12.5359 | 17.3638 | 0 | 0 | 0 | 7.2 | 101.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.07 | 0 | 4053.07 | 120012 | -260374 | 19 | 20 | 120012 | -1260374
1 | 1 | 22 | 7 | 6.6633 | 0 | 42.7453 | 16.2128 | 0 | 0 | 13.8598 | 17.3638 | 0 | 0 | 0 | 7.2 | 104.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.21 | 0 | 4053.21 | 126050 | -270277 | 17 | 18 | 126050 | -1270277
1 | 1 | 23 | 7 | 6.6633 | 0 | 42.7453 | 15.3588 | 0 | 0 | 12.5794 | 17.3638 | 0 | 0 | 0 | 6.4 | 101.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.35 | 0 | 4053.35 | 119631 | -258881 | 15 | 16 | 119631 | -1258881
1 | 1 | 24 | 7 | 6.6633 | 0 | 42.7453 | 16.9476 | 0 | 0 | 15.2693 | 17.3638 | 0 | 0 | 0 | 5.6 | 104.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.48 | 0 | 4053.48 | 120547 | -295802 | 13 | 14 | 120547 | -1295802
1 | 2 | 1 | 8 | 5.1054 | 0 | 42.7453 | 17.8796 | 0 | 0 | 16.5833 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.54 | 0 | 4053.54 | 119153 | -312642 | 12 | 13 | 119153 | -1312642
1 | 2 | 2 | 8 | 5.1054 | 0 | 42.7453 | 18.962 | 0 | 0 | 18.4254 | 17.3638 | 0 | 0 | 0 | 4.8 | 107.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.7 | 0 | 4053.7 | 122366 | -335767 | 11 | 12 | 122366 | -1335767
1 | 2 | 3 | 8 | 5.1054 | 0 | 42.7453 | 19.1019 | 0 | 0 | 18.6424 | 17.3638 | 0 | 0 | 0 | 4.8 | 107.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.88 | 0 | 4053.88 | 118754 | -332674 | 10 | 11 | 118754 | -1332674
1 | 2 | 4 | 8 | 5.1054 | 0 | 42.7453 | 20.2022 | 0 | 0 | 20.7048 | 17.3638 | 0 | 0 | 0 | 4.8 | 110.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.06 | 0 | 4054.06 | 128301 | -347856 | 10 | 10 | 128301 | -1347856
1 | 2 | 5 | 8 | 5.1054 | 0 | 42.7453 | 18.6091 | 0 | 0 | 17.5816 | 17.3638 | 0 | 0 | 0 | 4.8 | 106.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.21 | 0 | 4054.21 | 118368 | -319416 | 9 | 10 | 118368 | -1319416
1 | 2 | 6 | 8 | 5.1054 | 0 | 42.7453 | 20.2231 | 0 | 0 | 21.2966 | 17.3638 | 0 | 0 | 0 | 4.8 | 111.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.32 | 0 | 4054.32 | 120973 | -364077 | 8 | 9 | 120973 | -1364077
1 | 2 | 7 | 8 | 5.1054 | 0 | 42.7453 | 20.5801 | 0 | 0 | 22.4373 | 17.3638 | 0 | 0 | 0 | 3.2 | 111.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.35 | 0 | 4054.35 | 118006 | -364332 | 9 | 9 | 118006 | -1364332
1 | 2 | 8 | 8 | 5.0263 | 0 | 42.7453 | 21.033 | 0 | 0 | 23.6416 | 17.3638 | 0 | 0 | 0 | 0.8 | 110.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.49 | 0 | 4054.49 | 120309 | -376493 | 9 | 10 | 120309 | -1376493
1 | 2 | 9 | 8 | 4.0935 | 0 | 42.7453 | 18.4227 | 0 | 0 | 18.0993 | 17.3638 | 0 | 0 | 0 | 0 | 100.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.65 | 0 | 4054.65 | 118001 | -320222 | 9 | 10 | 118001 | -1320222
1 | 2 | 10 | 8 | 4.2024 | 0 | 42.7453 | 15.9298 | 0 | 0 | 13.8832 | 17.3638 | 0 | 0 | 0 | 0 | 94.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.8 | 0 | 4054.8 | 119147 | -282985 | 12 | 13 | 119147 | -1282985
1 | 2 | 11 | 8 | 4.1563 | 0 | 42.7453 | 16.1747 | 0 | 0 | 14.2405 | 17.3638 | 0 | 0 | 0 | 0 | 94.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.87 | 0 | 4054.87 | 118501 | -289271 | 14 | 15 | 118501 | -1289271
1 | 2 | 12 | 8 | 4.1506 | 0 | 42.7453 | 14.5925 | 0 | 0 | 12.0932 | 17.3638 | 0 | 0 | 0 | 0 | 90.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.8 | 0 | 4054.8 | 118477 | -257567 | 16 | 18 | 118477 | -1257567
1 | 2 | 13 | 8 | 4.1506 | 0 | 42.7453 | 13.091 | 0 | 0 | 10.3213 | 17.3638 | 0 | 0 | 0 | 0 | 87.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.76 | 0 | 4054.76 | 120275 | -228347 | 18 | 20 | 120275 | -1228347
1 | 2 | 14 | 8 | 4.1529 | 0 | 42.7453 | 11.7688 | 0 | 0 | 9.0804 | 17.3638 | 0 | 0 | 0 | 0 | 85.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.78 | 0 | 4054.78 | 119035 | -207924 | 20 | 22 | 119035 | -1207924
1 | 2 | 15 | 8 | 4.163 | 0 | 42.7453 | 11.3592 | 0 | 0 | 8.6987 | 17.3638 | 0 | 0 | 0 | 0 | 84.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.73 | 0 | 4054.73 | 120555 | -198128 | 21 | 24 | 120555 | -1198128
1 | 2 | 16 | 8 | 4.329 | 0 | 42.7453 | 11.6567 | 0 | 0 | 8.9759 | 17.3638 | 0 | 0 | 0 | 0 | 85.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.58 | 0 | 4054.58 | 119325 | -201619 | 20 | 22 | 119325 | -1201619
1 | 2 | 17 | 8 | 6.2207 | 0 | 42.7453 | 12.9393 | 0 | 0 | 10.064 | 17.3638 | 0 | 0 | 0 | 2.4 | 91.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.49 | 0 | 4054.49 | 119019 | -226698 | 18 | 20 | 119019 | -1226698
1 | 2 | 18 | 8 | 6.6633 | 0 | 42.7453 | 15.7985 | 0 | 0 | 13.6506 | 17.3638 | 0 | 0 | 0 | 6.4 | 102.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.45 | 0 | 4054.45 | 118990 | -274462 | 16 | 18 | 118990 | -1274462
1 | 2 | 19 | 8 | 6.6633 | 0 | 42.7453 | 17.0766 | 0 | 0 | 15.5455 | 17.3638 | 0 | 0 | 0 | 7.2 | 106.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.64 | 0 | 4054.64 | 118639 | -298603 | 14 | 16 | 118639 | -1298603
1 | 2 | 20 | 8 | 6.6633 | 0 | 42.7453 | 18.1028 | 0 | 0 | 17.6137 | 17.3638 | 0 | 0 | 0 | 7.2 | 109.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.79 | 0 | 4054.79 | 118440 | -315770 | 12 | 13 | 118440 | -1315770
1 | 2 | 21 | 8 | 6.6633 | 0 | 42.7453 | 18.841 | 0 | 0 | 18.7981 | 17.3638 | 0 | 0 | 0 | 7.2 | 111.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4054.97 | 0 | 4054.97 | 120631 | -327235 | 10 | 11 | 120631 | -1327235
1 | 2 | 22 | 8 | 6.6633 | 0 | 42.7453 | 19.2732 | 0 | 0 | 19.7261 | 17.3638 | 0 | 0 | 0 | 7.2 | 112.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4055.12 | 0 | 4055.12 | 118026 | -327227 | 8 | 9 | 118026 | -1327227
1 | 2 | 23 | 8 | 6.6633 | 0 | 42.7453 | 19.0336 | 0 | 0 | 18.7867 | 17.3638 | 0 | 0 | 0 | 6.4 | 110.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4055.25 | 0 | 4055.25 | 117813 | -321977 | 7 | 7 | 117813 | -1321977
1 | 2 | 24 | 8 | 6.6633 | 0 | 42.7453 | 19.7268 | 0 | 0 | 20.4422 | 17.3638 | 0 | 0 | 0 | 5.6 | 112.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4055.35 | 0 | 4055.35 | 119618 | -333519 | 5 | 5 | 119618 | -1333519
1 | 3 | 1 | 2 | 10.424 | 0 | 42.3304 | 20.0233 | 0 | 0 | 21.095 | 17.3638 | 0 | 0 | 0 | 4.8 | 116.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10681.4 | 0 | 10681.4 | 117670 | -335824 | 2 | 3 | 117670 | -1335824
1 | 3 | 2 | 2 | 10.424 | 0 | 42.3304 | 20.6567 | 0 | 0 | 22.2695 | 17.3638 | 0 | 0 | 0 | 4.8 | 117.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10681.5 | 0 | 10681.5 | 118831 | -347277 | 0 | 0 | 118831 | -1347277
1 | 3 | 3 | 2 | 10.424 | 0 | 42.3304 | 20.9825 | 0 | 0 | 23.0381 | 17.3638 | 0 | 0 | 0 | 4.8 | 118.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10681 | 0 | 10681 | 117292 | -350917 | -2 | -2 | 117292 | -1350917
1 | 3 | 4 | 2 | 10.424 | 0 | 42.3304 | 21.0304 | 0 | 0 | 23.1534 | 17.3638 | 0 | 0 | 0 | 4.8 | 119.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10680.9 | 0 | 10680.9 | 118182 | -351101 | 0 | 1 | 118182 | -1351101
1 | 3 | 5 | 2 | 11.8202 | 0 | 44.8242 | 20.7776 | 0 | 0 | 22.7767 | 17.5105 | 0 | 0 | 0 | 4.8 | 122.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11854.6 | 0 | 11854.6 | 119986 | -351945 | 3 | 3 | 119986 | -1351945
1 | 3 | 6 | 2 | 24.3093 | 0 | 69.9783 | 19.846 | 0 | 0 | 20.6282 | 17.5105 | 0 | 0 | 0 | 4.8 | 157.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28703.9 | 0 | 28703.9 | 166789 | -338896 | 6 | 6 | 166789 | -1338896
1 | 3 | 7 | 2 | 49.0171 | 0 | 140.608 | 81.9749 | 0 | 0 | 25.2343 | 20.3145 | 0 | 0 | 0 | 3.2 | 320.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84954.2 | 0 | 84954.2 | 305303 | -1433240 | 5 | 6 | 305303 | -2433240
1 | 3 | 8 | 2 | 52.8769 | 0 | 168.222 | 72.3431 | 0 | 0 | 25.2181 | 19.6009 | 0 | 0 | 0 | 0.8 | 339.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103167 | 0 | 103167 | 367828 | -1300390 | 5 | 5 | 367828 | -2300390
1 | 3 | 9 | 2 | 42.5391 | 0 | 173.795 | 60.9983 | 0 | 0 | 25.2083 | 19.2422 | 0 | 0 | 0 | 0 | 321.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142762 | 0 | 142762 | 387677 | -1139240 | 4 | 5 | 387677 | -2139240
1 | 3 | 10 | 2 | 41.0652 | 0 | 172.186 | 58.0328 | 0 | 0 | 25.2073 | 19.1096 | 0 | 0 | 0 | 0 | 315.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167981 | 0 | 167981 | 386128 | -1074430 | 5 | 7 | 386128 | -2074430
1 | 3 | 11 | 2 | 41.2529 | 0 | 163.102 | 60.0216 | 0 | 0 | 25.2079 | 19.0363 | 0 | 0 | 0 | 0 | 308.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171576 | 0 | 171576 | 367853 | -1074460 | 7 | 8 | 367853 | -2074460
1 | 3 | 12 | 2 | 40.898 | 0 | 149.692 | 56.6345 | 0 | 0 | 25.2142 | 19.0363 | 0 | 0 | 0 | 0 | 291.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171573 | 0 | 171573 | 345883 | -974292 | 8 | 10 | 345883 | -1974292
1 | 3 | 13 | 2 | 39.8313 | 0 | 150.207 | 54.3428 | 0 | 0 | 25.2141 | 19.0363 | 0 | 0 | 0 | 0 | 288.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171571 | 0 | 171571 | 342213 | -950717 | 8 | 10 | 342213 | -1950717
1 | 3 | 14 | 2 | 42.1058 | 0 | 165.698 | 48.8506 | 0 | 0 | 25.2116 | 19.0363 | 0 | 0 | 0 | 0 | 300.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171568 | 0 | 171568 | 375524 | -912674 | 8 | 10 | 375524 | -1912674
1 | 3 | 15 | 2 | 41.4336 | 0 | 172.702 | 46.7276 | 0 | 0 | 25.2143 | 19.0363 | 0 | 0 | 0 | 0 | 305.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169350 | 0 | 169350 | 394683 | -891492 | 7 | 10 | 394683 | -1891492
1 | 3 | 16 | 2 | 51.1588 | 0 | 173.986 | 47.8544 | 0 | 0 | 25.2147 | 19.0363 | 0 | 0 | 0 | 0 | 317.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153953 | 0 | 153953 | 398254 | -910585 | 7 | 9 | 398254 | -1910585
1 | 3 | 17 | 2 | 56.2294 | 0 | 169.782 | 51.0034 | 0 | 0 | 25.2137 | 19.0363 | 0 | 0 | 0 | 2.4 | 323.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125661 | 0 | 125661 | 388815 | -943384 | 7 | 9 | 388815 | -1943384
1 | 3 | 18 | 2 | 49.7836 | 0 | 152.497 | 57.5359 | 0 | 0 | 25.2131 | 19.0363 | 0 | 0 | 0 | 6.4 | 310.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94226.9 | 0 | 94226.9 | 367033 | -1019410 | 6 | 8 | 367033 | -2019410
1 | 3 | 19 | 2 | 34.11 | 0 | 93.4203 | 64.6608 | 0 | 0 | 25.2148 | 19.0913 | 0 | 0 | 0 | 7.2 | 243.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58326.7 | 0 | 58326.7 | 297345 | -1049960 | 4 | 6 | 297345 | -2049960
1 | 3 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.9303 | 0 | 5.9785 | 17.5105 | 0 | 0 | 0 | 7.2 | 132.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41720.9 | 0 | 41720.9 | 201758 | -19590.2 | 2 | 4 | 201758 | -1019590.2
1 | 3 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.3105 | 0 | 5.9201 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37024.6 | 0 | 37024.6 | 168765 | -149477 | 0 | 2 | 168765 | -1149477
1 | 3 | 22 | 2 | 13.825 | 0 | 48.8953 | 11.6368 | 0 | 0 | 9.1876 | 17.5105 | 0 | 0 | 0 | 7.2 | 108.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22716.8 | 0 | 22716.8 | 151793 | -223935 | 0 | 1 | 151793 | -1223935
1 | 3 | 23 | 2 | 11.1963 | 0 | 44.3342 | 16.0588 | 0 | 0 | 14.2926 | 17.5105 | 0 | 0 | 0 | 6.4 | 109.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12216.8 | 0 | 12216.8 | 140389 | -277702 | -1 | 1 | 140389 | -1277702
1 | 3 | 24 | 2 | 10.3176 | 0 | 42.5403 | 17.2804 | 0 | 0 | 16.2157 | 17.5105 | 0 | 0 | 0 | 5.6 | 109.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10630.8 | 0 | 10630.8 | 133460 | -299116 | -1 | 0 | 133460 | -1299116
1 | 4 | 1 | 3 | 10.8489 | 0 | 42.3304 | 18.8556 | 0 | 0 | 19.1085 | 17.3638 | 0 | 0 | 0 | 4.8 | 113.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10635.1 | 0 | 10635.1 | 131531 | -322900 | -3 | -2 | 131531 | -1322900
1 | 4 | 2 | 3 | 10.8489 | 0 | 42.3304 | 19.9994 | 0 | 0 | 21.4638 | 17.3638 | 0 | 0 | 0 | 4.8 | 116.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10638.6 | 0 | 10638.6 | 130251 | -338855 | -4 | -3 | 130251 | -1338855
1 | 4 | 3 | 3 | 10.8489 | 0 | 42.3304 | 21.5207 | 0 | 0 | 25.0656 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10641.6 | 0 | 10641.6 | 129156 | -362905 | -6 | -5 | 129156 | -1362905
1 | 4 | 4 | 3 | 10.8489 | 0 | 42.3304 | 22.543 | 0 | 0 | 25.3009 | 17.3638 | 0 | 0 | 0 | 4.8 | 123.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10644.3 | 0 | 10644.3 | 128145 | -376803 | -7 | -6 | 128145 | -1376803
1 | 4 | 5 | 3 | 11.8202 | 0 | 44.8242 | 24.5085 | 0 | 0 | 25.2981 | 17.5105 | 0 | 0 | 0 | 4.8 | 128.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11820.6 | 0 | 11820.6 | 129850 | -402389 | -8 | -7 | 129850 | -1402389
1 | 4 | 6 | 3 | 24.3093 | 0 | 69.9783 | 23.7003 | 0 | 0 | 25.3036 | 17.5105 | 0 | 0 | 0 | 4.8 | 165.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28672.4 | 0 | 28672.4 | 175604 | -381720 | -9 | -8 | 175604 | -1381720
1 | 4 | 7 | 3 | 49.0171 | 0 | 140.608 | 88.1382 | 0 | 0 | 25.2648 | 20.1791 | 0 | 0 | 0 | 3.2 | 326.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84925 | 0 | 84925 | 312087 | -1574940 | -8 | -7 | 312087 | -2574940
1 | 4 | 8 | 3 | 52.6156 | 0 | 168.222 | 78.9256 | 0 | 0 | 25.2343 | 19.6459 | 0 | 0 | 0 | 0.8 | 345.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103138 | 0 | 103138 | 374471 | -1447620 | -7 | -6 | 374471 | -2447620
1 | 4 | 9 | 3 | 41.6369 | 0 | 173.795 | 67.154 | 0 | 0 | 25.213 | 19.2233 | 0 | 0 | 0 | 0 | 327.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142741 | 0 | 142741 | 394248 | -1249830 | -6 | -5 | 394248 | -2249830
1 | 4 | 10 | 3 | 40.9083 | 0 | 172.186 | 63.0476 | 0 | 0 | 25.2081 | 19.0673 | 0 | 0 | 0 | 0 | 320.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167962 | 0 | 167962 | 392053 | -1168730 | -4 | -3 | 392053 | -2168730
1 | 4 | 11 | 3 | 41.2395 | 0 | 163.102 | 62.3652 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 0 | 310.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171557 | 0 | 171557 | 373238 | -1140590 | -2 | -1 | 373238 | -2140590
1 | 4 | 12 | 3 | 40.7803 | 0 | 149.692 | 55.9099 | 0 | 0 | 25.2098 | 19.0363 | 0 | 0 | 0 | 0 | 290.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171556 | 0 | 171556 | 346503 | -1001250 | 0 | 1 | 346503 | -2001250
1 | 4 | 13 | 3 | 39.8406 | 0 | 150.207 | 52.7527 | 0 | 0 | 11.2008 | 19.0363 | 0 | 0 | 0 | 0 | 273.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171554 | 0 | 171554 | 346925 | -989077 | 0 | 2 | 346925 | -1989077
1 | 4 | 14 | 3 | 41.344 | 0 | 165.698 | 46.6406 | 0 | 0 | 6.207 | 19.0363 | 0 | 0 | 0 | 0 | 278.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171552 | 0 | 171552 | 379839 | -920188 | 1 | 2 | 379839 | -1920188
1 | 4 | 15 | 3 | 41.2087 | 0 | 172.702 | 45.472 | 0 | 0 | 6.2123 | 19.0363 | 0 | 0 | 0 | 0 | 284.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169333 | 0 | 169333 | 399008 | -895142 | 1 | 3 | 399008 | -1895142
1 | 4 | 16 | 3 | 42.1641 | 0 | 173.986 | 49.2026 | 0 | 0 | 6.2106 | 19.0363 | 0 | 0 | 0 | 0 | 290.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153937 | 0 | 153937 | 402271 | -966075 | -2 | 0 | 402271 | -1966075
1 | 4 | 17 | 3 | 53.0746 | 0 | 169.782 | 56.059 | 0 | 0 | 6.2054 | 19.0363 | 0 | 0 | 0 | 2.4 | 306.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125647 | 0 | 125647 | 393840 | -1095600 | -5 | -4 | 393840 | -2095600
1 | 4 | 18 | 3 | 49.7836 | 0 | 152.497 | 62.3801 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 6.4 | 315.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94213.9 | 0 | 94213.9 | 369188 | -1202490 | -8 | -7 | 369188 | -2202490
1 | 4 | 19 | 3 | 34.11 | 0 | 93.4203 | 71.6376 | 0 | 0 | 25.2088 | 19.0911 | 0 | 0 | 0 | 7.2 | 250.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58314.6 | 0 | 58314.6 | 320385 | -1194250 | -9 | -8 | 320385 | -2194250
1 | 4 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 15.6427 | 0 | 5.9936 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41709.1 | 0 | 41709.1 | 203939 | -40766 | -10 | -10 | 203939 | -1040766
1 | 4 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.2693 | 0 | 5.9346 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37012.7 | 0 | 37012.7 | 177187 | -168662 | -12 | -11 | 177187 | -1168662
1 | 4 | 22 | 3 | 13.825 | 0 | 48.8953 | 12.6775 | 0 | 0 | 9.7652 | 17.5105 | 0 | 0 | 0 | 7.2 | 109.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22702.8 | 0 | 22702.8 | 154820 | -222363 | -13 | -12 | 154820 | -1222363
1 | 4 | 23 | 3 | 11.1963 | 0 | 44.3342 | 16.8808 | 0 | 0 | 14.8085 | 17.5105 | 0 | 0 | 0 | 6.4 | 111.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12202.1 | 0 | 12202.1 | 146794 | -281517 | -14 | -14 | 146794 | -1281517
1 | 4 | 24 | 3 | 10.3176 | 0 | 42.5403 | 17.8171 | 0 | 0 | 16.2571 | 17.5105 | 0 | 0 | 0 | 5.6 | 110.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615.2 | 0 | 10615.2 | 136062 | -292794 | -15 | -15 | 136062 | -1292794
1 | 5 | 1 | 4 | 10.73 | 0 | 42.3304 | 19.5178 | 0 | 0 | 19.3258 | 17.3638 | 0 | 0 | 0 | 4.8 | 114.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10618.9 | 0 | 10618.9 | 137116 | -321855 | -16 | -16 | 137116 | -1321855
1 | 5 | 2 | 4 | 10.73 | 0 | 42.3304 | 20.7221 | 0 | 0 | 21.5067 | 17.3638 | 0 | 0 | 0 | 4.8 | 117.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10621.7 | 0 | 10621.7 | 132465 | -336032 | -17 | -17 | 132465 | -1336032
1 | 5 | 3 | 4 | 10.73 | 0 | 42.3304 | 24.0126 | 0 | 0 | 25.3062 | 17.3638 | 0 | 0 | 0 | 4.8 | 124.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10624.1 | 0 | 10624.1 | 131042 | -396128 | -18 | -18 | 131042 | -1396128
1 | 5 | 4 | 4 | 10.73 | 0 | 42.3304 | 24.4204 | 0 | 0 | 25.303 | 17.3638 | 0 | 0 | 0 | 4.8 | 124.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10626.2 | 0 | 10626.2 | 129719 | -390349 | -19 | -18 | 129719 | -1390349
1 | 5 | 5 | 4 | 11.8202 | 0 | 44.8242 | 28.9317 | 0 | 0 | 25.298 | 17.5105 | 0 | 0 | 0 | 4.8 | 133.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11803.2 | 0 | 11803.2 | 136538 | -463836 | -19 | -19 | 136538 | -1463836
1 | 5 | 6 | 4 | 24.3093 | 0 | 69.9783 | 27.6273 | 0 | 0 | 25.3042 | 17.5105 | 0 | 0 | 0 | 4.8 | 169.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28655.9 | 0 | 28655.9 | 176230 | -427696 | -19 | -19 | 176230 | -1427696
1 | 5 | 7 | 4 | 49.0171 | 0 | 140.608 | 91.6701 | 0 | 0 | 25.286 | 20.1765 | 0 | 0 | 0 | 3.2 | 329.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84909.5 | 0 | 84909.5 | 312393 | -1685320 | -16 | -16 | 312393 | -2685320
1 | 5 | 8 | 4 | 52.7282 | 0 | 168.222 | 83.2718 | 0 | 0 | 25.2491 | 19.768 | 0 | 0 | 0 | 0.8 | 350.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103124 | 0 | 103124 | 374823 | -1552780 | -14 | -13 | 374823 | -2552780
1 | 5 | 9 | 4 | 43.2194 | 0 | 173.795 | 72.2146 | 0 | 0 | 25.2184 | 19.3024 | 0 | 0 | 0 | 0 | 333.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142731 | 0 | 142731 | 394761 | -1344900 | -11 | -10 | 394761 | -2344900
1 | 5 | 10 | 4 | 41.0691 | 0 | 172.186 | 66.0673 | 0 | 0 | 25.2101 | 19.128 | 0 | 0 | 0 | 0 | 323.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167953 | 0 | 167953 | 392619 | -1232730 | -6 | -5 | 392619 | -2232730
1 | 5 | 11 | 4 | 41.2301 | 0 | 163.102 | 61.8836 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 0 | 310.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171549 | 0 | 171549 | 373920 | -1134840 | -1 | 0 | 373920 | -2134840
1 | 5 | 12 | 4 | 40.7878 | 0 | 149.692 | 53.339 | 0 | 0 | 25.2127 | 19.0363 | 0 | 0 | 0 | 0 | 288.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171548 | 0 | 171548 | 347287 | -945266 | 4 | 5 | 347287 | -1945266
1 | 5 | 13 | 4 | 39.8278 | 0 | 150.207 | 49.6969 | 0 | 0 | 25.2156 | 19.0363 | 0 | 0 | 0 | 0 | 283.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171545 | 0 | 171545 | 347844 | -896470 | 6 | 8 | 347844 | -1896470
1 | 5 | 14 | 4 | 41.3183 | 0 | 165.698 | 41.0452 | 0 | 0 | 25.2149 | 19.0363 | 0 | 0 | 0 | 0 | 292.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171541 | 0 | 171541 | 380985 | -808688 | 9 | 10 | 380985 | -1808688
1 | 5 | 15 | 4 | 40.7079 | 0 | 172.702 | 38.0982 | 0 | 0 | 7.3736 | 19.0363 | 0 | 0 | 0 | 0 | 277.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169323 | 0 | 169323 | 400054 | -751993 | 11 | 13 | 400054 | -1751993
1 | 5 | 16 | 4 | 41.8273 | 0 | 173.986 | 40.019 | 0 | 0 | 7.2611 | 19.0363 | 0 | 0 | 0 | 0 | 282.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153926 | 0 | 153926 | 403332 | -787772 | 12 | 14 | 403332 | -1787772
1 | 5 | 17 | 4 | 55.3612 | 0 | 169.782 | 42.3348 | 0 | 0 | 25.2268 | 19.0363 | 0 | 0 | 0 | 2.4 | 314.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125635 | 0 | 125635 | 393803 | -810128 | 13 | 14 | 393803 | -1810128
1 | 5 | 18 | 4 | 49.7836 | 0 | 152.497 | 47.4456 | 0 | 0 | 25.2284 | 19.0363 | 0 | 0 | 0 | 6.4 | 300.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94202.7 | 0 | 94202.7 | 374039 | -851689 | 13 | 15 | 374039 | -1851689
1 | 5 | 19 | 4 | 34.11 | 0 | 93.4203 | 52.7938 | 0 | 0 | 25.2364 | 19.0363 | 0 | 0 | 0 | 7.2 | 231.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58303.1 | 0 | 58303.1 | 296033 | -852350 | 14 | 16 | 296033 | -1852350
1 | 5 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 15.6943 | 0 | 5.9996 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41697.2 | 0 | 41697.2 | 209330 | -19328.4 | 15 | 17 | 209330 | -1019328.4
1 | 5 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.2125 | 0 | 5.9338 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37001.3 | 0 | 37001.3 | 176805 | -84196.4 | 15 | 18 | 176805 | -1084196.4
1 | 5 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 11.9756 | 0 | 5.9128 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22691 | 0 | 22691 | 159409 | -128262 | 16 | 18 | 159409 | -1128262
1 | 5 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.0329 | 0 | 5.9027 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12190 | 0 | 12190 | 146162 | -164481 | 16 | 17 | 146162 | -1164481
1 | 5 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 10.6793 | 0 | 5.9 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.5477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10603.3 | 0 | 10603.3 | 140682 | -183039 | 16 | 17 | 140682 | -1183039
1 | 6 | 1 | 5 | 10.8489 | 0 | 42.3304 | 11.2864 | 0 | 0 | 8.7379 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10607.4 | 0 | 10607.4 | 139561 | -202807 | 15 | 16 | 139561 | -1202807
1 | 6 | 2 | 5 | 10.8489 | 0 | 42.3304 | 12.1886 | 0 | 0 | 9.3894 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.9211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10610.5 | 0 | 10610.5 | 137265 | -214647 | 14 | 15 | 137265 | -1214647
1 | 6 | 3 | 5 | 10.8489 | 0 | 42.3304 | 12.9282 | 0 | 0 | 10.094 | 17.3638 | 0 | 0 | 0 | 4.8 | 98.3653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10613.3 | 0 | 10613.3 | 136149 | -231795 | 13 | 14 | 136149 | -1231795
1 | 6 | 4 | 5 | 10.8489 | 0 | 42.3304 | 13.482 | 0 | 0 | 10.7226 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.5477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615.6 | 0 | 10615.6 | 135177 | -240270 | 12 | 13 | 135177 | -1240270
1 | 6 | 5 | 5 | 11.8202 | 0 | 44.8242 | 14.3357 | 0 | 0 | 11.7466 | 17.5105 | 0 | 0 | 0 | 4.8 | 105.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11791.7 | 0 | 11791.7 | 137217 | -257156 | 10 | 11 | 137217 | -1257156
1 | 6 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.5772 | 0 | 5.9335 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28643.3 | 0 | 28643.3 | 183699 | -228342 | 9 | 10 | 183699 | -1228342
1 | 6 | 7 | 5 | 49.0171 | 0 | 140.608 | 65.6891 | 0 | 0 | 25.209 | 19.5021 | 0 | 0 | 0 | 3.2 | 303.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84895.7 | 0 | 84895.7 | 317045 | -1163920 | 9 | 10 | 317045 | -2163920
1 | 6 | 8 | 5 | 52.6609 | 0 | 168.222 | 57.9444 | 0 | 0 | 25.2074 | 19.2334 | 0 | 0 | 0 | 0.8 | 324.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103109 | 0 | 103109 | 379001 | -1066430 | 9 | 9 | 379001 | -2066430
1 | 6 | 9 | 5 | 41.6684 | 0 | 173.795 | 50.2818 | 0 | 0 | 25.212 | 19.0622 | 0 | 0 | 0 | 0 | 310.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142723 | 0 | 142723 | 398269 | -940523 | 9 | 9 | 398269 | -1940523
1 | 6 | 10 | 5 | 40.7221 | 0 | 172.186 | 46.6752 | 0 | 0 | 25.2189 | 19.0363 | 0 | 0 | 0 | 0 | 303.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167942 | 0 | 167942 | 396255 | -865404 | 11 | 12 | 396255 | -1865404
1 | 6 | 11 | 5 | 41.2274 | 0 | 163.102 | 46.2508 | 0 | 0 | 25.2264 | 19.0363 | 0 | 0 | 0 | 0 | 294.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171538 | 0 | 171538 | 377693 | -832883 | 14 | 15 | 377693 | -1832883
1 | 6 | 12 | 5 | 40.9817 | 0 | 149.692 | 43.1665 | 0 | 0 | 25.2419 | 19.0363 | 0 | 0 | 0 | 0 | 278.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171537 | 0 | 171537 | 364091 | -755693 | 16 | 18 | 364091 | -1755693
1 | 6 | 13 | 5 | 39.8376 | 0 | 150.207 | 39.5644 | 0 | 0 | 6.2459 | 19.0363 | 0 | 0 | 0 | 0 | 254.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171535 | 0 | 171535 | 351613 | -697300 | 19 | 21 | 351613 | -1697300
1 | 6 | 14 | 5 | 41.3196 | 0 | 165.698 | 32.2736 | 0 | 0 | 6.2512 | 19.0363 | 0 | 0 | 0 | 0 | 264.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171532 | 0 | 171532 | 384918 | -605176 | 22 | 24 | 384918 | -1605176
1 | 6 | 15 | 5 | 40.7309 | 0 | 172.702 | 27.5072 | 0 | 0 | 6.2582 | 19.0363 | 0 | 0 | 0 | 0 | 266.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169313 | 0 | 169313 | 403570 | -540796 | 25 | 27 | 403570 | -1540796
1 | 6 | 16 | 5 | 42.8933 | 0 | 173.986 | 26.2196 | 0 | 0 | 6.2625 | 19.0363 | 0 | 0 | 0 | 0 | 268.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153916 | 0 | 153916 | 406549 | -517838 | 26 | 29 | 406549 | -1517838
1 | 6 | 17 | 5 | 54.0666 | 0 | 169.782 | 27.9681 | 0 | 0 | 6.2749 | 19.0363 | 0 | 0 | 0 | 2.4 | 279.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125625 | 0 | 125625 | 397480 | -519454 | 28 | 30 | 397480 | -1519454
1 | 6 | 18 | 5 | 49.7836 | 0 | 152.497 | 29.9725 | 0 | 0 | 6.2777 | 19.0363 | 0 | 0 | 0 | 6.4 | 263.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94191.3 | 0 | 94191.3 | 382880 | -529478 | 29 | 32 | 382880 | -1529478
1 | 6 | 19 | 5 | 34.11 | 0 | 93.4203 | 33.6011 | 0 | 0 | 25.2854 | 19.0363 | 0 | 0 | 0 | 7.2 | 212.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58291.4 | 0 | 58291.4 | 296539 | -565257 | 30 | 32 | 296539 | -1565257
1 | 6 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.4534 | 0 | 5.9523 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41685.5 | 0 | 41685.5 | 178953 | -16209.7 | 30 | 33 | 178953 | -1016209.7
1 | 6 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.8523 | 0 | 5.9205 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36990.8 | 0 | 36990.8 | 159900 | -25380.5 | 30 | 33 | 159900 | -1025380.5
1 | 6 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.6418 | 0 | 5.935 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22678 | 0 | 22678 | 171524 | -35937.7 | 30 | 33 | 171524 | -1035937.7
1 | 6 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.3478 | 0 | 5.9133 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12175.4 | 0 | 12175.4 | 153552 | -63739.5 | 30 | 32 | 153552 | -1063739.5
1 | 6 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.8362 | 0 | 5.9072 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.3 | 0 | 10588.3 | 147066 | -73312.9 | 29 | 32 | 147066 | -1073312.9
1 | 7 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.5725 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10592 | 0 | 10592 | 144027 | -90810.5 | 28 | 31 | 144027 | -1090810.5
1 | 7 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3971 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10594.8 | 0 | 10594.8 | 142166 | -106252 | 27 | 30 | 142166 | -1106252
1 | 7 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2467 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.1 | 0 | 10598.1 | 140849 | -122385 | 26 | 29 | 140849 | -1122385
1 | 7 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.1285 | 0 | 5.9015 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10600.5 | 0 | 10600.5 | 139813 | -135343 | 26 | 28 | 139813 | -1135343
1 | 7 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0022 | 0 | 5.9008 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10602.9 | 0 | 10602.9 | 138713 | -147368 | 25 | 27 | 138713 | -1147368
1 | 7 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8867 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10605 | 0 | 10605 | 137719 | -159029 | 24 | 26 | 137719 | -1159029
1 | 7 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7783 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10607.1 | 0 | 10607.1 | 136786 | -169738 | 23 | 25 | 136786 | -1169738
1 | 7 | 8 | 6 | 6.2816 | 0 | 42.7453 | 63.312 | 0 | 0 | 25.2259 | 19.5638 | 0 | 0 | 0 | 0.8 | 157.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10609.1 | 0 | 10609.1 | 123879 | -999557 | 23 | 25 | 123879 | -1999557
1 | 7 | 9 | 6 | 5.3483 | 0 | 42.7453 | 53.6129 | 0 | 0 | 25.2349 | 19.1003 | 0 | 0 | 0 | 0 | 146.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10610.9 | 0 | 10610.9 | 127013 | -847437 | 22 | 24 | 127013 | -1847437
1 | 7 | 10 | 6 | 5.7138 | 0 | 42.7453 | 40.6873 | 0 | 0 | 25.2433 | 18.8896 | 0 | 0 | 0 | 0 | 133.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10596 | 0 | 10596 | 122753 | -681091 | 24 | 26 | 122753 | -1681091
1 | 7 | 11 | 6 | 5.5661 | 0 | 42.7453 | 34.6078 | 0 | 0 | 25.2492 | 18.8896 | 0 | 0 | 0 | 0 | 127.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.5 | 0 | 10593.5 | 122294 | -590689 | 26 | 29 | 122294 | -1590689
1 | 7 | 12 | 6 | 5.5167 | 0 | 42.7453 | 30.0969 | 0 | 0 | 25.2563 | 18.8896 | 0 | 0 | 0 | 0 | 122.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10591.8 | 0 | 10591.8 | 121833 | -528240 | 27 | 31 | 121833 | -1528240
1 | 7 | 13 | 6 | 5.4816 | 0 | 42.7453 | 27.5323 | 0 | 0 | 9.5803 | 18.8896 | 0 | 0 | 0 | 0 | 104.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.7 | 0 | 10590.7 | 121414 | -497010 | 28 | 31 | 121414 | -1497010
1 | 7 | 14 | 6 | 5.4933 | 0 | 42.7453 | 25.8768 | 0 | 0 | 6.2608 | 18.8896 | 0 | 0 | 0 | 0 | 99.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.9 | 0 | 10589.9 | 121011 | -472768 | 28 | 32 | 121011 | -1472768
1 | 7 | 15 | 6 | 5.5428 | 0 | 42.7453 | 0 | 10.1516 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 77.1651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.3 | 0 | 10589.3 | 122226 | -17367.3 | 28 | 32 | 122226 | -1017367.3
1 | 7 | 16 | 6 | 5.7396 | 0 | 42.7453 | 0 | 10.0083 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 77.2187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.9 | 0 | 10588.9 | 120344 | -22780.7 | 26 | 29 | 120344 | -1022780.7
1 | 7 | 17 | 6 | 7.9601 | 0 | 42.7453 | 0 | 11.7022 | 0 | 5.9054 | 17.3638 | 0 | 0 | 0 | 2.4 | 88.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.1 | 0 | 10593.1 | 144254 | -44837.9 | 24 | 27 | 144254 | -1044837.9
1 | 7 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3229 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.5316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.6 | 0 | 10595.6 | 139306 | -55285.2 | 22 | 24 | 139306 | -1055285.2
1 | 7 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.5547 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.5 | 0 | 10598.5 | 141222 | -77597.2 | 22 | 23 | 141222 | -1077597.2
1 | 7 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9579 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10601.6 | 0 | 10601.6 | 134038 | -85422.8 | 21 | 23 | 134038 | -1085422.8
1 | 7 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7192 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604.1 | 0 | 10604.1 | 133254 | -111665 | 21 | 22 | 133254 | -1111665
1 | 7 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.476 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10606.1 | 0 | 10606.1 | 131100 | -128799 | 20 | 21 | 131100 | -1128799
1 | 7 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.347 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10608.5 | 0 | 10608.5 | 130732 | -149999 | 19 | 21 | 130732 | -1149999
1 | 7 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2419 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10610.8 | 0 | 10610.8 | 129660 | -161200 | 19 | 20 | 129660 | -1161200
1 | 8 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1219 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3987.05 | 0 | 3987.05 | 128894 | -172257 | 19 | 21 | 128894 | -1172257
1 | 8 | 2 | 7 | 5.1054 | 0 | 42.7453 | 10.383 | 0 | 0 | 8.1003 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3989.16 | 0 | 3989.16 | 128339 | -180576 | 20 | 21 | 128339 | -1180576
1 | 8 | 3 | 7 | 5.1054 | 0 | 42.7453 | 10.667 | 0 | 0 | 8.275 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3991.35 | 0 | 3991.35 | 127761 | -184423 | 21 | 22 | 127761 | -1184423
1 | 8 | 4 | 7 | 5.1054 | 0 | 42.7453 | 10.9527 | 0 | 0 | 8.4917 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3993.41 | 0 | 3993.41 | 128120 | -188886 | 23 | 25 | 128120 | -1188886
1 | 8 | 5 | 7 | 5.1054 | 0 | 42.7453 | 10.9254 | 0 | 0 | 8.4695 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.34 | 0 | 3995.34 | 127208 | -185277 | 25 | 28 | 127208 | -1185277
1 | 8 | 6 | 7 | 5.1054 | 0 | 42.7453 | 10.7062 | 0 | 0 | 8.29 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3997.18 | 0 | 3997.18 | 127385 | -179986 | 27 | 31 | 127385 | -1179986
1 | 8 | 7 | 7 | 5.1054 | 0 | 42.7453 | 10.4649 | 0 | 0 | 8.0541 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.9334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.91 | 0 | 3998.91 | 126918 | -175528 | 29 | 32 | 126918 | -1175528
1 | 8 | 8 | 7 | 5.0675 | 0 | 42.7453 | 0 | 10.1366 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000.53 | 0 | 4000.53 | 126683 | -170112 | 30 | 33 | 126683 | -1170112
1 | 8 | 9 | 7 | 4.163 | 0 | 42.7453 | 0 | 10.198 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 80.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4001.99 | 0 | 4001.99 | 127050 | -144230 | 31 | 34 | 127050 | -1144230
1 | 8 | 10 | 7 | 4.198 | 0 | 42.7453 | 0 | 10.289 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 80.4934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4003.31 | 0 | 4003.31 | 127661 | -109601 | 32 | 36 | 127661 | -1109601
1 | 8 | 11 | 7 | 4.1787 | 0 | 42.7453 | 0 | 10.42 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.6053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4004.57 | 0 | 4004.57 | 128425 | -89499.1 | 34 | 37 | 128425 | -1089499.1
1 | 8 | 12 | 7 | 4.1657 | 0 | 42.7453 | 0 | 10.616 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 0 | 80.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4005.64 | 0 | 4005.64 | 130032 | -80861.9 | 34 | 39 | 130032 | -1080861.9
1 | 8 | 13 | 7 | 4.1539 | 0 | 42.7453 | 0 | 10.7736 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 80.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.29 | 0 | 4006.29 | 131061 | -75243.3 | 35 | 40 | 131061 | -1075243.3
1 | 8 | 14 | 7 | 4.1536 | 0 | 42.7453 | 0 | 10.8463 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 0 | 81.0079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.41 | 0 | 4006.41 | 131162 | -67828.9 | 36 | 40 | 131162 | -1067828.9
1 | 8 | 15 | 7 | 4.1663 | 0 | 42.7453 | 0 | 10.923 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 0 | 81.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.57 | 0 | 4006.57 | 131836 | -65862.4 | 36 | 41 | 131836 | -1065862.4
1 | 8 | 16 | 7 | 4.2782 | 0 | 42.7453 | 0 | 10.9018 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 0 | 81.1882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007.01 | 0 | 4007.01 | 131205 | -65673.2 | 36 | 40 | 131205 | -1065673.2
1 | 8 | 17 | 7 | 6.4235 | 0 | 42.7453 | 0 | 10.7736 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007.28 | 0 | 4007.28 | 129681 | -70519 | 36 | 40 | 129681 | -1070519
1 | 8 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6318 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007.84 | 0 | 4007.84 | 128190 | -81731.1 | 36 | 39 | 128190 | -1081731.1
1 | 8 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5439 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.7 | 0 | 4008.7 | 127245 | -88349 | 36 | 39 | 127245 | -1088349
1 | 8 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4854 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4009.91 | 0 | 4009.91 | 126654 | -98029.2 | 36 | 38 | 126654 | -1098029.2
1 | 8 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4394 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.03 | 0 | 4011.03 | 126255 | -105788 | 36 | 38 | 126255 | -1105788
1 | 8 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4193 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4012.19 | 0 | 4012.19 | 126190 | -116996 | 35 | 37 | 126190 | -1116996
1 | 8 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.391 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4013.24 | 0 | 4013.24 | 125924 | -120383 | 35 | 37 | 125924 | -1120383
1 | 8 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3869 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.6566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.24 | 0 | 4014.24 | 125972 | -126579 | 34 | 36 | 125972 | -1126579
1 | 9 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3689 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10641.2 | 0 | 10641.2 | 125901 | -127155 | 33 | 35 | 125901 | -1127155
1 | 9 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3418 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10642.1 | 0 | 10642.1 | 125902 | -131921 | 32 | 35 | 125902 | -1131921
1 | 9 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3214 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10642.2 | 0 | 10642.2 | 125763 | -137960 | 31 | 34 | 125763 | -1137960
1 | 9 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.2973 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10642.8 | 0 | 10642.8 | 125664 | -144381 | 30 | 33 | 125664 | -1144381
1 | 9 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.5078 | 0 | 5.8978 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11817.1 | 0 | 11817.1 | 128825 | -153926 | 29 | 31 | 128825 | -1153926
1 | 9 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.9799 | 0 | 5.942 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28667.2 | 0 | 28667.2 | 176326 | -124246 | 27 | 30 | 176326 | -1124246
1 | 9 | 7 | 1 | 49.0171 | 0 | 140.608 | 48.7385 | 0 | 0 | 25.2252 | 19.286 | 0 | 0 | 0 | 3.2 | 286.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84918.1 | 0 | 84918.1 | 311470 | -849102 | 28 | 31 | 311470 | -1849102
1 | 9 | 8 | 1 | 52.5893 | 0 | 168.222 | 41.6446 | 0 | 0 | 25.2416 | 19.1191 | 0 | 0 | 0 | 0.8 | 307.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103130 | 0 | 103130 | 373817 | -732149 | 27 | 31 | 373817 | -1732149
1 | 9 | 9 | 1 | 42.4689 | 0 | 173.795 | 29.5849 | 0 | 0 | 25.2503 | 19.0363 | 0 | 0 | 0 | 0 | 290.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142737 | 0 | 142737 | 392773 | -567527 | 27 | 32 | 392773 | -1567527
1 | 9 | 10 | 1 | 41.6326 | 0 | 172.186 | 0 | 25.5713 | 0 | 6.2719 | 19.0363 | 0 | 0 | 0 | 0 | 264.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167955 | 0 | 167955 | 391781 | -471628 | 29 | 34 | 391781 | -1471628
1 | 9 | 11 | 1 | 41.5168 | 0 | 163.102 | 0 | 26.3164 | 0 | 6.3001 | 19.0363 | 0 | 0 | 0 | 0 | 256.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171550 | 0 | 171550 | 382472 | -414373 | 31 | 37 | 382472 | -1414373
1 | 9 | 12 | 1 | 40.8897 | 0 | 149.692 | 0 | 26.459 | 0 | 6.3133 | 19.0363 | 0 | 0 | 0 | 0 | 242.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171547 | 0 | 171547 | 385012 | -362588 | 32 | 39 | 385012 | -1362588
1 | 9 | 13 | 1 | 39.8655 | 0 | 150.207 | 0 | 23.9932 | 0 | 6.3182 | 19.0363 | 0 | 0 | 0 | 0 | 239.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171544 | 0 | 171544 | 358409 | -325190 | 32 | 39 | 358409 | -1325190
1 | 9 | 14 | 1 | 41.3464 | 0 | 165.698 | 0 | 25.9089 | 0 | 6.3235 | 19.0363 | 0 | 0 | 0 | 0 | 258.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171542 | 0 | 171542 | 398809 | -299804 | 32 | 38 | 398809 | -1299804
1 | 9 | 15 | 1 | 40.92 | 0 | 172.702 | 0 | 27.3156 | 0 | 6.3296 | 19.0363 | 0 | 0 | 0 | 0 | 266.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169323 | 0 | 169323 | 418993 | -294200 | 31 | 38 | 418993 | -1294200
1 | 9 | 16 | 1 | 41.7858 | 0 | 173.986 | 0 | 25.6969 | 0 | 6.3255 | 19.0363 | 0 | 0 | 0 | 0 | 266.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153924 | 0 | 153924 | 403729 | -303423 | 30 | 36 | 403729 | -1303423
1 | 9 | 17 | 1 | 52.3396 | 0 | 169.782 | 0 | 25.2261 | 0 | 6.3059 | 19.0363 | 0 | 0 | 0 | 2.4 | 275.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125631 | 0 | 125631 | 396845 | -373666 | 29 | 33 | 396845 | -1373666
1 | 9 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 25.9761 | 0 | 6.2904 | 19.0363 | 0 | 0 | 0 | 6.4 | 259.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94197.6 | 0 | 94197.6 | 385527 | -464673 | 27 | 31 | 385527 | -1464673
1 | 9 | 19 | 1 | 34.11 | 0 | 93.4203 | 30.1731 | 0 | 0 | 25.2955 | 19.0363 | 0 | 0 | 0 | 7.2 | 209.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58297.9 | 0 | 58297.9 | 297146 | -502566 | 28 | 31 | 297146 | -1502566
1 | 9 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 14.2763 | 0 | 5.9481 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41692.8 | 0 | 41692.8 | 176588 | -13765.5 | 28 | 31 | 176588 | -1013765.5
1 | 9 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.5216 | 0 | 5.9164 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36998.1 | 0 | 36998.1 | 157639 | -19153.6 | 28 | 31 | 157639 | -1019153.6
1 | 9 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.4721 | 0 | 5.9308 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22685.4 | 0 | 22685.4 | 167612 | -33528.4 | 29 | 31 | 167612 | -1033528.4
1 | 9 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.302 | 0 | 5.9124 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.6555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12182.4 | 0 | 12182.4 | 152198 | -46043.6 | 29 | 32 | 152198 | -1046043.6
1 | 9 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.7656 | 0 | 5.9063 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.2 | 0 | 10595.2 | 145426 | -60978.3 | 29 | 32 | 145426 | -1060978.3
1 | 10 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.5644 | 0 | 5.9043 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.9 | 0 | 10598.9 | 142727 | -70539.6 | 29 | 32 | 142727 | -1070539.6
1 | 10 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4128 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10601.6 | 0 | 10601.6 | 140994 | -80997 | 29 | 31 | 140994 | -1080997
1 | 10 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.2812 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604 | 0 | 10604 | 139672 | -92382.9 | 29 | 31 | 139672 | -1092382.9
1 | 10 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.1899 | 0 | 5.9016 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10606.1 | 0 | 10606.1 | 138838 | -101980 | 29 | 31 | 138838 | -1101980
1 | 10 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.3561 | 0 | 5.9028 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11781.8 | 0 | 11781.8 | 141174 | -109306 | 29 | 30 | 141174 | -1109306
1 | 10 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.6922 | 0 | 5.9612 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28632.9 | 0 | 28632.9 | 188696 | -93293.9 | 28 | 30 | 188696 | -1093293.9
1 | 10 | 7 | 2 | 49.0171 | 0 | 140.608 | 41.7276 | 0 | 0 | 25.2337 | 19.0929 | 0 | 0 | 0 | 3.2 | 278.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84884.9 | 0 | 84884.9 | 319908 | -744013 | 29 | 30 | 319908 | -1744013
1 | 10 | 8 | 2 | 52.8597 | 0 | 168.222 | 37.6034 | 0 | 0 | 25.249 | 19.0363 | 0 | 0 | 0 | 0.8 | 303.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103098 | 0 | 103098 | 381924 | -667293 | 29 | 30 | 381924 | -1667293
1 | 10 | 9 | 2 | 46.0177 | 0 | 173.795 | 28.9468 | 0 | 0 | 25.2562 | 19.0363 | 0 | 0 | 0 | 0 | 293.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142716 | 0 | 142716 | 400555 | -556968 | 28 | 30 | 400555 | -1556968
1 | 10 | 10 | 2 | 40.9738 | 0 | 172.186 | 0 | 25.711 | 0 | 6.2683 | 19.0363 | 0 | 0 | 0 | 0 | 264.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167934 | 0 | 167934 | 398820 | -497335 | 30 | 32 | 398820 | -1497335
1 | 10 | 11 | 2 | 41.4129 | 0 | 163.102 | 0 | 25.9992 | 0 | 6.2991 | 19.0363 | 0 | 0 | 0 | 0 | 255.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171530 | 0 | 171530 | 385435 | -407872 | 32 | 35 | 385435 | -1407872
1 | 10 | 12 | 2 | 40.9999 | 0 | 149.692 | 0 | 25.4828 | 0 | 6.3235 | 19.0363 | 0 | 0 | 0 | 0 | 241.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171528 | 0 | 171528 | 375507 | -338364 | 33 | 37 | 375507 | -1338364
1 | 10 | 13 | 2 | 39.8546 | 0 | 150.207 | 0 | 23.433 | 0 | 6.3164 | 19.0363 | 0 | 0 | 0 | 0 | 238.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171526 | 0 | 171526 | 354421 | -331241 | 32 | 37 | 354421 | -1331241
1 | 10 | 14 | 2 | 41.3414 | 0 | 165.698 | 0 | 24.6385 | 0 | 6.3235 | 19.0363 | 0 | 0 | 0 | 0 | 257.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171523 | 0 | 171523 | 387515 | -293118 | 32 | 36 | 387515 | -1293118
1 | 10 | 15 | 2 | 40.7286 | 0 | 172.702 | 0 | 25.8021 | 0 | 6.3318 | 19.0363 | 0 | 0 | 0 | 0 | 264.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169304 | 0 | 169304 | 405818 | -282858 | 31 | 36 | 405818 | -1282858
1 | 10 | 16 | 2 | 41.5189 | 0 | 173.986 | 0 | 25.9806 | 0 | 6.3175 | 19.0363 | 0 | 0 | 0 | 0 | 266.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153905 | 0 | 153905 | 408784 | -331866 | 30 | 34 | 408784 | -1331866
1 | 10 | 17 | 2 | 51.7795 | 0 | 169.782 | 0 | 25.6072 | 0 | 6.3057 | 19.0363 | 0 | 0 | 0 | 2.4 | 274.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125613 | 0 | 125613 | 402992 | -376360 | 29 | 33 | 402992 | -1376360
1 | 10 | 18 | 2 | 49.7836 | 0 | 152.497 | 0 | 26.1153 | 0 | 6.288 | 19.0363 | 0 | 0 | 0 | 6.4 | 260.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94180.3 | 0 | 94180.3 | 390920 | -461045 | 28 | 31 | 390920 | -1461045
1 | 10 | 19 | 2 | 34.11 | 0 | 93.4203 | 31.635 | 0 | 0 | 25.2926 | 19.0363 | 0 | 0 | 0 | 7.2 | 210.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58280.5 | 0 | 58280.5 | 306145 | -518337 | 26 | 29 | 306145 | -1518337
1 | 10 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.6563 | 0 | 5.9565 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41675.8 | 0 | 41675.8 | 180423 | -15087.9 | 24 | 26 | 180423 | -1015087.9
1 | 10 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.9461 | 0 | 5.9221 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36981.3 | 0 | 36981.3 | 161352 | -21733.9 | 21 | 24 | 161352 | -1021733.9
1 | 10 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.4745 | 0 | 5.9331 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22668.6 | 0 | 22668.6 | 171592 | -44859.7 | 21 | 24 | 171592 | -1044859.7
1 | 10 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.3089 | 0 | 5.9139 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12166.1 | 0 | 12166.1 | 155903 | -69058.9 | 21 | 23 | 155903 | -1069058.9
1 | 10 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.7722 | 0 | 5.9074 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10579.6 | 0 | 10579.6 | 148945 | -85775.4 | 21 | 23 | 148945 | -1085775.4
1 | 11 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.4999 | 0 | 5.9049 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10583.9 | 0 | 10583.9 | 146008 | -105650 | 20 | 22 | 146008 | -1105650
1 | 11 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3188 | 0 | 5.9034 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10587.3 | 0 | 10587.3 | 144110 | -120078 | 20 | 21 | 144110 | -1120078
1 | 11 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.1446 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.3 | 0 | 10590.3 | 142566 | -134890 | 19 | 20 | 142566 | -1134890
1 | 11 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.011 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10592.9 | 0 | 10592.9 | 141432 | -148547 | 19 | 21 | 141432 | -1148547
1 | 11 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.1298 | 0 | 5.9024 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.9871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11769.1 | 0 | 11769.1 | 143525 | -159204 | 20 | 21 | 143525 | -1159204
1 | 11 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.3462 | 0 | 5.9575 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28620.8 | 0 | 28620.8 | 190625 | -135170 | 20 | 22 | 190625 | -1135170
1 | 11 | 7 | 3 | 49.0171 | 0 | 140.608 | 50.1437 | 0 | 0 | 25.2161 | 19.1613 | 0 | 0 | 0 | 3.2 | 287.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84873.2 | 0 | 84873.2 | 321274 | -887121 | 21 | 22 | 321274 | -1887121
1 | 11 | 8 | 3 | 53.1394 | 0 | 168.222 | 44.5246 | 0 | 0 | 25.2301 | 19.0527 | 0 | 0 | 0 | 0.8 | 310.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103087 | 0 | 103087 | 383177 | -787193 | 22 | 23 | 383177 | -1787193
1 | 11 | 9 | 3 | 47.2137 | 0 | 173.795 | 36.5145 | 0 | 0 | 25.2416 | 19.0363 | 0 | 0 | 0 | 0 | 301.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142706 | 0 | 142706 | 402015 | -674768 | 22 | 23 | 402015 | -1674768
1 | 11 | 10 | 3 | 41.1032 | 0 | 172.186 | 33.6562 | 0 | 0 | 25.2562 | 19.0363 | 0 | 0 | 0 | 0 | 291.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167925 | 0 | 167925 | 399911 | -603934 | 23 | 24 | 399911 | -1603934
1 | 11 | 11 | 3 | 41.2334 | 0 | 163.102 | 33.6101 | 0 | 0 | 25.2652 | 19.0363 | 0 | 0 | 0 | 0 | 282.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171522 | 0 | 171522 | 385915 | -585767 | 23 | 24 | 385915 | -1585767
1 | 11 | 12 | 3 | 40.7977 | 0 | 149.692 | 29.226 | 0 | 0 | 25.2876 | 19.0363 | 0 | 0 | 0 | 0 | 264.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171521 | 0 | 171521 | 371091 | -500994 | 24 | 25 | 371091 | -1500994
1 | 11 | 13 | 3 | 39.8887 | 0 | 150.207 | 27.232 | 0 | 0 | 25.2846 | 19.0363 | 0 | 0 | 0 | 0 | 261.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171519 | 0 | 171519 | 354642 | -487832 | 24 | 25 | 354642 | -1487832
1 | 11 | 14 | 3 | 41.3501 | 0 | 165.698 | 0 | 24.8091 | 0 | 6.2856 | 19.0363 | 0 | 0 | 0 | 0 | 257.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171517 | 0 | 171517 | 387755 | -430335 | 24 | 26 | 387755 | -1430335
1 | 11 | 15 | 3 | 41.3572 | 0 | 172.702 | 0 | 25.7611 | 0 | 6.2925 | 19.0363 | 0 | 0 | 0 | 0 | 265.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169298 | 0 | 169298 | 406178 | -418209 | 23 | 26 | 406178 | -1418209
1 | 11 | 16 | 3 | 42.1933 | 0 | 173.986 | 0 | 25.9133 | 0 | 6.2806 | 19.0363 | 0 | 0 | 0 | 0 | 267.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153901 | 0 | 153901 | 408817 | -479607 | 20 | 22 | 408817 | -1479607
1 | 11 | 17 | 3 | 50.7028 | 0 | 169.782 | 30.0938 | 0 | 0 | 25.2649 | 19.0363 | 0 | 0 | 0 | 2.4 | 297.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125611 | 0 | 125611 | 402094 | -585283 | 16 | 17 | 402094 | -1585283
1 | 11 | 18 | 3 | 49.7836 | 0 | 152.497 | 39.5178 | 0 | 0 | 25.2453 | 19.0363 | 0 | 0 | 0 | 6.4 | 292.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94179.7 | 0 | 94179.7 | 387637 | -722444 | 12 | 13 | 387637 | -1722444
1 | 11 | 19 | 3 | 34.11 | 0 | 93.4203 | 46.0207 | 0 | 0 | 25.2526 | 19.0363 | 0 | 0 | 0 | 7.2 | 225.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58281.9 | 0 | 58281.9 | 314996 | -742464 | 13 | 14 | 314996 | -1742464
1 | 11 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.0692 | 0 | 5.9478 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41677.4 | 0 | 41677.4 | 180096 | -19262.4 | 14 | 15 | 180096 | -1019262.4
1 | 11 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.1726 | 0 | 5.9517 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36981.7 | 0 | 36981.7 | 185710 | -45599.4 | 15 | 16 | 185710 | -1045599.4
1 | 11 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.8217 | 0 | 5.9241 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22668.5 | 0 | 22668.5 | 167608 | -78358 | 16 | 17 | 167608 | -1078358
1 | 11 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.8055 | 0 | 5.9093 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12167.1 | 0 | 12167.1 | 153534 | -107357 | 17 | 18 | 153534 | -1107357
1 | 11 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.3411 | 0 | 5.9044 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10580.2 | 0 | 10580.2 | 147190 | -125489 | 18 | 19 | 147190 | -1125489
1 | 12 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.1299 | 0 | 5.9027 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10584.4 | 0 | 10584.4 | 144845 | -134964 | 20 | 21 | 144845 | -1134964
1 | 12 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.0428 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10587.8 | 0 | 10587.8 | 143379 | -144319 | 22 | 22 | 143379 | -1144319
1 | 12 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.986 | 0 | 5.9015 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.7 | 0 | 10590.7 | 142220 | -146417 | 23 | 24 | 142220 | -1146417
1 | 12 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.0466 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.2 | 0 | 10593.2 | 142548 | -146177 | 25 | 27 | 142548 | -1146177
1 | 12 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.1887 | 0 | 5.9027 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11769.2 | 0 | 11769.2 | 143691 | -140927 | 27 | 29 | 143691 | -1140927
1 | 12 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.6044 | 0 | 5.9619 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28620.7 | 0 | 28620.7 | 191346 | -106978 | 28 | 32 | 191346 | -1106978
1 | 12 | 7 | 4 | 49.0171 | 0 | 140.608 | 41.1624 | 0 | 0 | 25.2407 | 19.1153 | 0 | 0 | 0 | 3.2 | 278.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84872.8 | 0 | 84872.8 | 322171 | -717969 | 29 | 33 | 322171 | -1717969
1 | 12 | 8 | 4 | 53.2613 | 0 | 168.222 | 35.186 | 0 | 0 | 25.2545 | 19.0363 | 0 | 0 | 0 | 0.8 | 301.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103086 | 0 | 103086 | 383985 | -629934 | 29 | 33 | 383985 | -1629934
1 | 12 | 9 | 4 | 49.0885 | 0 | 173.795 | 0 | 25.73 | 0 | 6.2635 | 19.0363 | 0 | 0 | 0 | 0 | 273.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142703 | 0 | 142703 | 402525 | -502678 | 29 | 34 | 402525 | -1502678
1 | 12 | 10 | 4 | 45.0719 | 0 | 172.186 | 0 | 25.7475 | 0 | 6.2812 | 19.0363 | 0 | 0 | 0 | 0 | 268.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167922 | 0 | 167922 | 400863 | -450087 | 31 | 36 | 400863 | -1450087
1 | 12 | 11 | 4 | 42.6937 | 0 | 163.102 | 0 | 26.2471 | 0 | 6.2922 | 19.0363 | 0 | 0 | 0 | 0 | 257.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171517 | 0 | 171517 | 391981 | -434187 | 33 | 37 | 391981 | -1434187
1 | 12 | 12 | 4 | 41.7238 | 0 | 149.692 | 0 | 26.2503 | 0 | 6.2945 | 19.0363 | 0 | 0 | 0 | 0 | 242.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171515 | 0 | 171515 | 393742 | -392641 | 34 | 39 | 393742 | -1392641
1 | 12 | 13 | 4 | 40.0195 | 0 | 150.207 | 0 | 23.7453 | 0 | 6.2921 | 19.0363 | 0 | 0 | 0 | 0 | 239.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171513 | 0 | 171513 | 364300 | -371276 | 35 | 39 | 364300 | -1371276
1 | 12 | 14 | 4 | 42.5006 | 0 | 165.698 | 0 | 26.4303 | 0 | 6.3026 | 19.0363 | 0 | 0 | 0 | 0 | 259.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171511 | 0 | 171511 | 406819 | -332235 | 35 | 39 | 406819 | -1332235
1 | 12 | 15 | 4 | 41.8296 | 0 | 172.702 | 0 | 28.1496 | 0 | 6.3116 | 19.0363 | 0 | 0 | 0 | 0 | 268.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169293 | 0 | 169293 | 430013 | -325321 | 36 | 39 | 430013 | -1325321
1 | 12 | 16 | 4 | 45.3566 | 0 | 173.986 | 0 | 26.0483 | 0 | 6.3027 | 19.0363 | 0 | 0 | 0 | 0 | 270.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153895 | 0 | 153895 | 409715 | -362851 | 31 | 34 | 409715 | -1362851
1 | 12 | 17 | 4 | 55.3442 | 0 | 169.782 | 0 | 25.5111 | 0 | 6.2834 | 19.0363 | 0 | 0 | 0 | 2.4 | 278.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125603 | 0 | 125603 | 401931 | -445271 | 27 | 29 | 401931 | -1445271
1 | 12 | 18 | 4 | 49.7836 | 0 | 152.497 | 32.9707 | 0 | 0 | 25.2705 | 19.0363 | 0 | 0 | 0 | 6.4 | 285.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94169.8 | 0 | 94169.8 | 395957 | -579146 | 22 | 24 | 395957 | -1579146
1 | 12 | 19 | 4 | 34.11 | 0 | 93.4203 | 39.017 | 0 | 0 | 25.2757 | 19.0363 | 0 | 0 | 0 | 7.2 | 218.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58270.8 | 0 | 58270.8 | 311670 | -634527 | 20 | 22 | 311670 | -1634527
1 | 12 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.4044 | 0 | 5.9534 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41666.7 | 0 | 41666.7 | 181271 | -18045.2 | 18 | 20 | 181271 | -1018045.2
1 | 12 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.5662 | 0 | 5.9598 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36972 | 0 | 36972 | 188698 | -36795.4 | 16 | 18 | 188698 | -1036795.4
1 | 12 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.0558 | 0 | 5.9276 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22659.4 | 0 | 22659.4 | 169699 | -66530.2 | 16 | 18 | 169699 | -1066530.2
1 | 12 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.9871 | 0 | 5.9112 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12158.1 | 0 | 12158.1 | 155314 | -105491 | 16 | 17 | 155314 | -1105491
1 | 12 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.4158 | 0 | 5.9052 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10571.7 | 0 | 10571.7 | 148709 | -128992 | 15 | 17 | 148709 | -1128992
1 | 13 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.1683 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10576.3 | 0 | 10576.3 | 145959 | -150734 | 14 | 16 | 145959 | -1150734
1 | 13 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9937 | 0 | 5.9019 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10580 | 0 | 10580 | 144144 | -169608 | 13 | 14 | 144144 | -1169608
1 | 13 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.8129 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10583.3 | 0 | 10583.3 | 142607 | -188765 | 11 | 13 | 142607 | -1188765
1 | 13 | 4 | 5 | 10.8489 | 0 | 42.3304 | 11.4299 | 0 | 0 | 8.8905 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10586.2 | 0 | 10586.2 | 141230 | -207452 | 9 | 11 | 141230 | -1207452
1 | 13 | 5 | 5 | 11.8202 | 0 | 44.8242 | 12.7381 | 0 | 0 | 10.1081 | 17.5105 | 0 | 0 | 0 | 4.8 | 101.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11762.7 | 0 | 11762.7 | 142803 | -229897 | 7 | 8 | 142803 | -1229897
1 | 13 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.7321 | 0 | 5.9472 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28614.9 | 0 | 28614.9 | 189049 | -221887 | 5 | 6 | 189049 | -1221887
1 | 13 | 7 | 5 | 49.0171 | 0 | 140.608 | 65.6786 | 0 | 0 | 25.2107 | 19.3289 | 0 | 0 | 0 | 3.2 | 303.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84867.8 | 0 | 84867.8 | 319892 | -1168060 | 4 | 5 | 319892 | -2168060
1 | 13 | 8 | 5 | 52.5714 | 0 | 168.222 | 59.9678 | 0 | 0 | 25.2074 | 19.1682 | 0 | 0 | 0 | 0.8 | 325.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103082 | 0 | 103082 | 381816 | -1104780 | 3 | 5 | 381816 | -2104780
1 | 13 | 9 | 5 | 42.3798 | 0 | 173.795 | 50.9774 | 0 | 0 | 25.2108 | 19.0363 | 0 | 0 | 0 | 0 | 311.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142701 | 0 | 142701 | 400995 | -956205 | 3 | 4 | 400995 | -1956205
1 | 13 | 10 | 5 | 41.5851 | 0 | 172.186 | 47.9751 | 0 | 0 | 25.2158 | 19.0363 | 0 | 0 | 0 | 0 | 305.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167922 | 0 | 167922 | 398633 | -891590 | 4 | 5 | 398633 | -1891590
1 | 13 | 11 | 5 | 41.4985 | 0 | 163.102 | 46.9736 | 0 | 0 | 25.2192 | 19.0363 | 0 | 0 | 0 | 0 | 295.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171519 | 0 | 171519 | 379769 | -866372 | 5 | 7 | 379769 | -1866372
1 | 13 | 12 | 5 | 40.8299 | 0 | 149.692 | 42.8841 | 0 | 0 | 25.2297 | 19.0363 | 0 | 0 | 0 | 0 | 277.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171519 | 0 | 171519 | 354750 | -766954 | 6 | 8 | 354750 | -1766954
1 | 13 | 13 | 5 | 39.863 | 0 | 150.207 | 39.6893 | 0 | 0 | 25.2333 | 19.0363 | 0 | 0 | 0 | 0 | 274.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171518 | 0 | 171518 | 353042 | -736103 | 8 | 10 | 353042 | -1736103
1 | 13 | 14 | 5 | 41.3469 | 0 | 165.698 | 33.3961 | 0 | 0 | 25.2399 | 19.0363 | 0 | 0 | 0 | 0 | 284.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171515 | 0 | 171515 | 385915 | -663055 | 10 | 12 | 385915 | -1663055
1 | 13 | 15 | 5 | 40.9814 | 0 | 172.702 | 32.0494 | 0 | 0 | 25.2504 | 19.0363 | 0 | 0 | 0 | 0 | 290.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169297 | 0 | 169297 | 404775 | -634948 | 11 | 14 | 404775 | -1634948
1 | 13 | 16 | 5 | 41.912 | 0 | 173.986 | 34.5228 | 0 | 0 | 6.5397 | 19.0363 | 0 | 0 | 0 | 0 | 275.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153901 | 0 | 153901 | 407736 | -681385 | 9 | 12 | 407736 | -1681385
1 | 13 | 17 | 5 | 50.178 | 0 | 169.782 | 39.4817 | 0 | 0 | 25.2339 | 19.0363 | 0 | 0 | 0 | 2.4 | 306.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125611 | 0 | 125611 | 397577 | -775711 | 7 | 9 | 397577 | -1775711
1 | 13 | 18 | 5 | 49.7836 | 0 | 152.497 | 48.5647 | 0 | 0 | 25.2219 | 19.0363 | 0 | 0 | 0 | 6.4 | 301.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94179.7 | 0 | 94179.7 | 380243 | -891615 | 5 | 7 | 380243 | -1891615
1 | 13 | 19 | 5 | 34.11 | 0 | 93.4203 | 57.0686 | 0 | 0 | 25.2274 | 19.0363 | 0 | 0 | 0 | 7.2 | 236.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58281.3 | 0 | 58281.3 | 316958 | -932312 | 5 | 6 | 316958 | -1932312
1 | 13 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 15.6206 | 0 | 6.0021 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41676.2 | 0 | 41676.2 | 212644 | -19524.7 | 4 | 6 | 212644 | -1019524.7
1 | 13 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.044 | 0 | 5.9337 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36980.4 | 0 | 36980.4 | 179579 | -103144 | 4 | 5 | 179579 | -1103144
1 | 13 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 11.8296 | 0 | 5.9133 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22669.1 | 0 | 22669.1 | 163116 | -164249 | 3 | 4 | 163116 | -1164249
1 | 13 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 10.9079 | 0 | 5.9027 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12168.6 | 0 | 12168.6 | 149467 | -208695 | 2 | 3 | 149467 | -1208695
1 | 13 | 24 | 5 | 10.3176 | 0 | 42.5403 | 13.4625 | 0 | 0 | 11.2024 | 17.5105 | 0 | 0 | 0 | 5.6 | 100.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10582.3 | 0 | 10582.3 | 143618 | -235051 | 1 | 2 | 143618 | -1235051
1 | 14 | 1 | 6 | 6.3817 | 0 | 42.7453 | 15.5448 | 0 | 0 | 13.854 | 17.3638 | 0 | 0 | 0 | 4.8 | 100.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10587 | 0 | 10587 | 140762 | -270746 | -2 | -1 | 140762 | -1270746
1 | 14 | 2 | 6 | 6.3817 | 0 | 42.7453 | 17.1506 | 0 | 0 | 15.89 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.8 | 0 | 10590.8 | 138757 | -294688 | -4 | -3 | 138757 | -1294688
1 | 14 | 3 | 6 | 6.3817 | 0 | 42.7453 | 18.9529 | 0 | 0 | 19.0072 | 17.3638 | 0 | 0 | 0 | 4.8 | 109.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595 | 0 | 10595 | 136992 | -325646 | -7 | -6 | 136992 | -1325646
1 | 14 | 4 | 6 | 6.3817 | 0 | 42.7453 | 20.654 | 0 | 0 | 22.601 | 17.3638 | 0 | 0 | 0 | 4.8 | 114.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.5 | 0 | 10598.5 | 135369 | -348078 | -10 | -9 | 135369 | -1348078
1 | 14 | 5 | 6 | 6.3817 | 0 | 42.7453 | 22.7184 | 0 | 0 | 25.3038 | 17.3638 | 0 | 0 | 0 | 4.8 | 119.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10602 | 0 | 10602 | 133841 | -379347 | -12 | -11 | 133841 | -1379347
1 | 14 | 6 | 6 | 6.3817 | 0 | 42.7453 | 24.7238 | 0 | 0 | 25.2992 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10605.4 | 0 | 10605.4 | 132392 | -406857 | -15 | -14 | 132392 | -1406857
1 | 14 | 7 | 6 | 6.3817 | 0 | 42.7453 | 26.8413 | 0 | 0 | 25.2883 | 17.3638 | 0 | 0 | 0 | 3.2 | 121.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10608.9 | 0 | 10608.9 | 131082 | -432290 | -16 | -15 | 131082 | -1432290
1 | 14 | 8 | 6 | 6.2457 | 0 | 42.7453 | 104.72 | 0 | 0 | 25.2223 | 20.6384 | 0 | 0 | 0 | 0.8 | 200.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10612.3 | 0 | 10612.3 | 120854 | -1630510 | -17 | -16 | 120854 | -2630510
1 | 14 | 9 | 6 | 5.3354 | 0 | 42.7453 | 95.4124 | 0 | 0 | 25.2092 | 19.7503 | 0 | 0 | 0 | 0 | 188.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615.1 | 0 | 10615.1 | 120059 | -1444810 | -18 | -17 | 120059 | -2444810
1 | 14 | 10 | 6 | 5.7076 | 0 | 42.7453 | 82.6777 | 0 | 0 | 25.2075 | 19.1436 | 0 | 0 | 0 | 0 | 175.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.2 | 0 | 10595.2 | 119340 | -1271390 | -16 | -15 | 119340 | -2271390
1 | 14 | 11 | 6 | 5.5693 | 0 | 42.7453 | 77.1996 | 0 | 0 | 25.2087 | 18.9782 | 0 | 0 | 0 | 0 | 169.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10592.4 | 0 | 10592.4 | 118651 | -1192500 | -14 | -14 | 118651 | -2192500
1 | 14 | 12 | 6 | 5.5115 | 0 | 42.7453 | 72.5103 | 0 | 0 | 25.211 | 18.9292 | 0 | 0 | 0 | 0 | 164.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.8 | 0 | 10589.8 | 118026 | -1134200 | -13 | -12 | 118026 | -2134200
1 | 14 | 13 | 6 | 5.4803 | 0 | 42.7453 | 69.4782 | 0 | 0 | 25.2116 | 18.9057 | 0 | 0 | 0 | 0 | 161.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.8 | 0 | 10588.8 | 117419 | -1113470 | -13 | -12 | 117419 | -2113470
1 | 14 | 14 | 6 | 5.4918 | 0 | 42.7453 | 65.5811 | 0 | 0 | 25.2121 | 18.8896 | 0 | 0 | 0 | 0 | 157.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.1 | 0 | 10588.1 | 116834 | -1085000 | -12 | -11 | 116834 | -2085000
1 | 14 | 15 | 6 | 5.4984 | 0 | 42.7453 | 0 | 10.3766 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 0 | 81.8847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10587.6 | 0 | 10587.6 | 149367 | -42673.6 | -12 | -11 | 149367 | -1042673.6
1 | 14 | 16 | 6 | 5.6065 | 0 | 42.7453 | 0 | 9.872 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 81.4846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10587.7 | 0 | 10587.7 | 131941 | -184873 | -13 | -12 | 131941 | -1184873
1 | 14 | 17 | 6 | 7.9772 | 0 | 42.7453 | 13.572 | 0 | 0 | 5.9372 | 17.3638 | 0 | 0 | 0 | 2.4 | 89.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10597.3 | 0 | 10597.3 | 128069 | -236831 | -14 | -13 | 128069 | -1236831
1 | 14 | 18 | 6 | 8.7973 | 0 | 42.7453 | 20.144 | 0 | 0 | 21.0345 | 17.3638 | 0 | 0 | 0 | 6.4 | 116.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604 | 0 | 10604 | 128687 | -342331 | -15 | -14 | 128687 | -1342331
1 | 14 | 19 | 6 | 8.7973 | 0 | 42.7453 | 23.7844 | 0 | 0 | 25.3071 | 17.3638 | 0 | 0 | 0 | 7.2 | 125.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10609.5 | 0 | 10609.5 | 124399 | -381017 | -16 | -15 | 124399 | -1381017
1 | 14 | 20 | 6 | 8.7973 | 0 | 42.7453 | 26.3047 | 0 | 0 | 25.3015 | 17.3638 | 0 | 0 | 0 | 7.2 | 127.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10614.2 | 0 | 10614.2 | 125185 | -420987 | -17 | -16 | 125185 | -1420987
1 | 14 | 21 | 6 | 8.7973 | 0 | 42.7453 | 28.4948 | 0 | 0 | 25.2884 | 17.3638 | 0 | 0 | 0 | 7.2 | 129.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10618.2 | 0 | 10618.2 | 122293 | -444149 | -18 | -17 | 122293 | -1444149
1 | 14 | 22 | 6 | 8.7973 | 0 | 42.7453 | 30.5028 | 0 | 0 | 25.2776 | 17.3638 | 0 | 0 | 0 | 7.2 | 131.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10621.9 | 0 | 10621.9 | 122649 | -474786 | -18 | -18 | 122649 | -1474786
1 | 14 | 23 | 6 | 8.7973 | 0 | 42.7453 | 31.2723 | 0 | 0 | 25.2758 | 17.3638 | 0 | 0 | 0 | 6.4 | 131.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10624.8 | 0 | 10624.8 | 120878 | -487955 | -19 | -18 | 120878 | -1487955
1 | 14 | 24 | 6 | 8.7973 | 0 | 42.7453 | 32.8003 | 0 | 0 | 25.2715 | 17.3638 | 0 | 0 | 0 | 5.6 | 132.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10626.8 | 0 | 10626.8 | 121815 | -507654 | -20 | -19 | 121815 | -1507654
1 | 15 | 1 | 7 | 5.1054 | 0 | 42.7453 | 34.0299 | 0 | 0 | 25.2674 | 17.3638 | 0 | 0 | 0 | 4.8 | 129.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4002.63 | 0 | 4002.63 | 119465 | -532007 | -20 | -19 | 119465 | -1532007
1 | 15 | 2 | 7 | 5.1054 | 0 | 42.7453 | 34.9252 | 0 | 0 | 25.2661 | 17.3638 | 0 | 0 | 0 | 4.8 | 130.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4004.27 | 0 | 4004.27 | 119700 | -549038 | -20 | -20 | 119700 | -1549038
1 | 15 | 3 | 7 | 5.1054 | 0 | 42.7453 | 35.5508 | 0 | 0 | 25.2652 | 17.3638 | 0 | 0 | 0 | 4.8 | 130.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4005.94 | 0 | 4005.94 | 118309 | -557557 | -21 | -20 | 118309 | -1557557
1 | 15 | 4 | 7 | 5.1054 | 0 | 42.7453 | 36.6352 | 0 | 0 | 25.2644 | 17.3638 | 0 | 0 | 0 | 4.8 | 131.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007.46 | 0 | 4007.46 | 118783 | -571832 | -22 | -21 | 118783 | -1571832
1 | 15 | 5 | 7 | 5.1054 | 0 | 42.7453 | 37.3809 | 0 | 0 | 25.2637 | 17.3638 | 0 | 0 | 0 | 4.8 | 132.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.93 | 0 | 4008.93 | 117212 | -579484 | -23 | -22 | 117212 | -1579484
1 | 15 | 6 | 7 | 5.1054 | 0 | 42.7453 | 38.3991 | 0 | 0 | 25.2631 | 17.3638 | 0 | 0 | 0 | 4.8 | 133.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4010.33 | 0 | 4010.33 | 117098 | -593697 | -24 | -23 | 117098 | -1593697
1 | 15 | 7 | 7 | 5.1054 | 0 | 42.7453 | 39.0467 | 0 | 0 | 25.2627 | 17.3638 | 0 | 0 | 0 | 3.2 | 132.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.7 | 0 | 4011.7 | 116194 | -600593 | -23 | -23 | 116194 | -1600593
1 | 15 | 8 | 7 | 5.0117 | 0 | 42.7453 | 38.9384 | 0 | 0 | 25.264 | 17.3638 | 0 | 0 | 0 | 0.8 | 130.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4013.01 | 0 | 4013.01 | 116217 | -599173 | -23 | -22 | 116217 | -1599173
1 | 15 | 9 | 7 | 4.0598 | 0 | 42.7453 | 35.475 | 0 | 0 | 25.2728 | 17.3638 | 0 | 0 | 0 | 0 | 124.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.28 | 0 | 4014.28 | 115850 | -541696 | -23 | -22 | 115850 | -1541696
1 | 15 | 10 | 7 | 4.2789 | 0 | 42.7453 | 31.5307 | 0 | 0 | 25.282 | 17.3638 | 0 | 0 | 0 | 0 | 121.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.51 | 0 | 4015.51 | 116088 | -482086 | -21 | -20 | 116088 | -1482086
1 | 15 | 11 | 7 | 4.1929 | 0 | 42.7453 | 28.6545 | 0 | 0 | 25.2902 | 17.3638 | 0 | 0 | 0 | 0 | 118.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.65 | 0 | 4016.65 | 116773 | -442719 | -19 | -18 | 116773 | -1442719
1 | 15 | 12 | 7 | 4.164 | 0 | 42.7453 | 26.8214 | 0 | 0 | 25.2916 | 17.3638 | 0 | 0 | 0 | 0 | 116.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.6 | 0 | 4017.6 | 117131 | -414686 | -17 | -16 | 117131 | -1414686
1 | 15 | 13 | 7 | 4.1537 | 0 | 42.7453 | 24.8976 | 0 | 0 | 25.2918 | 17.3638 | 0 | 0 | 0 | 0 | 114.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.55 | 0 | 4018.55 | 116622 | -390201 | -16 | -15 | 116622 | -1390201
1 | 15 | 14 | 7 | 4.1559 | 0 | 42.7453 | 23.1681 | 0 | 0 | 25.2964 | 17.3638 | 0 | 0 | 0 | 0 | 112.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.4 | 0 | 4019.4 | 116689 | -373889 | -15 | -14 | 116689 | -1373889
1 | 15 | 15 | 7 | 4.1836 | 0 | 42.7453 | 22.2317 | 0 | 0 | 24.6547 | 17.3638 | 0 | 0 | 0 | 0 | 111.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.17 | 0 | 4020.17 | 117397 | -363817 | -14 | -13 | 117397 | -1363817
1 | 15 | 16 | 7 | 4.2963 | 0 | 42.7453 | 22.3502 | 0 | 0 | 24.7184 | 17.3638 | 0 | 0 | 0 | 0 | 111.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.92 | 0 | 4020.92 | 115984 | -360947 | -15 | -14 | 115984 | -1360947
1 | 15 | 17 | 7 | 5.7444 | 0 | 42.7453 | 24.9291 | 0 | 0 | 25.2841 | 17.3638 | 0 | 0 | 0 | 2.4 | 118.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.74 | 0 | 4021.74 | 115558 | -397740 | -16 | -15 | 115558 | -1397740
1 | 15 | 18 | 7 | 6.6633 | 0 | 42.7453 | 30.0583 | 0 | 0 | 25.2764 | 17.3638 | 0 | 0 | 0 | 6.4 | 128.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.7 | 0 | 4022.7 | 119287 | -480654 | -17 | -16 | 119287 | -1480654
1 | 15 | 19 | 7 | 6.6633 | 0 | 42.7453 | 31.9699 | 0 | 0 | 25.2709 | 17.3638 | 0 | 0 | 0 | 7.2 | 131.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023.63 | 0 | 4023.63 | 114545 | -498876 | -17 | -17 | 114545 | -1498876
1 | 15 | 20 | 7 | 6.6633 | 0 | 42.7453 | 34.2696 | 0 | 0 | 25.2687 | 17.3638 | 0 | 0 | 0 | 7.2 | 133.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4024.63 | 0 | 4024.63 | 118665 | -537333 | -18 | -17 | 118665 | -1537333
1 | 15 | 21 | 7 | 6.6633 | 0 | 42.7453 | 34.6748 | 0 | 0 | 25.2674 | 17.3638 | 0 | 0 | 0 | 7.2 | 133.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4025.62 | 0 | 4025.62 | 113744 | -536720 | -19 | -18 | 113744 | -1536720
1 | 15 | 22 | 7 | 6.6633 | 0 | 42.7453 | 36.0652 | 0 | 0 | 25.2665 | 17.3638 | 0 | 0 | 0 | 7.2 | 135.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.57 | 0 | 4026.57 | 116431 | -560423 | -19 | -18 | 116431 | -1560423
1 | 15 | 23 | 7 | 6.6633 | 0 | 42.7453 | 35.9572 | 0 | 0 | 25.2659 | 17.3638 | 0 | 0 | 0 | 6.4 | 134.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.47 | 0 | 4027.47 | 113175 | -556249 | -19 | -18 | 113175 | -1556249
1 | 15 | 24 | 7 | 6.6633 | 0 | 42.7453 | 36.9166 | 0 | 0 | 25.2654 | 17.3638 | 0 | 0 | 0 | 5.6 | 134.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.32 | 0 | 4028.32 | 115604 | -571898 | -19 | -18 | 115604 | -1571898
1 | 16 | 1 | 8 | 5.1054 | 0 | 42.7453 | 37.3002 | 0 | 0 | 25.2641 | 17.3638 | 0 | 0 | 0 | 4.8 | 132.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.15 | 0 | 4029.15 | 112728 | -577863 | -17 | -16 | 112728 | -1577863
1 | 16 | 2 | 8 | 5.1054 | 0 | 42.7453 | 37.1752 | 0 | 0 | 25.2637 | 17.3638 | 0 | 0 | 0 | 4.8 | 132.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.92 | 0 | 4029.92 | 114496 | -584081 | -15 | -14 | 114496 | -1584081
1 | 16 | 3 | 8 | 5.1054 | 0 | 42.7453 | 36.5928 | 0 | 0 | 25.2635 | 17.3638 | 0 | 0 | 0 | 4.8 | 131.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.66 | 0 | 4030.66 | 112562 | -576032 | -13 | -12 | 112562 | -1576032
1 | 16 | 4 | 8 | 5.1054 | 0 | 42.7453 | 36.0951 | 0 | 0 | 25.2634 | 17.3638 | 0 | 0 | 0 | 4.8 | 131.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.35 | 0 | 4031.35 | 114320 | -572931 | -10 | -9 | 114320 | -1572931
1 | 16 | 5 | 8 | 5.1054 | 0 | 42.7453 | 35.1394 | 0 | 0 | 25.2633 | 17.3638 | 0 | 0 | 0 | 4.8 | 130.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.01 | 0 | 4032.01 | 112679 | -559344 | -7 | -6 | 112679 | -1559344
1 | 16 | 6 | 8 | 5.1054 | 0 | 42.7453 | 34.1009 | 0 | 0 | 25.2636 | 17.3638 | 0 | 0 | 0 | 4.8 | 129.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.63 | 0 | 4032.63 | 114720 | -549231 | -4 | -3 | 114720 | -1549231
1 | 16 | 7 | 8 | 5.1054 | 0 | 42.7453 | 33.1852 | 0 | 0 | 25.2636 | 17.3638 | 0 | 0 | 0 | 3.2 | 126.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.21 | 0 | 4033.21 | 112949 | -535113 | -3 | -2 | 112949 | -1535113
1 | 16 | 8 | 8 | 5.0662 | 0 | 42.7453 | 32.0427 | 0 | 0 | 25.2641 | 17.3638 | 0 | 0 | 0 | 0.8 | 123.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.78 | 0 | 4033.78 | 113091 | -521929 | -2 | 0 | 113091 | -1521929
1 | 16 | 9 | 8 | 4.8432 | 0 | 42.7453 | 30.834 | 0 | 0 | 25.2661 | 17.3638 | 0 | 0 | 0 | 0 | 121.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034.31 | 0 | 4034.31 | 114324 | -502059 | 0 | 1 | 114324 | -1502059
1 | 16 | 10 | 8 | 5.08 | 0 | 42.7453 | 28.7478 | 0 | 0 | 25.2687 | 17.3638 | 0 | 0 | 0 | 0 | 119.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034.82 | 0 | 4034.82 | 113566 | -470973 | 2 | 3 | 113566 | -1470973
1 | 16 | 11 | 8 | 4.745 | 0 | 42.7453 | 26.7352 | 0 | 0 | 25.2721 | 17.3638 | 0 | 0 | 0 | 0 | 116.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.31 | 0 | 4035.31 | 115580 | -444672 | 4 | 6 | 115580 | -1444672
1 | 16 | 12 | 8 | 4.728 | 0 | 42.7453 | 25.2048 | 0 | 0 | 25.273 | 17.3638 | 0 | 0 | 0 | 0 | 115.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.75 | 0 | 4035.75 | 114263 | -422159 | 6 | 8 | 114263 | -1422159
1 | 16 | 13 | 8 | 4.1501 | 0 | 42.7453 | 22.1577 | 0 | 0 | 25.2773 | 17.3638 | 0 | 0 | 0 | 0 | 111.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.17 | 0 | 4036.17 | 114647 | -375708 | 9 | 11 | 114647 | -1375708
1 | 16 | 14 | 8 | 4.151 | 0 | 42.7453 | 20.3442 | 0 | 0 | 22.1728 | 17.3638 | 0 | 0 | 0 | 0 | 106.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.54 | 0 | 4036.54 | 117318 | -350797 | 11 | 14 | 117318 | -1350797
1 | 16 | 15 | 8 | 4.1523 | 0 | 42.7453 | 17.9722 | 0 | 0 | 16.995 | 17.3638 | 0 | 0 | 0 | 0 | 99.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.89 | 0 | 4036.89 | 115389 | -314809 | 14 | 17 | 115389 | -1314809
1 | 16 | 16 | 8 | 4.199 | 0 | 42.7453 | 17.8229 | 0 | 0 | 16.7617 | 17.3638 | 0 | 0 | 0 | 0 | 98.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.19 | 0 | 4037.19 | 118551 | -316755 | 14 | 17 | 118551 | -1316755
1 | 16 | 17 | 8 | 5.7193 | 0 | 42.7453 | 18.6144 | 0 | 0 | 18.9199 | 17.3638 | 0 | 0 | 0 | 2.4 | 105.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.52 | 0 | 4037.52 | 115794 | -328486 | 15 | 17 | 115794 | -1328486
1 | 16 | 18 | 8 | 6.6633 | 0 | 42.7453 | 19.8919 | 0 | 0 | 22.0272 | 17.3638 | 0 | 0 | 0 | 6.4 | 115.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.84 | 0 | 4037.84 | 117237 | -352020 | 15 | 17 | 117237 | -1352020
1 | 16 | 19 | 8 | 6.6633 | 0 | 42.7453 | 19.8129 | 0 | 0 | 22.0359 | 17.3638 | 0 | 0 | 0 | 7.2 | 115.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4038.2 | 0 | 4038.2 | 115922 | -349712 | 16 | 18 | 115922 | -1349712
1 | 16 | 20 | 8 | 6.6633 | 0 | 42.7453 | 19.8909 | 0 | 0 | 22.2114 | 17.3638 | 0 | 0 | 0 | 7.2 | 116.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4038.58 | 0 | 4038.58 | 117553 | -350693 | 17 | 19 | 117553 | -1350693
1 | 16 | 21 | 8 | 6.6633 | 0 | 42.7453 | 19.5607 | 0 | 0 | 21.3787 | 17.3638 | 0 | 0 | 0 | 7.2 | 114.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4038.96 | 0 | 4038.96 | 116187 | -342081 | 18 | 20 | 116187 | -1342081
1 | 16 | 22 | 8 | 6.6633 | 0 | 42.7453 | 19.1884 | 0 | 0 | 20.4582 | 17.3638 | 0 | 0 | 0 | 7.2 | 113.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.31 | 0 | 4039.31 | 117472 | -335691 | 20 | 22 | 117472 | -1335691
1 | 16 | 23 | 8 | 6.6633 | 0 | 42.7453 | 18.6299 | 0 | 0 | 19.1378 | 17.3638 | 0 | 0 | 0 | 6.4 | 110.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.64 | 0 | 4039.64 | 116674 | -323421 | 22 | 24 | 116674 | -1323421
1 | 16 | 24 | 8 | 6.6633 | 0 | 42.7453 | 18.0452 | 0 | 0 | 17.8726 | 17.3638 | 0 | 0 | 0 | 5.6 | 108.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.93 | 0 | 4039.93 | 116854 | -311571 | 23 | 26 | 116854 | -1311571
1 | 17 | 1 | 2 | 10.424 | 0 | 42.3304 | 18.0978 | 0 | 0 | 18.6023 | 17.3638 | 0 | 0 | 0 | 4.8 | 111.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10666.2 | 0 | 10666.2 | 117425 | -306022 | 24 | 26 | 117425 | -1306022
1 | 17 | 2 | 2 | 10.424 | 0 | 42.3304 | 17.3835 | 0 | 0 | 16.6877 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10666.5 | 0 | 10666.5 | 117727 | -296014 | 24 | 27 | 117727 | -1296014
1 | 17 | 3 | 2 | 10.424 | 0 | 42.3304 | 17.261 | 0 | 0 | 16.4472 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10666.2 | 0 | 10666.2 | 119263 | -294040 | 25 | 27 | 119263 | -1294040
1 | 17 | 4 | 2 | 10.424 | 0 | 42.3304 | 17.0701 | 0 | 0 | 16.0942 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10666.3 | 0 | 10666.3 | 118086 | -289384 | 24 | 26 | 118086 | -1289384
1 | 17 | 5 | 2 | 11.8202 | 0 | 44.8242 | 17.175 | 0 | 0 | 16.2893 | 17.5105 | 0 | 0 | 0 | 4.8 | 112.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11840.1 | 0 | 11840.1 | 121408 | -292702 | 24 | 25 | 121408 | -1292702
1 | 17 | 6 | 2 | 24.3093 | 0 | 69.9783 | 14.3778 | 0 | 0 | 12.0521 | 17.5105 | 0 | 0 | 0 | 4.8 | 143.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28689.7 | 0 | 28689.7 | 168712 | -248944 | 23 | 24 | 168712 | -1248944
1 | 17 | 7 | 2 | 49.0171 | 0 | 140.608 | 68.6208 | 0 | 0 | 25.2076 | 19.997 | 0 | 0 | 0 | 3.2 | 306.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84940.2 | 0 | 84940.2 | 306029 | -1145190 | 23 | 24 | 306029 | -2145190
1 | 17 | 8 | 2 | 52.1982 | 0 | 168.222 | 56.2041 | 0 | 0 | 25.2167 | 19.385 | 0 | 0 | 0 | 0.8 | 322.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103153 | 0 | 103153 | 368783 | -954507 | 23 | 25 | 368783 | -1954507
1 | 17 | 9 | 2 | 41.6993 | 0 | 173.795 | 45.2009 | 0 | 0 | 25.2284 | 19.1114 | 0 | 0 | 0 | 0 | 305.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142752 | 0 | 142752 | 388095 | -802734 | 23 | 25 | 388095 | -1802734
1 | 17 | 10 | 2 | 41.0248 | 0 | 172.186 | 37.7993 | 0 | 0 | 25.244 | 19.0363 | 0 | 0 | 0 | 0 | 295.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167971 | 0 | 167971 | 387054 | -665885 | 25 | 28 | 387054 | -1665885
1 | 17 | 11 | 2 | 41.2414 | 0 | 163.102 | 35.6518 | 0 | 0 | 25.2583 | 19.0363 | 0 | 0 | 0 | 0 | 284.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171566 | 0 | 171566 | 371311 | -609748 | 27 | 30 | 371311 | -1609748
1 | 17 | 12 | 2 | 40.895 | 0 | 149.692 | 29.2432 | 0 | 0 | 25.2785 | 19.0363 | 0 | 0 | 0 | 0 | 264.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171564 | 0 | 171564 | 353875 | -502547 | 29 | 33 | 353875 | -1502547
1 | 17 | 13 | 2 | 39.8613 | 0 | 150.207 | 26.3868 | 0 | 0 | 25.2798 | 19.0363 | 0 | 0 | 0 | 0 | 260.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171561 | 0 | 171561 | 344232 | -466576 | 30 | 34 | 344232 | -1466576
1 | 17 | 14 | 2 | 41.3329 | 0 | 165.698 | 0 | 24.7543 | 0 | 6.295 | 19.0363 | 0 | 0 | 0 | 0 | 257.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171558 | 0 | 171558 | 377952 | -386607 | 31 | 36 | 377952 | -1386607
1 | 17 | 15 | 2 | 40.9144 | 0 | 172.702 | 0 | 25.4116 | 0 | 6.3048 | 19.0363 | 0 | 0 | 0 | 0 | 264.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169339 | 0 | 169339 | 398852 | -358245 | 32 | 37 | 398852 | -1358245
1 | 17 | 16 | 2 | 41.3246 | 0 | 173.986 | 0 | 25.4085 | 0 | 6.305 | 19.0363 | 0 | 0 | 0 | 0 | 266.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153940 | 0 | 153940 | 399852 | -366743 | 32 | 36 | 399852 | -1366743
1 | 17 | 17 | 2 | 48.5815 | 0 | 169.782 | 0 | 25.4229 | 0 | 6.3 | 19.0363 | 0 | 0 | 0 | 2.4 | 271.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125648 | 0 | 125648 | 393090 | -402919 | 31 | 35 | 393090 | -1402919
1 | 17 | 18 | 2 | 49.7836 | 0 | 152.497 | 27.5001 | 0 | 0 | 25.2875 | 19.0363 | 0 | 0 | 0 | 6.4 | 280.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94214 | 0 | 94214 | 379776 | -480686 | 30 | 34 | 379776 | -1480686
1 | 17 | 19 | 2 | 34.11 | 0 | 93.4203 | 32.7012 | 0 | 0 | 25.2828 | 19.0363 | 0 | 0 | 0 | 7.2 | 211.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58313.6 | 0 | 58313.6 | 293896 | -539073 | 30 | 34 | 293896 | -1539073
1 | 17 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.2214 | 0 | 5.9454 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41708.1 | 0 | 41708.1 | 173740 | -15354.7 | 30 | 33 | 173740 | -1015354.7
1 | 17 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.5755 | 0 | 5.9157 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37013 | 0 | 37013 | 154801 | -22277.3 | 30 | 33 | 154801 | -1022277.3
1 | 17 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.0349 | 0 | 5.9232 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22700.7 | 0 | 22700.7 | 162295 | -40450.7 | 30 | 33 | 162295 | -1040450.7
1 | 17 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 11.9088 | 0 | 5.9078 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12197.9 | 0 | 12197.9 | 147189 | -66714.9 | 30 | 32 | 147189 | -1066714.9
1 | 17 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.4036 | 0 | 5.903 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10610.7 | 0 | 10610.7 | 140704 | -77949.2 | 30 | 32 | 140704 | -1077949.2
1 | 18 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.1575 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10614.1 | 0 | 10614.1 | 138246 | -88063.5 | 31 | 33 | 138246 | -1088063.5
1 | 18 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.0826 | 0 | 5.9008 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10616.8 | 0 | 10616.8 | 137327 | -99736.9 | 32 | 33 | 137327 | -1099736.9
1 | 18 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9915 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10619.1 | 0 | 10619.1 | 136086 | -105304 | 33 | 34 | 136086 | -1105304
1 | 18 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.0033 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10621 | 0 | 10621 | 136131 | -109452 | 34 | 36 | 136131 | -1109452
1 | 18 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.2265 | 0 | 5.9016 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11796.3 | 0 | 11796.3 | 138440 | -108190 | 36 | 37 | 138440 | -1108190
1 | 18 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.7424 | 0 | 5.9601 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28647.2 | 0 | 28647.2 | 186375 | -78188.3 | 38 | 39 | 186375 | -1078188.3
1 | 18 | 7 | 3 | 49.0171 | 0 | 140.608 | 36.6325 | 0 | 0 | 25.2466 | 19.0764 | 0 | 0 | 0 | 3.2 | 273.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84898.6 | 0 | 84898.6 | 318733 | -647464 | 38 | 39 | 318733 | -1647464
1 | 18 | 8 | 3 | 52.9766 | 0 | 168.222 | 32.1583 | 0 | 0 | 25.2593 | 19.0363 | 0 | 0 | 0 | 0.8 | 298.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103111 | 0 | 103111 | 417626 | -582320 | 38 | 40 | 417626 | -1582320
1 | 18 | 9 | 3 | 48.18 | 0 | 173.795 | 0 | 28.6705 | 0 | 6.2752 | 19.0363 | 0 | 0 | 0 | 0 | 275.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142727 | 0 | 142727 | 433692 | -462595 | 39 | 40 | 433692 | -1462595
1 | 18 | 10 | 3 | 42.3723 | 0 | 172.186 | 0 | 28.494 | 0 | 6.2844 | 19.0363 | 0 | 0 | 0 | 0 | 268.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167944 | 0 | 167944 | 430382 | -431426 | 39 | 40 | 430382 | -1431426
1 | 18 | 11 | 3 | 42.1064 | 0 | 163.102 | 0 | 27.512 | 0 | 6.291 | 19.0363 | 0 | 0 | 0 | 0 | 258.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171539 | 0 | 171539 | 416694 | -404300 | 39 | 41 | 416694 | -1404300
1 | 18 | 12 | 3 | 41.417 | 0 | 149.692 | 0 | 27.0614 | 0 | 6.2909 | 19.0363 | 0 | 0 | 0 | 0 | 243.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171536 | 0 | 171536 | 405930 | -382729 | 39 | 41 | 405930 | -1382729
1 | 18 | 13 | 3 | 39.8259 | 0 | 150.207 | 0 | 24.9727 | 0 | 6.2985 | 19.0363 | 0 | 0 | 0 | 0 | 240.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171533 | 0 | 171533 | 378789 | -346061 | 38 | 41 | 378789 | -1346061
1 | 18 | 14 | 3 | 41.314 | 0 | 165.698 | 0 | 27.6711 | 0 | 6.3202 | 19.0363 | 0 | 0 | 0 | 0 | 260.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171530 | 0 | 171530 | 417712 | -303102 | 38 | 41 | 417712 | -1303102
1 | 18 | 15 | 3 | 40.7169 | 0 | 172.702 | 0 | 29.3583 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169311 | 0 | 169311 | 439988 | -290440 | 37 | 41 | 439988 | -1290440
1 | 18 | 16 | 3 | 41.3123 | 0 | 173.986 | 0 | 26.6647 | 0 | 6.3281 | 19.0363 | 0 | 0 | 0 | 0 | 267.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153912 | 0 | 153912 | 414840 | -302116 | 33 | 37 | 414840 | -1302116
1 | 18 | 17 | 3 | 47.9161 | 0 | 169.782 | 0 | 25.6212 | 0 | 6.3007 | 19.0363 | 0 | 0 | 0 | 2.4 | 271.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125619 | 0 | 125619 | 403244 | -393105 | 30 | 32 | 403244 | -1393105
1 | 18 | 18 | 3 | 49.7836 | 0 | 152.497 | 29.3338 | 0 | 0 | 25.2756 | 19.0363 | 0 | 0 | 0 | 6.4 | 282.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94186.2 | 0 | 94186.2 | 393742 | -520353 | 26 | 28 | 393742 | -1520353
1 | 18 | 19 | 3 | 34.11 | 0 | 93.4203 | 38.0403 | 0 | 0 | 25.2765 | 19.0363 | 0 | 0 | 0 | 7.2 | 217.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58287.3 | 0 | 58287.3 | 313370 | -614854 | 22 | 24 | 313370 | -1614854
1 | 18 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.4254 | 0 | 5.9523 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41683 | 0 | 41683 | 179282 | -16292.8 | 18 | 19 | 179282 | -1016292.8
1 | 18 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.3946 | 0 | 5.9548 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36988.9 | 0 | 36988.9 | 185584 | -42187.4 | 13 | 15 | 185584 | -1042187.4
1 | 18 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.7619 | 0 | 5.9227 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22676.3 | 0 | 22676.3 | 166198 | -80348.3 | 11 | 13 | 166198 | -1080348.3
1 | 18 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.5755 | 0 | 5.9071 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12175.1 | 0 | 12175.1 | 151552 | -128823 | 9 | 10 | 151552 | -1128823
1 | 18 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 10.9744 | 0 | 5.9021 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.9 | 0 | 10588.9 | 145040 | -167396 | 7 | 8 | 145040 | -1167396
1 | 19 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.6806 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.7 | 0 | 10593.7 | 142479 | -198826 | 6 | 7 | 142479 | -1198826
1 | 19 | 2 | 4 | 10.73 | 0 | 42.3304 | 12.3083 | 0 | 0 | 9.8247 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10597.5 | 0 | 10597.5 | 140698 | -221762 | 5 | 6 | 140698 | -1221762
1 | 19 | 3 | 4 | 10.73 | 0 | 42.3304 | 13.4398 | 0 | 0 | 11.0603 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.7243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10601 | 0 | 10601 | 139145 | -239268 | 4 | 5 | 139145 | -1239268
1 | 19 | 4 | 4 | 10.73 | 0 | 42.3304 | 14.2434 | 0 | 0 | 12.0865 | 17.3638 | 0 | 0 | 0 | 4.8 | 101.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604.1 | 0 | 10604.1 | 137784 | -253858 | 3 | 5 | 137784 | -1253858
1 | 19 | 5 | 4 | 11.8202 | 0 | 44.8242 | 15.6247 | 0 | 0 | 13.8963 | 17.5105 | 0 | 0 | 0 | 4.8 | 108.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11780.8 | 0 | 11780.8 | 139325 | -269660 | 3 | 4 | 139325 | -1269660
1 | 19 | 6 | 4 | 24.3093 | 0 | 69.9783 | 14.7511 | 0 | 0 | 12.4797 | 17.5105 | 0 | 0 | 0 | 4.8 | 143.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28633 | 0 | 28633 | 185485 | -251427 | 2 | 4 | 185485 | -1251427
1 | 19 | 7 | 4 | 49.0171 | 0 | 140.608 | 70.071 | 0 | 0 | 25.215 | 19.4655 | 0 | 0 | 0 | 3.2 | 307.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84885.8 | 0 | 84885.8 | 318209 | -1238320 | 3 | 5 | 318209 | -2238320
1 | 19 | 8 | 4 | 52.9253 | 0 | 168.222 | 62.8068 | 0 | 0 | 25.2085 | 19.2396 | 0 | 0 | 0 | 0.8 | 329.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103100 | 0 | 103100 | 380231 | -1146470 | 4 | 5 | 380231 | -2146470
1 | 19 | 9 | 4 | 47.7249 | 0 | 173.795 | 53.6338 | 0 | 0 | 25.2088 | 19.0832 | 0 | 0 | 0 | 0 | 319.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142715 | 0 | 142715 | 399609 | -993600 | 5 | 6 | 399609 | -1993600
1 | 19 | 10 | 4 | 45.1788 | 0 | 172.186 | 53.7646 | 0 | 0 | 25.2112 | 19.0427 | 0 | 0 | 0 | 0 | 315.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167936 | 0 | 167936 | 397240 | -976875 | 6 | 7 | 397240 | -1976875
1 | 19 | 11 | 4 | 42.0151 | 0 | 163.102 | 55.5283 | 0 | 0 | 25.2127 | 19.0363 | 0 | 0 | 0 | 0 | 304.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171532 | 0 | 171532 | 380845 | -980391 | 6 | 7 | 380845 | -1980391
1 | 19 | 12 | 4 | 41.6597 | 0 | 149.692 | 53.6933 | 0 | 0 | 25.2211 | 19.0363 | 0 | 0 | 0 | 0 | 289.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171532 | 0 | 171532 | 362148 | -912389 | 7 | 8 | 362148 | -1912389
1 | 19 | 13 | 4 | 39.9888 | 0 | 150.207 | 52.0801 | 0 | 0 | 25.2197 | 19.0363 | 0 | 0 | 0 | 0 | 286.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171530 | 0 | 171530 | 351667 | -914462 | 7 | 8 | 351667 | -1914462
1 | 19 | 14 | 4 | 42.6085 | 0 | 165.698 | 43.7034 | 0 | 0 | 25.2176 | 19.0363 | 0 | 0 | 0 | 0 | 296.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171527 | 0 | 171527 | 384497 | -846324 | 7 | 9 | 384497 | -1846324
1 | 19 | 15 | 4 | 41.9451 | 0 | 172.702 | 42.1426 | 0 | 0 | 18.0495 | 19.0363 | 0 | 0 | 0 | 0 | 293.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169309 | 0 | 169309 | 403425 | -832938 | 8 | 9 | 403425 | -1832938
1 | 19 | 16 | 4 | 44.5501 | 0 | 173.986 | 41.8813 | 0 | 0 | 9.6314 | 19.0363 | 0 | 0 | 0 | 0 | 289.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153913 | 0 | 153913 | 406483 | -822938 | 8 | 10 | 406483 | -1822938
1 | 19 | 17 | 4 | 53.6688 | 0 | 169.782 | 44.7088 | 0 | 0 | 25.2231 | 19.0363 | 0 | 0 | 0 | 2.4 | 314.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125623 | 0 | 125623 | 396698 | -851993 | 9 | 10 | 396698 | -1851993
1 | 19 | 18 | 4 | 49.7836 | 0 | 152.497 | 50.5164 | 0 | 0 | 25.2243 | 19.0363 | 0 | 0 | 0 | 6.4 | 303.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94190.9 | 0 | 94190.9 | 373303 | -888548 | 9 | 11 | 373303 | -1888548
1 | 19 | 19 | 4 | 34.11 | 0 | 93.4203 | 55.6597 | 0 | 0 | 25.232 | 19.0363 | 0 | 0 | 0 | 7.2 | 234.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58291.8 | 0 | 58291.8 | 304132 | -890802 | 10 | 11 | 304132 | -1890802
1 | 19 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 15.9601 | 0 | 6.0078 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41686.1 | 0 | 41686.1 | 212090 | -19526.1 | 10 | 12 | 212090 | -1019526.1
1 | 19 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.3164 | 0 | 5.9362 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36990.3 | 0 | 36990.3 | 178660 | -85928.9 | 10 | 12 | 178660 | -1085928.9
1 | 19 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 12.1203 | 0 | 5.9152 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22679.2 | 0 | 22679.2 | 162309 | -135699 | 11 | 12 | 162309 | -1135699
1 | 19 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.1451 | 0 | 5.904 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12178.4 | 0 | 12178.4 | 148967 | -170235 | 11 | 13 | 148967 | -1170235
1 | 19 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 10.7988 | 0 | 5.901 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.6682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10591.8 | 0 | 10591.8 | 143291 | -190835 | 11 | 13 | 143291 | -1190835
1 | 20 | 1 | 5 | 10.8489 | 0 | 42.3304 | 11.5524 | 0 | 0 | 9.2276 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10596.1 | 0 | 10596.1 | 141248 | -203058 | 12 | 13 | 141248 | -1203058
1 | 20 | 2 | 5 | 10.8489 | 0 | 42.3304 | 12.0795 | 0 | 0 | 9.5567 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.9793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599.4 | 0 | 10599.4 | 141251 | -211453 | 12 | 13 | 141251 | -1211453
1 | 20 | 3 | 5 | 10.8489 | 0 | 42.3304 | 12.3724 | 0 | 0 | 9.7592 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.4748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10602.3 | 0 | 10602.3 | 138632 | -212846 | 12 | 13 | 138632 | -1212846
1 | 20 | 4 | 5 | 10.8489 | 0 | 42.3304 | 13.0556 | 0 | 0 | 10.3961 | 17.3638 | 0 | 0 | 0 | 4.8 | 98.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604.9 | 0 | 10604.9 | 143597 | -221532 | 13 | 13 | 143597 | -1221532
1 | 20 | 5 | 5 | 11.8202 | 0 | 44.8242 | 12.4285 | 0 | 0 | 9.7183 | 17.5105 | 0 | 0 | 0 | 4.8 | 101.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11780.9 | 0 | 11780.9 | 139593 | -211425 | 13 | 14 | 139593 | -1211425
1 | 20 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.0729 | 0 | 5.9519 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28632.4 | 0 | 28632.4 | 192003 | -209826 | 13 | 14 | 192003 | -1209826
1 | 20 | 7 | 5 | 49.0171 | 0 | 140.608 | 63.3993 | 0 | 0 | 25.2073 | 19.3967 | 0 | 0 | 0 | 3.2 | 300.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84884.1 | 0 | 84884.1 | 318709 | -1100570 | 13 | 14 | 318709 | -2100570
1 | 20 | 8 | 5 | 52.7938 | 0 | 168.222 | 55.2617 | 0 | 0 | 25.2104 | 19.187 | 0 | 0 | 0 | 0.8 | 321.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103098 | 0 | 103098 | 380807 | -985180 | 14 | 15 | 380807 | -1985180
1 | 20 | 9 | 5 | 46.7618 | 0 | 173.795 | 47.3994 | 0 | 0 | 25.2197 | 19.0627 | 0 | 0 | 0 | 0 | 312.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142713 | 0 | 142713 | 399919 | -859136 | 14 | 15 | 399919 | -1859136
1 | 20 | 10 | 5 | 41.8733 | 0 | 172.186 | 46.093 | 0 | 0 | 25.2253 | 19.0363 | 0 | 0 | 0 | 0 | 304.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167932 | 0 | 167932 | 397773 | -826250 | 14 | 16 | 397773 | -1826250
1 | 20 | 11 | 5 | 41.3977 | 0 | 163.102 | 47.8061 | 0 | 0 | 25.2279 | 19.0363 | 0 | 0 | 0 | 0 | 296.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171529 | 0 | 171529 | 382806 | -833211 | 15 | 16 | 382806 | -1833211
1 | 20 | 12 | 5 | 40.7789 | 0 | 149.692 | 43.9902 | 0 | 0 | 25.2422 | 19.0363 | 0 | 0 | 0 | 0 | 278.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171528 | 0 | 171528 | 361550 | -742751 | 15 | 17 | 361550 | -1742751
1 | 20 | 13 | 5 | 39.8358 | 0 | 150.207 | 40.9929 | 0 | 0 | 25.2424 | 19.0363 | 0 | 0 | 0 | 0 | 275.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171526 | 0 | 171526 | 352559 | -712239 | 15 | 17 | 352559 | -1712239
1 | 20 | 14 | 5 | 41.3175 | 0 | 165.698 | 32.3866 | 0 | 0 | 25.2451 | 19.0363 | 0 | 0 | 0 | 0 | 283.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171523 | 0 | 171523 | 385389 | -622579 | 15 | 17 | 385389 | -1622579
1 | 20 | 15 | 5 | 40.7417 | 0 | 172.702 | 30.883 | 0 | 0 | 25.2522 | 19.0363 | 0 | 0 | 0 | 0 | 288.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169306 | 0 | 169306 | 404119 | -612893 | 14 | 17 | 404119 | -1612893
1 | 20 | 16 | 5 | 40.7181 | 0 | 173.986 | 35.2165 | 0 | 0 | 25.2428 | 19.0363 | 0 | 0 | 0 | 0 | 294.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153909 | 0 | 153909 | 407061 | -685170 | 12 | 14 | 407061 | -1685170
1 | 20 | 17 | 5 | 49.0199 | 0 | 169.782 | 40.8535 | 0 | 0 | 25.2301 | 19.0363 | 0 | 0 | 0 | 2.4 | 306.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125619 | 0 | 125619 | 397133 | -783479 | 10 | 12 | 397133 | -1783479
1 | 20 | 18 | 5 | 49.7836 | 0 | 152.497 | 50.2438 | 0 | 0 | 25.2231 | 19.0363 | 0 | 0 | 0 | 6.4 | 303.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94187.9 | 0 | 94187.9 | 385954 | -896444 | 7 | 9 | 385954 | -1896444
1 | 20 | 19 | 5 | 34.11 | 0 | 93.4203 | 56.3802 | 0 | 0 | 25.2292 | 19.0363 | 0 | 0 | 0 | 7.2 | 235.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58289.1 | 0 | 58289.1 | 307956 | -914777 | 7 | 8 | 307956 | -1914777
1 | 20 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 15.7929 | 0 | 6.0047 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41684.1 | 0 | 41684.1 | 212170 | -19591.3 | 6 | 7 | 212170 | -1019591.3
1 | 20 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.4676 | 0 | 5.9398 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36988.2 | 0 | 36988.2 | 181347 | -92053.4 | 5 | 6 | 181347 | -1092053.4
1 | 20 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.3662 | 0 | 5.9173 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22677 | 0 | 22677 | 162447 | -139962 | 5 | 6 | 162447 | -1139962
1 | 20 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.6106 | 0 | 5.9065 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12176.3 | 0 | 12176.3 | 148932 | -163953 | 4 | 5 | 148932 | -1163953
1 | 20 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.4677 | 0 | 5.9047 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.6 | 0 | 10589.6 | 145865 | -191219 | 4 | 5 | 145865 | -1191219
1 | 21 | 1 | 6 | 6.3817 | 0 | 42.7453 | 11.9713 | 0 | 0 | 9.264 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.2 | 0 | 10593.2 | 140700 | -201575 | 3 | 5 | 140700 | -1201575
1 | 21 | 2 | 6 | 6.3817 | 0 | 42.7453 | 12.9041 | 0 | 0 | 9.9841 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.9 | 0 | 10595.9 | 140631 | -218833 | 3 | 4 | 140631 | -1218833
1 | 21 | 3 | 6 | 6.3817 | 0 | 42.7453 | 13.3371 | 0 | 0 | 10.3651 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.9 | 0 | 10598.9 | 137582 | -224052 | 3 | 4 | 137582 | -1224052
1 | 21 | 4 | 6 | 6.3817 | 0 | 42.7453 | 13.86 | 0 | 0 | 10.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10601.2 | 0 | 10601.2 | 137591 | -233628 | 3 | 4 | 137591 | -1233628
1 | 21 | 5 | 6 | 6.3817 | 0 | 42.7453 | 14.2077 | 0 | 0 | 11.2801 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10603.3 | 0 | 10603.3 | 135320 | -237126 | 3 | 4 | 135320 | -1237126
1 | 21 | 6 | 6 | 6.3817 | 0 | 42.7453 | 14.6322 | 0 | 0 | 11.8131 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.7361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10605.2 | 0 | 10605.2 | 135238 | -244476 | 3 | 4 | 135238 | -1244476
1 | 21 | 7 | 6 | 6.3817 | 0 | 42.7453 | 14.7355 | 0 | 0 | 11.9559 | 17.3638 | 0 | 0 | 0 | 3.2 | 96.3821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10607 | 0 | 10607 | 133533 | -244118 | 5 | 6 | 133533 | -1244118
1 | 21 | 8 | 6 | 6.3056 | 0 | 42.7453 | 76.9943 | 0 | 0 | 25.2097 | 19.9106 | 0 | 0 | 0 | 0.8 | 171.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10608.6 | 0 | 10608.6 | 121919 | -1200120 | 6 | 7 | 121919 | -2200120
1 | 21 | 9 | 6 | 6.7736 | 0 | 42.7453 | 72.1958 | 0 | 0 | 25.2175 | 19.4657 | 0 | 0 | 0 | 0 | 166.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10609.9 | 0 | 10609.9 | 121213 | -1086430 | 8 | 9 | 121213 | -2086430
1 | 21 | 10 | 6 | 6.4659 | 0 | 42.7453 | 60.2519 | 0 | 0 | 25.225 | 19.1027 | 0 | 0 | 0 | 0 | 153.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.2 | 0 | 10595.2 | 120792 | -936411 | 11 | 13 | 120792 | -1936411
1 | 21 | 11 | 6 | 6.3175 | 0 | 42.7453 | 55.3565 | 0 | 0 | 25.2271 | 19.0183 | 0 | 0 | 0 | 0 | 148.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10592.8 | 0 | 10592.8 | 120350 | -877387 | 15 | 16 | 120350 | -1877387
1 | 21 | 12 | 6 | 5.9694 | 0 | 42.7453 | 49.2302 | 0 | 0 | 25.2316 | 18.9437 | 0 | 0 | 0 | 0 | 142.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10590.8 | 0 | 10590.8 | 119952 | -802400 | 19 | 20 | 119952 | -1802400
1 | 21 | 13 | 6 | 6.1208 | 0 | 42.7453 | 44.6632 | 0 | 0 | 8.8182 | 18.9113 | 0 | 0 | 0 | 0 | 121.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.8 | 0 | 10589.8 | 119558 | -763264 | 20 | 22 | 119558 | -1763264
1 | 21 | 14 | 6 | 6.1934 | 0 | 42.7453 | 42.2354 | 0 | 0 | 6.2314 | 18.8896 | 0 | 0 | 0 | 0 | 116.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10589.1 | 0 | 10589.1 | 119194 | -731013 | 22 | 23 | 119194 | -1731013
1 | 21 | 15 | 6 | 6.4208 | 0 | 42.7453 | 0 | 9.6248 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 77.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.5 | 0 | 10588.5 | 118887 | -19265.2 | 23 | 25 | 118887 | -1019265.2
1 | 21 | 16 | 6 | 6.9891 | 0 | 42.7453 | 0 | 10.8727 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 0 | 83.8709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10588.3 | 0 | 10588.3 | 137948 | -64420.2 | 23 | 25 | 137948 | -1064420.2
1 | 21 | 17 | 6 | 8.2567 | 0 | 42.7453 | 0 | 10.5632 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 2.4 | 87.2275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10593.5 | 0 | 10593.5 | 133814 | -98834.9 | 24 | 24 | 133814 | -1098834.9
1 | 21 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3584 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.9 | 0 | 10598.9 | 131647 | -134910 | 23 | 24 | 131647 | -1134910
1 | 21 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2636 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10602.4 | 0 | 10602.4 | 130717 | -151353 | 24 | 25 | 130717 | -1151353
1 | 21 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2388 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10605.7 | 0 | 10605.7 | 130384 | -160695 | 25 | 25 | 130384 | -1160695
1 | 21 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.171 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.1746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10608.3 | 0 | 10608.3 | 129429 | -163511 | 26 | 26 | 129429 | -1163511
1 | 21 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2094 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10610.6 | 0 | 10610.6 | 129854 | -166189 | 27 | 27 | 129854 | -1166189
1 | 21 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.1541 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10612.7 | 0 | 10612.7 | 128640 | -166658 | 27 | 27 | 128640 | -1166658
1 | 21 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.1534 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10614.7 | 0 | 10614.7 | 128425 | -166490 | 28 | 28 | 128425 | -1166490
1 | 22 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1435 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3990.56 | 0 | 3990.56 | 128113 | -167818 | 29 | 29 | 128113 | -1167818
1 | 22 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1704 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.28 | 0 | 3992.28 | 128046 | -169716 | 30 | 31 | 128046 | -1169716
1 | 22 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1706 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3994.11 | 0 | 3994.11 | 127332 | -167115 | 31 | 32 | 127332 | -1167115
1 | 22 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.2033 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3995.72 | 0 | 3995.72 | 127148 | -167487 | 31 | 32 | 127148 | -1167487
1 | 22 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.198 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3997.26 | 0 | 3997.26 | 126841 | -170659 | 31 | 31 | 126841 | -1170659
1 | 22 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.166 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.68 | 0 | 3998.68 | 126602 | -175379 | 31 | 31 | 126602 | -1175379
1 | 22 | 7 | 7 | 5.1054 | 0 | 42.7453 | 10.5463 | 0 | 0 | 8.1052 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000.05 | 0 | 4000.05 | 126332 | -179448 | 30 | 31 | 126332 | -1179448
1 | 22 | 8 | 7 | 5.0581 | 0 | 42.7453 | 10.7323 | 0 | 0 | 8.2865 | 17.3638 | 0 | 0 | 0 | 0.8 | 84.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4001.43 | 0 | 4001.43 | 126125 | -181043 | 30 | 31 | 126125 | -1181043
1 | 22 | 9 | 7 | 4.7443 | 0 | 42.7453 | 10.6116 | 0 | 0 | 8.3477 | 17.3638 | 0 | 0 | 0 | 0 | 83.8126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4002.82 | 0 | 4002.82 | 125987 | -174950 | 29 | 31 | 125987 | -1174950
1 | 22 | 10 | 7 | 4.966 | 0 | 42.7453 | 0 | 10.0882 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 81.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4004.18 | 0 | 4004.18 | 125751 | -168412 | 27 | 29 | 125751 | -1168412
1 | 22 | 11 | 7 | 4.6723 | 0 | 42.7453 | 0 | 10.0397 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 80.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4005.55 | 0 | 4005.55 | 125491 | -162040 | 25 | 26 | 125491 | -1162040
1 | 22 | 12 | 7 | 4.6201 | 0 | 42.7453 | 0 | 9.9507 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.88 | 0 | 4006.88 | 125254 | -166959 | 22 | 24 | 125254 | -1166959
1 | 22 | 13 | 7 | 4.1497 | 0 | 42.7453 | 0 | 9.8667 | 0 | 5.8941 | 17.3638 | 0 | 0 | 0 | 0 | 80.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.19 | 0 | 4008.19 | 125089 | -156083 | 22 | 24 | 125089 | -1156083
1 | 22 | 14 | 7 | 4.1503 | 0 | 42.7453 | 0 | 9.8145 | 0 | 5.8965 | 17.3638 | 0 | 0 | 0 | 0 | 79.9704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4009.54 | 0 | 4009.54 | 124834 | -153713 | 21 | 23 | 124834 | -1153713
1 | 22 | 15 | 7 | 4.1509 | 0 | 42.7453 | 0 | 9.7754 | 0 | 5.8888 | 17.3638 | 0 | 0 | 0 | 0 | 79.9241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.02 | 0 | 4011.02 | 124653 | -160639 | 20 | 23 | 124653 | -1160639
1 | 22 | 16 | 7 | 4.181 | 0 | 42.7453 | 10.3855 | 0 | 0 | 8.2725 | 17.3638 | 0 | 0 | 0 | 0 | 82.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4012.48 | 0 | 4012.48 | 124466 | -178481 | 18 | 20 | 124466 | -1178481
1 | 22 | 17 | 7 | 5.5501 | 0 | 42.7453 | 12.1706 | 0 | 0 | 9.8178 | 17.3638 | 0 | 0 | 0 | 2.4 | 90.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4013.9 | 0 | 4013.9 | 123960 | -211043 | 16 | 18 | 123960 | -1211043
1 | 22 | 18 | 7 | 6.6633 | 0 | 42.7453 | 14.7623 | 0 | 0 | 13.0374 | 17.3638 | 0 | 0 | 0 | 6.4 | 100.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.42 | 0 | 4015.42 | 123470 | -252907 | 13 | 15 | 123470 | -1252907
1 | 22 | 19 | 7 | 6.6633 | 0 | 42.7453 | 16.0708 | 0 | 0 | 15.2247 | 17.3638 | 0 | 0 | 0 | 7.2 | 105.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.64 | 0 | 4016.64 | 123022 | -275416 | 11 | 13 | 123022 | -1275416
1 | 22 | 20 | 7 | 6.6633 | 0 | 42.7453 | 17.4233 | 0 | 0 | 17.9275 | 17.3638 | 0 | 0 | 0 | 7.2 | 109.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.79 | 0 | 4017.79 | 122517 | -301889 | 9 | 10 | 122517 | -1301889
1 | 22 | 21 | 7 | 6.6633 | 0 | 42.7453 | 18.3183 | 0 | 0 | 20.0881 | 17.3638 | 0 | 0 | 0 | 7.2 | 112.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.92 | 0 | 4018.92 | 122056 | -317434 | 7 | 8 | 122056 | -1317434
1 | 22 | 22 | 7 | 6.6633 | 0 | 42.7453 | 19.552 | 0 | 0 | 23.099 | 17.3638 | 0 | 0 | 0 | 7.2 | 116.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020 | 0 | 4020 | 121684 | -336184 | 6 | 7 | 121684 | -1336184
1 | 22 | 23 | 7 | 6.6633 | 0 | 42.7453 | 20.274 | 0 | 0 | 24.8842 | 17.3638 | 0 | 0 | 0 | 6.4 | 118.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.03 | 0 | 4021.03 | 121312 | -345248 | 5 | 6 | 121312 | -1345248
1 | 22 | 24 | 7 | 6.6633 | 0 | 42.7453 | 21.1794 | 0 | 0 | 25.2736 | 17.3638 | 0 | 0 | 0 | 5.6 | 118.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.02 | 0 | 4022.02 | 120931 | -359044 | 4 | 5 | 120931 | -1359044
1 | 23 | 1 | 1 | 10.8489 | 0 | 42.3304 | 21.23 | 0 | 0 | 25.2718 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649 | 0 | 10649 | 120959 | -366907 | 4 | 5 | 120959 | -1366907
1 | 23 | 2 | 1 | 10.8489 | 0 | 42.3304 | 21.8406 | 0 | 0 | 25.2716 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649.9 | 0 | 10649.9 | 121494 | -377469 | 3 | 4 | 121494 | -1377469
1 | 23 | 3 | 1 | 10.8489 | 0 | 42.3304 | 22.1282 | 0 | 0 | 25.2711 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10650.2 | 0 | 10650.2 | 120533 | -379784 | 3 | 4 | 120533 | -1379784
1 | 23 | 4 | 1 | 10.8489 | 0 | 42.3304 | 22.4708 | 0 | 0 | 25.2706 | 17.3638 | 0 | 0 | 0 | 4.8 | 123.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10650.9 | 0 | 10650.9 | 121310 | -387497 | 3 | 4 | 121310 | -1387497
1 | 23 | 5 | 1 | 11.8202 | 0 | 44.8242 | 23.1403 | 0 | 0 | 25.2722 | 17.5105 | 0 | 0 | 0 | 4.8 | 127.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11825.3 | 0 | 11825.3 | 122998 | -390854 | 3 | 4 | 122998 | -1390854
1 | 23 | 6 | 1 | 24.3093 | 0 | 69.9783 | 20.8746 | 0 | 0 | 23.1844 | 17.5105 | 0 | 0 | 0 | 4.8 | 160.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28675.4 | 0 | 28675.4 | 169552 | -352739 | 3 | 4 | 169552 | -1352739
1 | 23 | 7 | 1 | 49.0171 | 0 | 140.608 | 80.7747 | 0 | 0 | 25.2284 | 20.1156 | 0 | 0 | 0 | 3.2 | 318.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84926.4 | 0 | 84926.4 | 306575 | -1406290 | 3 | 5 | 306575 | -2406290
1 | 23 | 8 | 1 | 52.9222 | 0 | 168.222 | 69.9418 | 0 | 0 | 25.2138 | 19.5689 | 0 | 0 | 0 | 0.8 | 336.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103140 | 0 | 103140 | 369176 | -1261640 | 4 | 5 | 369176 | -2261640
1 | 23 | 9 | 1 | 47.3406 | 0 | 173.795 | 57.3734 | 0 | 0 | 25.2073 | 19.2181 | 0 | 0 | 0 | 0 | 322.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142742 | 0 | 142742 | 389027 | -1072530 | 4 | 6 | 389027 | -2072530
1 | 23 | 10 | 1 | 40.865 | 0 | 172.186 | 54.3226 | 0 | 0 | 25.2088 | 19.0809 | 0 | 0 | 0 | 0 | 311.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167963 | 0 | 167963 | 387324 | -1009470 | 5 | 7 | 387324 | -2009470
1 | 23 | 11 | 1 | 41.2342 | 0 | 163.102 | 53.1966 | 0 | 0 | 25.2114 | 19.0363 | 0 | 0 | 0 | 0 | 301.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171558 | 0 | 171558 | 369009 | -967726 | 6 | 8 | 369009 | -1967726
1 | 23 | 12 | 1 | 40.7862 | 0 | 149.692 | 48.2736 | 0 | 0 | 25.2212 | 19.0363 | 0 | 0 | 0 | 0 | 283.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171557 | 0 | 171557 | 342511 | -851987 | 7 | 9 | 342511 | -1851987
1 | 23 | 13 | 1 | 39.8399 | 0 | 150.207 | 46.0045 | 0 | 0 | 25.2219 | 19.0363 | 0 | 0 | 0 | 0 | 280.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171554 | 0 | 171554 | 343410 | -820144 | 8 | 11 | 343410 | -1820144
1 | 23 | 14 | 1 | 41.3482 | 0 | 165.698 | 37.739 | 0 | 0 | 25.2263 | 19.0363 | 0 | 0 | 0 | 0 | 289.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171551 | 0 | 171551 | 376732 | -727433 | 10 | 12 | 376732 | -1727433
1 | 23 | 15 | 1 | 40.8633 | 0 | 172.702 | 36.3608 | 0 | 0 | 25.238 | 19.0363 | 0 | 0 | 0 | 0 | 294.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169332 | 0 | 169332 | 395938 | -694678 | 11 | 14 | 395938 | -1694678
1 | 23 | 16 | 1 | 41.7006 | 0 | 173.986 | 38.5937 | 0 | 0 | 25.2364 | 19.0363 | 0 | 0 | 0 | 0 | 298.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153935 | 0 | 153935 | 399279 | -733300 | 10 | 12 | 399279 | -1733300
1 | 23 | 17 | 1 | 46.1915 | 0 | 169.782 | 42.695 | 0 | 0 | 25.2267 | 19.0363 | 0 | 0 | 0 | 2.4 | 305.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125644 | 0 | 125644 | 389911 | -805256 | 8 | 11 | 389911 | -1805256
1 | 23 | 18 | 1 | 49.7836 | 0 | 152.497 | 51.6576 | 0 | 0 | 25.2187 | 19.0363 | 0 | 0 | 0 | 6.4 | 304.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94211.5 | 0 | 94211.5 | 377449 | -922440 | 7 | 9 | 377449 | -1922440
1 | 23 | 19 | 1 | 34.11 | 0 | 93.4203 | 57.5652 | 0 | 0 | 25.2258 | 19.0363 | 0 | 0 | 0 | 7.2 | 236.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58311.8 | 0 | 58311.8 | 295200 | -930338 | 7 | 9 | 295200 | -1930338
1 | 23 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 15.3381 | 0 | 5.9881 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41706.1 | 0 | 41706.1 | 204483 | -19392.4 | 7 | 8 | 204483 | -1019392.4
1 | 23 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 13.1106 | 0 | 5.9311 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37009.7 | 0 | 37009.7 | 174386 | -100515 | 6 | 8 | 174386 | -1100515
1 | 23 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.9128 | 0 | 5.9105 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22699.4 | 0 | 22699.4 | 154723 | -149440 | 7 | 8 | 154723 | -1149440
1 | 23 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 10.9088 | 0 | 5.9011 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12198.6 | 0 | 12198.6 | 141853 | -183002 | 7 | 9 | 141853 | -1183002
1 | 23 | 24 | 1 | 10.3176 | 0 | 42.5403 | 12.5549 | 0 | 0 | 10.0704 | 17.5105 | 0 | 0 | 0 | 5.6 | 98.5937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10611.6 | 0 | 10611.6 | 136478 | -225418 | 7 | 9 | 136478 | -1225418
1 | 24 | 1 | 2 | 10.424 | 0 | 42.3304 | 13.4456 | 0 | 0 | 11.1086 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615 | 0 | 10615 | 134579 | -237548 | 8 | 10 | 134579 | -1237548
1 | 24 | 2 | 2 | 10.424 | 0 | 42.3304 | 14.2867 | 0 | 0 | 12.0526 | 17.3638 | 0 | 0 | 0 | 4.8 | 101.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10618.1 | 0 | 10618.1 | 135153 | -255019 | 8 | 10 | 135153 | -1255019
1 | 24 | 3 | 2 | 10.424 | 0 | 42.3304 | 14.6375 | 0 | 0 | 12.5052 | 17.3638 | 0 | 0 | 0 | 4.8 | 102.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10620.9 | 0 | 10620.9 | 132581 | -256997 | 9 | 11 | 132581 | -1256997
1 | 24 | 4 | 2 | 10.424 | 0 | 42.3304 | 15.023 | 0 | 0 | 13.039 | 17.3638 | 0 | 0 | 0 | 4.8 | 102.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10623.5 | 0 | 10623.5 | 133052 | -265343 | 10 | 12 | 133052 | -1265343
1 | 24 | 5 | 2 | 11.8202 | 0 | 44.8242 | 15.2236 | 0 | 0 | 13.3352 | 17.5105 | 0 | 0 | 0 | 4.8 | 107.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11799.6 | 0 | 11799.6 | 134168 | -267280 | 11 | 13 | 134168 | -1267280
1 | 24 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.2764 | 0 | 5.9258 | 17.5105 | 0 | 0 | 0 | 4.8 | 135.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28651.1 | 0 | 28651.1 | 180987 | -236517 | 12 | 14 | 180987 | -1236517
1 | 24 | 7 | 2 | 49.0171 | 0 | 140.608 | 66.8735 | 0 | 0 | 25.2076 | 19.5565 | 0 | 0 | 0 | 3.2 | 304.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84903.3 | 0 | 84903.3 | 315266 | -1144870 | 13 | 15 | 315266 | -2144870
1 | 24 | 8 | 2 | 52.7262 | 0 | 168.222 | 55.969 | 0 | 0 | 25.2106 | 19.2643 | 0 | 0 | 0 | 0.8 | 322.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103116 | 0 | 103116 | 377670 | -990174 | 14 | 17 | 377670 | -1990174
1 | 24 | 9 | 2 | 49.5555 | 0 | 173.795 | 46.6597 | 0 | 0 | 25.2229 | 19.0842 | 0 | 0 | 0 | 0 | 314.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142728 | 0 | 142728 | 396742 | -838231 | 15 | 18 | 396742 | -1838231
1 | 24 | 10 | 2 | 42.2466 | 0 | 172.186 | 45.2253 | 0 | 0 | 25.23 | 19.0363 | 0 | 0 | 0 | 0 | 303.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167947 | 0 | 167947 | 395047 | -801949 | 17 | 19 | 395047 | -1801949
1 | 24 | 11 | 2 | 42.614 | 0 | 163.102 | 45.9218 | 0 | 0 | 25.2349 | 19.0363 | 0 | 0 | 0 | 0 | 295.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171542 | 0 | 171542 | 379533 | -788644 | 19 | 20 | 379533 | -1788644
1 | 24 | 12 | 2 | 41.2236 | 0 | 149.692 | 42.3063 | 0 | 0 | 25.2507 | 19.0363 | 0 | 0 | 0 | 0 | 277.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171541 | 0 | 171541 | 360631 | -704547 | 20 | 21 | 360631 | -1704547
1 | 24 | 13 | 2 | 39.9817 | 0 | 150.207 | 41.4652 | 0 | 0 | 25.2491 | 19.0363 | 0 | 0 | 0 | 0 | 275.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171538 | 0 | 171538 | 350289 | -704550 | 20 | 21 | 350289 | -1704550
1 | 24 | 14 | 2 | 42.3242 | 0 | 165.698 | 35.3571 | 0 | 0 | 25.2475 | 19.0363 | 0 | 0 | 0 | 0 | 287.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171535 | 0 | 171535 | 383479 | -644214 | 20 | 21 | 383479 | -1644214
1 | 24 | 15 | 2 | 41.6694 | 0 | 172.702 | 33.2851 | 0 | 0 | 25.2473 | 19.0363 | 0 | 0 | 0 | 0 | 291.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169317 | 0 | 169317 | 402139 | -630460 | 20 | 21 | 402139 | -1630460
1 | 24 | 16 | 2 | 43.4401 | 0 | 173.986 | 35.3734 | 0 | 0 | 25.2433 | 19.0363 | 0 | 0 | 0 | 0 | 297.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153920 | 0 | 153920 | 405014 | -667441 | 18 | 19 | 405014 | -1667441
1 | 24 | 17 | 2 | 51.8489 | 0 | 169.782 | 39.9942 | 0 | 0 | 25.2423 | 19.0363 | 0 | 0 | 0 | 2.4 | 308.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125630 | 0 | 125630 | 395464 | -723158 | 16 | 17 | 395464 | -1723158
1 | 24 | 18 | 2 | 49.7836 | 0 | 152.497 | 46.5331 | 0 | 0 | 25.2361 | 19.0363 | 0 | 0 | 0 | 6.4 | 299.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94197.3 | 0 | 94197.3 | 381327 | -807615 | 13 | 15 | 381327 | -1807615
1 | 24 | 19 | 2 | 34.11 | 0 | 93.4203 | 54.875 | 0 | 0 | 25.2357 | 19.0363 | 0 | 0 | 0 | 7.2 | 233.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58298.1 | 0 | 58298.1 | 310053 | -880874 | 10 | 11 | 310053 | -1880874
1 | 24 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 15.7222 | 0 | 6.0008 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41692.9 | 0 | 41692.9 | 209747 | -19261.3 | 6 | 8 | 209747 | -1019261.3
1 | 24 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.9473 | 0 | 5.9304 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36997.4 | 0 | 36997.4 | 176050 | -107998 | 3 | 4 | 176050 | -1107998
1 | 24 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 11.6198 | 0 | 5.9104 | 17.5105 | 0 | 0 | 0 | 7.2 | 104.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22686.4 | 0 | 22686.4 | 159708 | -178116 | 1 | 2 | 159708 | -1178116
1 | 24 | 23 | 2 | 11.1963 | 0 | 44.3342 | 12.9074 | 0 | 0 | 10.6961 | 17.5105 | 0 | 0 | 0 | 6.4 | 103.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12186.1 | 0 | 12186.1 | 146336 | -239951 | -1 | 1 | 146336 | -1239951
1 | 24 | 24 | 2 | 10.3176 | 0 | 42.5403 | 15.7666 | 0 | 0 | 14.3992 | 17.5105 | 0 | 0 | 0 | 5.6 | 106.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10600 | 0 | 10600 | 140473 | -274784 | -2 | -1 | 140473 | -1274784
1 | 25 | 1 | 3 | 10.8489 | 0 | 42.3304 | 17.4061 | 0 | 0 | 17.0477 | 17.3638 | 0 | 0 | 0 | 4.8 | 109.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604.6 | 0 | 10604.6 | 138023 | -301628 | -3 | -2 | 138023 | -1301628
1 | 25 | 2 | 3 | 10.8489 | 0 | 42.3304 | 18.6477 | 0 | 0 | 19.0562 | 17.3638 | 0 | 0 | 0 | 4.8 | 113.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10608.5 | 0 | 10608.5 | 136335 | -320828 | -4 | -3 | 136335 | -1320828
1 | 25 | 3 | 3 | 10.8489 | 0 | 42.3304 | 19.9162 | 0 | 0 | 21.4964 | 17.3638 | 0 | 0 | 0 | 4.8 | 116.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10612 | 0 | 10612 | 134836 | -340175 | -5 | -4 | 134836 | -1340175
1 | 25 | 4 | 3 | 10.8489 | 0 | 42.3304 | 21.2554 | 0 | 0 | 24.802 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615.2 | 0 | 10615.2 | 133541 | -359103 | -7 | -6 | 133541 | -1359103
1 | 25 | 5 | 3 | 11.8202 | 0 | 44.8242 | 23.6751 | 0 | 0 | 25.3023 | 17.5105 | 0 | 0 | 0 | 4.8 | 127.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11792 | 0 | 11792 | 134910 | -388592 | -9 | -8 | 134910 | -1388592
1 | 25 | 6 | 3 | 24.3093 | 0 | 69.9783 | 23.1624 | 0 | 0 | 25.3092 | 17.5105 | 0 | 0 | 0 | 4.8 | 165.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28644.4 | 0 | 28644.4 | 180393 | -375646 | -11 | -10 | 180393 | -1375646
1 | 25 | 7 | 3 | 49.0171 | 0 | 140.608 | 87.7674 | 0 | 0 | 25.2604 | 19.9579 | 0 | 0 | 0 | 3.2 | 325.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84897.5 | 0 | 84897.5 | 314965 | -1572900 | -11 | -10 | 314965 | -2572900
1 | 25 | 8 | 3 | 51.1424 | 0 | 168.222 | 80.137 | 0 | 0 | 25.2383 | 19.5893 | 0 | 0 | 0 | 0.8 | 345.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103111 | 0 | 103111 | 377012 | -1488210 | -12 | -11 | 377012 | -2488210
1 | 25 | 9 | 3 | 41.9973 | 0 | 173.795 | 70.3923 | 0 | 0 | 25.2125 | 19.1432 | 0 | 0 | 0 | 0 | 330.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142723 | 0 | 142723 | 396820 | -1300500 | -12 | -11 | 396820 | -2300500
1 | 25 | 10 | 3 | 41.6139 | 0 | 172.186 | 67.5381 | 0 | 0 | 25.2087 | 19.0363 | 0 | 0 | 0 | 0 | 325.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167944 | 0 | 167944 | 394508 | -1243060 | -11 | -10 | 394508 | -2243060
1 | 25 | 11 | 3 | 41.4976 | 0 | 163.102 | 67.4594 | 0 | 0 | 25.2086 | 19.0363 | 0 | 0 | 0 | 0 | 316.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171540 | 0 | 171540 | 381770 | -1237590 | -10 | -9 | 381770 | -2237590
1 | 25 | 12 | 3 | 40.8516 | 0 | 149.692 | 60.5979 | 0 | 0 | 25.2075 | 19.0363 | 0 | 0 | 0 | 0 | 295.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171540 | 0 | 171540 | 348177 | -1094730 | -9 | -8 | 348177 | -2094730
1 | 25 | 13 | 3 | 39.8342 | 0 | 150.207 | 61.7711 | 0 | 0 | 25.2073 | 19.0363 | 0 | 0 | 0 | 0 | 296.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171538 | 0 | 171538 | 348312 | -1127710 | -9 | -8 | 348312 | -2127710
1 | 25 | 14 | 3 | 41.3219 | 0 | 165.698 | 57.8734 | 0 | 0 | 25.2073 | 19.0363 | 0 | 0 | 0 | 0 | 309.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171535 | 0 | 171535 | 380997 | -1096740 | -9 | -7 | 380997 | -2096740
1 | 25 | 15 | 3 | 40.6887 | 0 | 172.702 | 55.6487 | 0 | 0 | 25.2078 | 19.0363 | 0 | 0 | 0 | 0 | 313.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169317 | 0 | 169317 | 400347 | -1094150 | -8 | -7 | 400347 | -2094150
1 | 25 | 16 | 3 | 40.7097 | 0 | 173.986 | 59.5469 | 0 | 0 | 25.2075 | 19.0363 | 0 | 0 | 0 | 0 | 318.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153921 | 0 | 153921 | 403558 | -1156330 | -9 | -8 | 403558 | -2156330
1 | 25 | 17 | 3 | 47.6309 | 0 | 169.782 | 64.7999 | 0 | 0 | 25.2083 | 19.0363 | 0 | 0 | 0 | 2.4 | 328.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125632 | 0 | 125632 | 393129 | -1242610 | -10 | -9 | 393129 | -2242610
1 | 25 | 18 | 3 | 49.7836 | 0 | 152.497 | 72.24 | 0 | 0 | 25.2096 | 19.0388 | 0 | 0 | 0 | 6.4 | 325.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94200 | 0 | 94200 | 382356 | -1317810 | -11 | -10 | 382356 | -2317810
1 | 25 | 19 | 3 | 34.11 | 0 | 93.4203 | 79.3344 | 0 | 0 | 25.2073 | 19.1289 | 0 | 0 | 0 | 7.2 | 258.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58300.6 | 0 | 58300.6 | 327838 | -1294520 | -11 | -10 | 327838 | -2294520
1 | 25 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 16.2528 | 0 | 6.0069 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41694.6 | 0 | 41694.6 | 205176 | -47231.5 | -11 | -10 | 205176 | -1047231.5
1 | 25 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.6799 | 0 | 5.9396 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36998.2 | 0 | 36998.2 | 177336 | -234810 | -11 | -10 | 177336 | -1234810
1 | 25 | 22 | 3 | 13.825 | 0 | 48.8953 | 17.7454 | 0 | 0 | 16.77 | 17.5105 | 0 | 0 | 0 | 7.2 | 121.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22689.5 | 0 | 22689.5 | 155987 | -294554 | -11 | -10 | 155987 | -1294554
1 | 25 | 23 | 3 | 11.1963 | 0 | 44.3342 | 21.4879 | 0 | 0 | 24.8411 | 17.5105 | 0 | 0 | 0 | 6.4 | 125.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12189.8 | 0 | 12189.8 | 147358 | -350826 | -11 | -10 | 147358 | -1350826
1 | 25 | 24 | 3 | 10.3176 | 0 | 42.5403 | 22.1257 | 0 | 0 | 25.3131 | 17.5105 | 0 | 0 | 0 | 5.6 | 123.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10604.1 | 0 | 10604.1 | 137171 | -357490 | -11 | -10 | 137171 | -1357490
1 | 26 | 1 | 4 | 10.73 | 0 | 42.3304 | 23.5958 | 0 | 0 | 25.3099 | 17.3638 | 0 | 0 | 0 | 4.8 | 124.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10609 | 0 | 10609 | 137964 | -383091 | -11 | -10 | 137964 | -1383091
1 | 26 | 2 | 4 | 10.73 | 0 | 42.3304 | 24.0728 | 0 | 0 | 25.3063 | 17.3638 | 0 | 0 | 0 | 4.8 | 124.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10613 | 0 | 10613 | 133669 | -388234 | -11 | -10 | 133669 | -1388234
1 | 26 | 3 | 4 | 10.73 | 0 | 42.3304 | 25.2069 | 0 | 0 | 25.3029 | 17.3638 | 0 | 0 | 0 | 4.8 | 125.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10616.7 | 0 | 10616.7 | 134904 | -409516 | -11 | -10 | 134904 | -1409516
1 | 26 | 4 | 4 | 10.73 | 0 | 42.3304 | 25.601 | 0 | 0 | 25.3001 | 17.3638 | 0 | 0 | 0 | 4.8 | 126.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10619.9 | 0 | 10619.9 | 131323 | -412208 | -11 | -10 | 131323 | -1412208
1 | 26 | 5 | 4 | 11.8202 | 0 | 44.8242 | 27.8289 | 0 | 0 | 25.2898 | 17.5105 | 0 | 0 | 0 | 4.8 | 132.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11796.7 | 0 | 11796.7 | 135029 | -438722 | -11 | -10 | 135029 | -1438722
1 | 26 | 6 | 4 | 24.3093 | 0 | 69.9783 | 25.5694 | 0 | 0 | 25.3019 | 17.5105 | 0 | 0 | 0 | 4.8 | 167.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28648.9 | 0 | 28648.9 | 178578 | -403702 | -11 | -10 | 178578 | -1403702
1 | 26 | 7 | 4 | 49.0171 | 0 | 140.608 | 89.3152 | 0 | 0 | 25.2703 | 20.0341 | 0 | 0 | 0 | 3.2 | 327.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84901.8 | 0 | 84901.8 | 313620 | -1612310 | -11 | -10 | 313620 | -2612310
1 | 26 | 8 | 4 | 52.3554 | 0 | 168.222 | 82.1131 | 0 | 0 | 25.2431 | 19.6661 | 0 | 0 | 0 | 0.8 | 348.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103116 | 0 | 103116 | 375792 | -1516390 | -11 | -10 | 375792 | -2516390
1 | 26 | 9 | 4 | 40.6483 | 0 | 173.795 | 72.621 | 0 | 0 | 25.2181 | 19.2445 | 0 | 0 | 0 | 0 | 331.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142725 | 0 | 142725 | 395677 | -1343330 | -11 | -10 | 395677 | -2343330
1 | 26 | 10 | 4 | 40.8676 | 0 | 172.186 | 67.6657 | 0 | 0 | 25.2099 | 19.0545 | 0 | 0 | 0 | 0 | 324.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167945 | 0 | 167945 | 393336 | -1251910 | -9 | -8 | 393336 | -2251910
1 | 26 | 11 | 4 | 41.2191 | 0 | 163.102 | 67.0812 | 0 | 0 | 25.2094 | 19.0363 | 0 | 0 | 0 | 0 | 315.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171541 | 0 | 171541 | 374111 | -1238840 | -8 | -7 | 374111 | -2238840
1 | 26 | 12 | 4 | 40.7603 | 0 | 149.692 | 60.9339 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 0 | 295.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171540 | 0 | 171540 | 347413 | -1089500 | -6 | -5 | 347413 | -2089500
1 | 26 | 13 | 4 | 39.8231 | 0 | 150.207 | 57.9138 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 0 | 292.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171538 | 0 | 171538 | 347756 | -1065610 | -5 | -4 | 347756 | -2065610
1 | 26 | 14 | 4 | 41.3048 | 0 | 165.698 | 53.6842 | 0 | 0 | 25.2075 | 19.0363 | 0 | 0 | 0 | 0 | 304.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171535 | 0 | 171535 | 380487 | -1020500 | -5 | -3 | 380487 | -2020500
1 | 26 | 15 | 4 | 40.7025 | 0 | 172.702 | 51.4057 | 0 | 0 | 25.2097 | 19.0363 | 0 | 0 | 0 | 0 | 309.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169317 | 0 | 169317 | 399768 | -1003150 | -4 | -2 | 399768 | -2003150
1 | 26 | 16 | 4 | 40.701 | 0 | 173.986 | 53.4293 | 0 | 0 | 25.2094 | 19.0363 | 0 | 0 | 0 | 0 | 312.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153921 | 0 | 153921 | 403130 | -1049910 | -4 | -3 | 403130 | -2049910
1 | 26 | 17 | 4 | 46.4193 | 0 | 169.782 | 57.4893 | 0 | 0 | 25.2075 | 19.0363 | 0 | 0 | 0 | 2.4 | 320.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125631 | 0 | 125631 | 392826 | -1123150 | -5 | -3 | 392826 | -2123150
1 | 26 | 18 | 4 | 49.7836 | 0 | 152.497 | 64.7099 | 0 | 0 | 25.2073 | 19.0363 | 0 | 0 | 0 | 6.4 | 317.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94199.5 | 0 | 94199.5 | 377109 | -1199960 | -6 | -4 | 377109 | -2199960
1 | 26 | 19 | 4 | 34.11 | 0 | 93.4203 | 73.1197 | 0 | 0 | 25.2085 | 19.0923 | 0 | 0 | 0 | 7.2 | 252.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58300 | 0 | 58300 | 317842 | -1198650 | -6 | -5 | 317842 | -2198650
1 | 26 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 15.8494 | 0 | 5.9991 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41694 | 0 | 41694 | 205570 | -45294.4 | -7 | -5 | 205570 | -1045294.4
1 | 26 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.2494 | 0 | 5.9333 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36997.7 | 0 | 36997.7 | 175545 | -203276 | -7 | -6 | 175545 | -1203276
1 | 26 | 22 | 4 | 13.825 | 0 | 48.8953 | 15.052 | 0 | 0 | 12.5042 | 17.5105 | 0 | 0 | 0 | 7.2 | 114.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22688.5 | 0 | 22688.5 | 156195 | -260150 | -8 | -6 | 156195 | -1260150
1 | 26 | 23 | 4 | 11.1963 | 0 | 44.3342 | 19.4817 | 0 | 0 | 19.9173 | 17.5105 | 0 | 0 | 0 | 6.4 | 118.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12188.6 | 0 | 12188.6 | 147227 | -321741 | -8 | -7 | 147227 | -1321741
1 | 26 | 24 | 4 | 10.3176 | 0 | 42.5403 | 20.1879 | 0 | 0 | 21.3844 | 17.5105 | 0 | 0 | 0 | 5.6 | 117.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10602.7 | 0 | 10602.7 | 137415 | -332336 | -8 | -7 | 137415 | -1332336
1 | 27 | 1 | 5 | 10.8489 | 0 | 42.3304 | 21.7045 | 0 | 0 | 24.9935 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10607.4 | 0 | 10607.4 | 137875 | -359153 | -8 | -7 | 137875 | -1359153
1 | 27 | 2 | 5 | 10.8489 | 0 | 42.3304 | 21.9709 | 0 | 0 | 25.0698 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10611.3 | 0 | 10611.3 | 134007 | -361390 | -7 | -6 | 134007 | -1361390
1 | 27 | 3 | 5 | 10.8489 | 0 | 42.3304 | 23.134 | 0 | 0 | 25.3068 | 17.3638 | 0 | 0 | 0 | 4.8 | 123.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10614.8 | 0 | 10614.8 | 134956 | -381704 | -7 | -6 | 134956 | -1381704
1 | 27 | 4 | 5 | 10.8489 | 0 | 42.3304 | 23.3389 | 0 | 0 | 25.3041 | 17.3638 | 0 | 0 | 0 | 4.8 | 123.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10618 | 0 | 10618 | 131771 | -382875 | -7 | -6 | 131771 | -1382875
1 | 27 | 5 | 5 | 11.8202 | 0 | 44.8242 | 24.8574 | 0 | 0 | 25.3031 | 17.5105 | 0 | 0 | 0 | 4.8 | 129.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11794.7 | 0 | 11794.7 | 135644 | -403811 | -8 | -7 | 135644 | -1403811
1 | 27 | 6 | 5 | 24.3093 | 0 | 69.9783 | 23.2471 | 0 | 0 | 25.309 | 17.5105 | 0 | 0 | 0 | 4.8 | 165.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28646.8 | 0 | 28646.8 | 179170 | -369574 | -8 | -7 | 179170 | -1369574
1 | 27 | 7 | 5 | 49.0171 | 0 | 140.608 | 84.4613 | 0 | 0 | 25.2533 | 19.935 | 0 | 0 | 0 | 3.2 | 322.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84899.6 | 0 | 84899.6 | 314036 | -1520690 | -7 | -6 | 314036 | -2520690
1 | 27 | 8 | 5 | 52.6966 | 0 | 168.222 | 75.0854 | 0 | 0 | 25.2272 | 19.5286 | 0 | 0 | 0 | 0.8 | 341.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103113 | 0 | 103113 | 376226 | -1391180 | -6 | -5 | 376226 | -2391180
1 | 27 | 9 | 5 | 45.4844 | 0 | 173.795 | 65.3938 | 0 | 0 | 25.211 | 19.2159 | 0 | 0 | 0 | 0 | 329.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142723 | 0 | 142723 | 395997 | -1218490 | -5 | -4 | 395997 | -2218490
1 | 27 | 10 | 5 | 41.9437 | 0 | 172.186 | 64.4834 | 0 | 0 | 25.2091 | 19.1074 | 0 | 0 | 0 | 0 | 322.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167943 | 0 | 167943 | 393635 | -1197210 | -5 | -4 | 393635 | -2197210
1 | 27 | 11 | 5 | 42.0539 | 0 | 163.102 | 65.1092 | 0 | 0 | 25.208 | 19.0363 | 0 | 0 | 0 | 0 | 314.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171539 | 0 | 171539 | 374627 | -1186600 | -4 | -3 | 374627 | -2186600
1 | 27 | 12 | 5 | 41.4897 | 0 | 149.692 | 63.5675 | 0 | 0 | 25.2079 | 19.0443 | 0 | 0 | 0 | 0 | 299.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171539 | 0 | 171539 | 356522 | -1114040 | -4 | -3 | 356522 | -2114040
1 | 27 | 13 | 5 | 39.9656 | 0 | 150.207 | 61.5575 | 0 | 0 | 25.2077 | 19.0541 | 0 | 0 | 0 | 0 | 295.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171536 | 0 | 171536 | 348073 | -1100180 | -3 | -2 | 348073 | -2100180
1 | 27 | 14 | 5 | 42.2526 | 0 | 165.698 | 54.1087 | 0 | 0 | 25.2073 | 19.0363 | 0 | 0 | 0 | 0 | 306.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171533 | 0 | 171533 | 380928 | -1055870 | -3 | -2 | 380928 | -2055870
1 | 27 | 15 | 5 | 41.5316 | 0 | 172.702 | 52.9418 | 0 | 0 | 25.2087 | 19.0363 | 0 | 0 | 0 | 0 | 311.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169315 | 0 | 169315 | 400162 | -1029560 | -2 | -1 | 400162 | -2029560
1 | 27 | 16 | 5 | 42.1553 | 0 | 173.986 | 53.371 | 0 | 0 | 25.2093 | 19.0363 | 0 | 0 | 0 | 0 | 313.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153919 | 0 | 153919 | 403374 | -1042920 | -2 | -1 | 403374 | -2042920
1 | 27 | 17 | 5 | 50.7112 | 0 | 169.782 | 54.77 | 0 | 0 | 25.2084 | 19.0363 | 0 | 0 | 0 | 2.4 | 321.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125629 | 0 | 125629 | 393329 | -1060250 | -1 | 0 | 393329 | -2060250
1 | 27 | 18 | 5 | 49.7703 | 0 | 152.497 | 61.3346 | 0 | 0 | 25.2086 | 19.0363 | 0 | 0 | 0 | 6.4 | 314.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94197.1 | 0 | 94197.1 | 370603 | -1118190 | -1 | 0 | 370603 | -2118190
1 | 27 | 19 | 5 | 34.11 | 0 | 93.4203 | 67.9319 | 0 | 0 | 25.2124 | 19.091 | 0 | 0 | 0 | 7.2 | 246.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58297.6 | 0 | 58297.6 | 307063 | -1103860 | -1 | 0 | 307063 | -2103860
1 | 27 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.9014 | 0 | 5.9827 | 17.5105 | 0 | 0 | 0 | 7.2 | 132.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41691.8 | 0 | 41691.8 | 206417 | -39571.8 | -1 | 0 | 206417 | -1039571.8
1 | 27 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.7785 | 0 | 5.9284 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36995.6 | 0 | 36995.6 | 175655 | -167889 | -1 | 0 | 175655 | -1167889
1 | 27 | 22 | 5 | 13.825 | 0 | 48.8953 | 12.5682 | 0 | 0 | 10.0654 | 17.5105 | 0 | 0 | 0 | 7.2 | 110.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22685.8 | 0 | 22685.8 | 157240 | -221651 | -1 | 0 | 157240 | -1221651
1 | 27 | 23 | 5 | 11.1963 | 0 | 44.3342 | 15.6862 | 0 | 0 | 13.9081 | 17.5105 | 0 | 0 | 0 | 6.4 | 109.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12185.7 | 0 | 12185.7 | 149072 | -267378 | -1 | 0 | 149072 | -1267378
1 | 27 | 24 | 5 | 10.3176 | 0 | 42.5403 | 16.5017 | 0 | 0 | 15.1695 | 17.5105 | 0 | 0 | 0 | 5.6 | 107.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599.4 | 0 | 10599.4 | 138710 | -272767 | -1 | 0 | 138710 | -1272767
1 | 28 | 1 | 6 | 6.3817 | 0 | 42.7453 | 18.0497 | 0 | 0 | 17.701 | 17.3638 | 0 | 0 | 0 | 4.8 | 107.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10603.9 | 0 | 10603.9 | 147643 | -303390 | -4 | -3 | 147643 | -1303390
1 | 28 | 2 | 6 | 6.3817 | 0 | 42.7453 | 17.339 | 0 | 0 | 15.8475 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10607.4 | 0 | 10607.4 | 134711 | -283382 | -6 | -5 | 134711 | -1283382
1 | 28 | 3 | 6 | 6.3817 | 0 | 42.7453 | 18.9728 | 0 | 0 | 18.655 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10611 | 0 | 10611 | 139347 | -318764 | -9 | -8 | 139347 | -1318764
1 | 28 | 4 | 6 | 6.3817 | 0 | 42.7453 | 19.2139 | 0 | 0 | 19.1169 | 17.3638 | 0 | 0 | 0 | 4.8 | 109.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10613.3 | 0 | 10613.3 | 132244 | -314100 | -10 | -9 | 132244 | -1314100
1 | 28 | 5 | 6 | 6.3817 | 0 | 42.7453 | 20.7353 | 0 | 0 | 22.4498 | 17.3638 | 0 | 0 | 0 | 4.8 | 114.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10615.5 | 0 | 10615.5 | 131077 | -341852 | -11 | -11 | 131077 | -1341852
1 | 28 | 6 | 6 | 6.3817 | 0 | 42.7453 | 23.1481 | 0 | 0 | 25.3069 | 17.3638 | 0 | 0 | 0 | 4.8 | 119.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10617.5 | 0 | 10617.5 | 129911 | -380295 | -13 | -12 | 129911 | -1380295
1 | 28 | 7 | 6 | 6.3817 | 0 | 42.7453 | 23.5274 | 0 | 0 | 25.3028 | 17.3638 | 0 | 0 | 0 | 3.2 | 118.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10619.4 | 0 | 10619.4 | 128863 | -379709 | -11 | -10 | 128863 | -1379709
1 | 28 | 8 | 6 | 6.1628 | 0 | 42.7453 | 100.036 | 0 | 0 | 25.215 | 20.7346 | 0 | 0 | 0 | 0.8 | 195.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10622.3 | 0 | 10622.3 | 118976 | -1549970 | -9 | -9 | 118976 | -2549970
1 | 28 | 9 | 6 | 5.1728 | 0 | 42.7453 | 89.3221 | 0 | 0 | 25.2075 | 19.8056 | 0 | 0 | 0 | 0 | 182.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10624.7 | 0 | 10624.7 | 118405 | -1340880 | -8 | -7 | 118405 | -2340880
1 | 28 | 10 | 6 | 5.5741 | 0 | 42.7453 | 75.9759 | 0 | 0 | 25.2106 | 19.1647 | 0 | 0 | 0 | 0 | 168.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10603.1 | 0 | 10603.1 | 117738 | -1163000 | -6 | -5 | 117738 | -2163000
1 | 28 | 11 | 6 | 5.4865 | 0 | 42.7453 | 69.7333 | 0 | 0 | 25.2146 | 18.9802 | 0 | 0 | 0 | 0 | 162.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10600.1 | 0 | 10600.1 | 117234 | -1068480 | -4 | -3 | 117234 | -2068480
1 | 28 | 12 | 6 | 5.4789 | 0 | 42.7453 | 64.9139 | 0 | 0 | 25.2187 | 18.9137 | 0 | 0 | 0 | 0 | 157.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10598.5 | 0 | 10598.5 | 116729 | -1003220 | -2 | -1 | 116729 | -2003220
1 | 28 | 13 | 6 | 5.4795 | 0 | 42.7453 | 60.7756 | 0 | 0 | 25.2214 | 18.8896 | 0 | 0 | 0 | 0 | 153.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10597.4 | 0 | 10597.4 | 116313 | -953444 | -1 | 1 | 116313 | -1953444
1 | 28 | 14 | 6 | 5.48 | 0 | 42.7453 | 56.6395 | 0 | 0 | 25.2227 | 18.8896 | 0 | 0 | 0 | 0 | 148.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10596.6 | 0 | 10596.6 | 115916 | -919322 | 1 | 2 | 115916 | -1919322
1 | 28 | 15 | 6 | 5.4814 | 0 | 42.7453 | 0 | 10.9173 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 0 | 82.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.9 | 0 | 10595.9 | 149592 | -19522.4 | 2 | 4 | 149592 | -1019522.4
1 | 28 | 16 | 6 | 5.536 | 0 | 42.7453 | 0 | 9.7954 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 81.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.6 | 0 | 10595.6 | 133824 | -118394 | 0 | 2 | 133824 | -1118394
1 | 28 | 17 | 6 | 6.6388 | 0 | 42.7453 | 0 | 9.6233 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 2.4 | 84.6679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10603.8 | 0 | 10603.8 | 129395 | -173932 | -2 | -1 | 129395 | -1173932
1 | 28 | 18 | 6 | 8.7892 | 0 | 42.7453 | 13.0547 | 0 | 0 | 10.5611 | 17.3638 | 0 | 0 | 0 | 6.4 | 98.9141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10609.5 | 0 | 10609.5 | 126240 | -236549 | -4 | -3 | 126240 | -1236549
1 | 28 | 19 | 6 | 8.7973 | 0 | 42.7453 | 16.9806 | 0 | 0 | 15.9323 | 17.3638 | 0 | 0 | 0 | 7.2 | 109.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10613.8 | 0 | 10613.8 | 125014 | -288698 | -5 | -4 | 125014 | -1288698
1 | 28 | 20 | 6 | 8.7973 | 0 | 42.7453 | 18.8964 | 0 | 0 | 19.4519 | 17.3638 | 0 | 0 | 0 | 7.2 | 114.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10618.2 | 0 | 10618.2 | 124436 | -318210 | -5 | -4 | 124436 | -1318210
1 | 28 | 21 | 6 | 8.7973 | 0 | 42.7453 | 20.5953 | 0 | 0 | 23.2225 | 17.3638 | 0 | 0 | 0 | 7.2 | 119.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10621.7 | 0 | 10621.7 | 123295 | -340416 | -6 | -5 | 123295 | -1340416
1 | 28 | 22 | 6 | 8.7973 | 0 | 42.7453 | 21.7055 | 0 | 0 | 25.3063 | 17.3638 | 0 | 0 | 0 | 7.2 | 123.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10625 | 0 | 10625 | 123216 | -359055 | -7 | -6 | 123216 | -1359055
1 | 28 | 23 | 6 | 8.7973 | 0 | 42.7453 | 23.0983 | 0 | 0 | 25.2945 | 17.3638 | 0 | 0 | 0 | 6.4 | 123.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10628 | 0 | 10628 | 121929 | -374492 | -7 | -6 | 121929 | -1374492
1 | 28 | 24 | 6 | 8.7973 | 0 | 42.7453 | 24.4862 | 0 | 0 | 25.2808 | 17.3638 | 0 | 0 | 0 | 5.6 | 124.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10630.8 | 0 | 10630.8 | 121353 | -394622 | -8 | -7 | 121353 | -1394622
1 | 29 | 1 | 7 | 5.1054 | 0 | 42.7453 | 25.4132 | 0 | 0 | 25.2745 | 17.3638 | 0 | 0 | 0 | 4.8 | 120.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4007.24 | 0 | 4007.24 | 120989 | -419288 | -6 | -5 | 120989 | -1419288
1 | 29 | 2 | 7 | 5.1054 | 0 | 42.7453 | 25.7447 | 0 | 0 | 25.2734 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.81 | 0 | 4008.81 | 120509 | -428493 | -5 | -4 | 120509 | -1428493
1 | 29 | 3 | 7 | 5.1054 | 0 | 42.7453 | 25.8362 | 0 | 0 | 25.2727 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4010.4 | 0 | 4010.4 | 120053 | -431453 | -3 | -2 | 120053 | -1431453
1 | 29 | 4 | 7 | 5.1054 | 0 | 42.7453 | 26.291 | 0 | 0 | 25.2716 | 17.3638 | 0 | 0 | 0 | 4.8 | 121.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.76 | 0 | 4011.76 | 119708 | -437171 | -4 | -3 | 119708 | -1437171
1 | 29 | 5 | 7 | 5.1054 | 0 | 42.7453 | 26.8096 | 0 | 0 | 25.2705 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4013.06 | 0 | 4013.06 | 119318 | -443304 | -5 | -4 | 119318 | -1443304
1 | 29 | 6 | 7 | 5.1054 | 0 | 42.7453 | 27.4041 | 0 | 0 | 25.27 | 17.3638 | 0 | 0 | 0 | 4.8 | 122.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.29 | 0 | 4014.29 | 118951 | -452083 | -6 | -5 | 118951 | -1452083
1 | 29 | 7 | 7 | 5.1054 | 0 | 42.7453 | 27.5974 | 0 | 0 | 25.2695 | 17.3638 | 0 | 0 | 0 | 3.2 | 121.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.48 | 0 | 4015.48 | 118863 | -456989 | -5 | -4 | 118863 | -1456989
1 | 29 | 8 | 7 | 4.838 | 0 | 42.7453 | 26.6171 | 0 | 0 | 25.2723 | 17.3638 | 0 | 0 | 0 | 0.8 | 117.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.61 | 0 | 4016.61 | 118545 | -440638 | -3 | -2 | 118545 | -1440638
1 | 29 | 9 | 7 | 3.9856 | 0 | 42.7453 | 23.3711 | 0 | 0 | 25.2805 | 17.3638 | 0 | 0 | 0 | 0 | 112.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.69 | 0 | 4017.69 | 118684 | -381804 | -2 | -1 | 118684 | -1381804
1 | 29 | 10 | 7 | 4.2462 | 0 | 42.7453 | 19.6851 | 0 | 0 | 20.8333 | 17.3638 | 0 | 0 | 0 | 0 | 104.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.73 | 0 | 4018.73 | 119251 | -325856 | 1 | 3 | 119251 | -1325856
1 | 29 | 11 | 7 | 4.1774 | 0 | 42.7453 | 17.5187 | 0 | 0 | 16.5935 | 17.3638 | 0 | 0 | 0 | 0 | 98.3986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.65 | 0 | 4019.65 | 121811 | -291065 | 5 | 6 | 121811 | -1291065
1 | 29 | 12 | 7 | 4.1526 | 0 | 42.7453 | 14.9719 | 0 | 0 | 12.6643 | 17.3638 | 0 | 0 | 0 | 0 | 91.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.41 | 0 | 4020.41 | 120544 | -254986 | 8 | 10 | 120544 | -1254986
1 | 29 | 13 | 7 | 4.1533 | 0 | 42.7453 | 13.7972 | 0 | 0 | 11.2599 | 17.3638 | 0 | 0 | 0 | 0 | 89.3194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.95 | 0 | 4020.95 | 121234 | -239521 | 10 | 12 | 121234 | -1239521
1 | 29 | 14 | 7 | 4.1536 | 0 | 42.7453 | 12.7219 | 0 | 0 | 10.1174 | 17.3638 | 0 | 0 | 0 | 0 | 87.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.37 | 0 | 4021.37 | 121589 | -222897 | 11 | 14 | 121589 | -1222897
1 | 29 | 15 | 7 | 4.1668 | 0 | 42.7453 | 12.197 | 0 | 0 | 9.5484 | 17.3638 | 0 | 0 | 0 | 0 | 86.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.8 | 0 | 4021.8 | 123566 | -220802 | 13 | 16 | 123566 | -1220802
1 | 29 | 16 | 7 | 4.2302 | 0 | 42.7453 | 12.3054 | 0 | 0 | 9.5223 | 17.3638 | 0 | 0 | 0 | 0 | 86.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.25 | 0 | 4022.25 | 121073 | -219542 | 11 | 14 | 121073 | -1219542
1 | 29 | 17 | 7 | 4.7272 | 0 | 42.7453 | 13.5915 | 0 | 0 | 10.9208 | 17.3638 | 0 | 0 | 0 | 2.4 | 91.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.84 | 0 | 4022.84 | 119986 | -241164 | 9 | 11 | 119986 | -1241164
1 | 29 | 18 | 7 | 6.6463 | 0 | 42.7453 | 15.9597 | 0 | 0 | 14.4363 | 17.3638 | 0 | 0 | 0 | 6.4 | 103.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023.66 | 0 | 4023.66 | 119082 | -277757 | 7 | 9 | 119082 | -1277757
1 | 29 | 19 | 7 | 6.6633 | 0 | 42.7453 | 19.539 | 0 | 0 | 21.649 | 17.3638 | 0 | 0 | 0 | 7.2 | 115.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4024.66 | 0 | 4024.66 | 119140 | -333471 | 5 | 7 | 119140 | -1333471
1 | 29 | 20 | 7 | 6.6633 | 0 | 42.7453 | 21.1326 | 0 | 0 | 25.2763 | 17.3638 | 0 | 0 | 0 | 7.2 | 120.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4025.85 | 0 | 4025.85 | 118333 | -358600 | 3 | 4 | 118333 | -1358600
1 | 29 | 21 | 7 | 6.6633 | 0 | 42.7453 | 22.5531 | 0 | 0 | 25.2745 | 17.3638 | 0 | 0 | 0 | 7.2 | 121.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.81 | 0 | 4026.81 | 117967 | -379187 | 0 | 2 | 117967 | -1379187
1 | 29 | 22 | 7 | 6.6633 | 0 | 42.7453 | 23.6227 | 0 | 0 | 25.2739 | 17.3638 | 0 | 0 | 0 | 7.2 | 122.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.71 | 0 | 4027.71 | 117815 | -394001 | -1 | 1 | 117815 | -1394001
1 | 29 | 23 | 7 | 6.6633 | 0 | 42.7453 | 24.6097 | 0 | 0 | 25.2729 | 17.3638 | 0 | 0 | 0 | 6.4 | 123.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.54 | 0 | 4028.54 | 117334 | -406877 | -2 | -1 | 117334 | -1406877
1 | 29 | 24 | 7 | 6.6633 | 0 | 42.7453 | 25.4318 | 0 | 0 | 25.2722 | 17.3638 | 0 | 0 | 0 | 5.6 | 123.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.35 | 0 | 4029.35 | 117043 | -418674 | -3 | -2 | 117043 | -1418674
1 | 30 | 1 | 1 | 10.8489 | 0 | 42.3304 | 26.8188 | 0 | 0 | 25.271 | 17.3638 | 0 | 0 | 0 | 4.8 | 127.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656.1 | 0 | 10656.1 | 117617 | -435492 | -5 | -4 | 117617 | -1435492
1 | 30 | 2 | 1 | 10.8489 | 0 | 42.3304 | 27.3726 | 0 | 0 | 25.2703 | 17.3638 | 0 | 0 | 0 | 4.8 | 127.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656.9 | 0 | 10656.9 | 116850 | -447163 | -8 | -7 | 116850 | -1447163
1 | 30 | 3 | 1 | 10.8489 | 0 | 42.3304 | 27.9502 | 0 | 0 | 25.2705 | 17.3638 | 0 | 0 | 0 | 4.8 | 128.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10657.1 | 0 | 10657.1 | 116582 | -452634 | -10 | -9 | 116582 | -1452634
1 | 30 | 4 | 1 | 10.8489 | 0 | 42.3304 | 28.6385 | 0 | 0 | 25.2703 | 17.3638 | 0 | 0 | 0 | 4.8 | 129.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10657.6 | 0 | 10657.6 | 127549 | -462050 | -11 | -10 | 127549 | -1462050
1 | 30 | 5 | 1 | 11.8202 | 0 | 44.8242 | 28.0192 | 0 | 0 | 25.2706 | 17.5105 | 0 | 0 | 0 | 4.8 | 132.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11831.9 | 0 | 11831.9 | 118450 | -438282 | -12 | -12 | 118450 | -1438282
1 | 30 | 6 | 1 | 24.3093 | 0 | 69.9783 | 28.973 | 0 | 0 | 25.2776 | 17.5105 | 0 | 0 | 0 | 4.8 | 170.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28681.9 | 0 | 28681.9 | 172859 | -456115 | -14 | -13 | 172859 | -1456115
1 | 30 | 7 | 1 | 49.0171 | 0 | 140.608 | 94.9552 | 0 | 0 | 25.2856 | 20.5776 | 0 | 0 | 0 | 3.2 | 333.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84932.7 | 0 | 84932.7 | 302658 | -1685410 | -12 | -11 | 302658 | -2685410
1 | 30 | 8 | 1 | 50.0836 | 0 | 168.222 | 85.0892 | 0 | 0 | 25.25 | 19.8197 | 0 | 0 | 0 | 0.8 | 349.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103146 | 0 | 103146 | 365388 | -1532540 | -10 | -9 | 365388 | -2532540
1 | 30 | 9 | 1 | 41.6284 | 0 | 173.795 | 69.4284 | 0 | 0 | 25.2136 | 19.1953 | 0 | 0 | 0 | 0 | 329.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142747 | 0 | 142747 | 385756 | -1269010 | -8 | -7 | 385756 | -2269010
1 | 30 | 10 | 1 | 41.4626 | 0 | 172.186 | 62.2158 | 0 | 0 | 25.2076 | 19.0363 | 0 | 0 | 0 | 0 | 320.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167968 | 0 | 167968 | 384111 | -1135870 | -4 | -3 | 384111 | -2135870
1 | 30 | 11 | 1 | 41.4274 | 0 | 163.102 | 58.6929 | 0 | 0 | 25.2074 | 19.0363 | 0 | 0 | 0 | 0 | 307.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171563 | 0 | 171563 | 365606 | -1073320 | -1 | 0 | 365606 | -2073320
1 | 30 | 12 | 1 | 40.814 | 0 | 149.692 | 50.8507 | 0 | 0 | 25.2124 | 19.0363 | 0 | 0 | 0 | 0 | 285.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171561 | 0 | 171561 | 339387 | -899423 | 2 | 4 | 339387 | -1899423
1 | 30 | 13 | 1 | 39.858 | 0 | 150.207 | 48.623 | 0 | 0 | 25.2137 | 19.0363 | 0 | 0 | 0 | 0 | 282.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171559 | 0 | 171559 | 340351 | -865688 | 3 | 6 | 340351 | -1865688
1 | 30 | 14 | 1 | 41.326 | 0 | 165.698 | 42.9382 | 0 | 0 | 25.219 | 19.0363 | 0 | 0 | 0 | 0 | 294.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171556 | 0 | 171556 | 373680 | -802936 | 5 | 7 | 373680 | -1802936
1 | 30 | 15 | 1 | 40.7035 | 0 | 172.702 | 41.0839 | 0 | 0 | 25.2295 | 19.0363 | 0 | 0 | 0 | 0 | 298.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169337 | 0 | 169337 | 393063 | -766434 | 6 | 9 | 393063 | -1766434
1 | 30 | 16 | 1 | 41.1332 | 0 | 173.986 | 43.0216 | 0 | 0 | 25.2286 | 19.0363 | 0 | 0 | 0 | 0 | 302.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153940 | 0 | 153940 | 396682 | -800667 | 4 | 7 | 396682 | -1800667
1 | 30 | 17 | 1 | 43.4454 | 0 | 169.782 | 49.2158 | 0 | 0 | 25.2182 | 19.0363 | 0 | 0 | 0 | 2.4 | 309.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125649 | 0 | 125649 | 387143 | -907232 | 2 | 4 | 387143 | -1907232
1 | 30 | 18 | 1 | 49.5225 | 0 | 152.497 | 57.8762 | 0 | 0 | 25.2103 | 19.0363 | 0 | 0 | 0 | 6.4 | 310.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94216.6 | 0 | 94216.6 | 366978 | -1033080 | 0 | 2 | 366978 | -2033080
1 | 30 | 19 | 1 | 34.11 | 0 | 93.4203 | 65.6699 | 0 | 0 | 25.2164 | 19.0459 | 0 | 0 | 0 | 7.2 | 244.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58316.9 | 0 | 58316.9 | 303801 | -1042020 | 1 | 3 | 303801 | -2042020
1 | 30 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 14.6624 | 0 | 5.9734 | 17.5105 | 0 | 0 | 0 | 7.2 | 132.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41710.9 | 0 | 41710.9 | 200790 | -38161.3 | 2 | 3 | 200790 | -1038161.3
1 | 30 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.0937 | 0 | 5.9173 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37014.4 | 0 | 37014.4 | 166967 | -142177 | 2 | 4 | 166967 | -1142177
1 | 30 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.1497 | 0 | 5.9047 | 17.5105 | 0 | 0 | 0 | 7.2 | 104.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22704.6 | 0 | 22704.6 | 151467 | -202666 | 3 | 5 | 151467 | -1202666
1 | 30 | 23 | 1 | 11.1963 | 0 | 44.3342 | 14.1762 | 0 | 0 | 12.5816 | 17.5105 | 0 | 0 | 0 | 6.4 | 106.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12204.1 | 0 | 12204.1 | 138787 | -239987 | 4 | 6 | 138787 | -1239987
1 | 30 | 24 | 1 | 10.3176 | 0 | 42.5403 | 15.5501 | 0 | 0 | 14.6562 | 17.5105 | 0 | 0 | 0 | 5.6 | 106.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10617.7 | 0 | 10617.7 | 133706 | -263106 | 5 | 7 | 133706 | -1263106
1 | 31 | 1 | 2 | 10.424 | 0 | 42.3304 | 16.1614 | 0 | 0 | 15.6319 | 17.3638 | 0 | 0 | 0 | 4.8 | 106.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10621.8 | 0 | 10621.8 | 132003 | -275270 | 6 | 7 | 132003 | -1275270
1 | 31 | 2 | 2 | 10.424 | 0 | 42.3304 | 16.456 | 0 | 0 | 15.5661 | 17.3638 | 0 | 0 | 0 | 4.8 | 106.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10625 | 0 | 10625 | 131390 | -283413 | 7 | 8 | 131390 | -1283413
1 | 31 | 3 | 2 | 10.424 | 0 | 42.3304 | 16.8727 | 0 | 0 | 16.3361 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10627.8 | 0 | 10627.8 | 130170 | -289574 | 7 | 8 | 130170 | -1289574
1 | 31 | 4 | 2 | 10.424 | 0 | 42.3304 | 17.1654 | 0 | 0 | 16.9026 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10630.4 | 0 | 10630.4 | 129493 | -294744 | 8 | 9 | 129493 | -1294744
1 | 31 | 5 | 2 | 11.8202 | 0 | 44.8242 | 17.9351 | 0 | 0 | 18.2881 | 17.5105 | 0 | 0 | 0 | 4.8 | 115.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11806.4 | 0 | 11806.4 | 131771 | -304460 | 8 | 9 | 131771 | -1304460
1 | 31 | 6 | 2 | 24.3093 | 0 | 69.9783 | 15.9015 | 0 | 0 | 14.474 | 17.5105 | 0 | 0 | 0 | 4.8 | 146.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28657.9 | 0 | 28657.9 | 178458 | -267382 | 9 | 10 | 178458 | -1267382
1 | 31 | 7 | 2 | 49.0171 | 0 | 140.608 | 72.438 | 0 | 0 | 25.212 | 19.6739 | 0 | 0 | 0 | 3.2 | 310.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84910.1 | 0 | 84910.1 | 313383 | -1234670 | 10 | 11 | 313383 | -2234670
1 | 31 | 8 | 2 | 52.578 | 0 | 168.222 | 61.3879 | 0 | 0 | 25.2073 | 19.3224 | 0 | 0 | 0 | 0.8 | 327.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103123 | 0 | 103123 | 375740 | -1082440 | 11 | 12 | 375740 | -2082440
1 | 31 | 9 | 2 | 45.8582 | 0 | 173.795 | 51.6242 | 0 | 0 | 25.2138 | 19.1081 | 0 | 0 | 0 | 0 | 315.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142732 | 0 | 142732 | 395071 | -920170 | 12 | 13 | 395071 | -1920170
1 | 31 | 10 | 2 | 40.778 | 0 | 172.186 | 47.4793 | 0 | 0 | 25.2216 | 19.0363 | 0 | 0 | 0 | 0 | 304.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167952 | 0 | 167952 | 393244 | -839959 | 13 | 15 | 393244 | -1839959
1 | 31 | 11 | 2 | 41.2378 | 0 | 163.102 | 42.6853 | 0 | 0 | 25.2314 | 19.0363 | 0 | 0 | 0 | 0 | 291.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171547 | 0 | 171547 | 374898 | -747611 | 15 | 17 | 374898 | -1747611
1 | 31 | 12 | 2 | 40.8001 | 0 | 149.692 | 37.7684 | 0 | 0 | 25.2525 | 19.0363 | 0 | 0 | 0 | 0 | 272.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171545 | 0 | 171545 | 356398 | -636752 | 17 | 19 | 356398 | -1636752
1 | 31 | 13 | 2 | 39.8552 | 0 | 150.207 | 34.9074 | 0 | 0 | 25.2614 | 19.0363 | 0 | 0 | 0 | 0 | 269.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171543 | 0 | 171543 | 348979 | -592762 | 18 | 21 | 348979 | -1592762
1 | 31 | 14 | 2 | 41.3361 | 0 | 165.698 | 28.6251 | 0 | 0 | 25.2704 | 19.0363 | 0 | 0 | 0 | 0 | 279.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171540 | 0 | 171540 | 382226 | -523066 | 20 | 22 | 382226 | -1523066
1 | 31 | 15 | 2 | 40.7174 | 0 | 172.702 | 0 | 25.4087 | 0 | 6.276 | 19.0363 | 0 | 0 | 0 | 0 | 264.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169321 | 0 | 169321 | 400999 | -481217 | 21 | 24 | 400999 | -1481217
1 | 31 | 16 | 2 | 40.612 | 0 | 173.986 | 26.9611 | 0 | 0 | 25.2746 | 19.0363 | 0 | 0 | 0 | 0 | 285.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153924 | 0 | 153924 | 404164 | -515452 | 21 | 23 | 404164 | -1515452
1 | 31 | 17 | 2 | 43.6893 | 0 | 169.782 | 30.7255 | 0 | 0 | 25.2704 | 19.0363 | 0 | 0 | 0 | 2.4 | 290.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125633 | 0 | 125633 | 397236 | -562831 | 21 | 23 | 397236 | -1562831
1 | 31 | 18 | 2 | 49.7836 | 0 | 152.497 | 36.8763 | 0 | 0 | 25.2628 | 19.0363 | 0 | 0 | 0 | 6.4 | 289.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94199.9 | 0 | 94199.9 | 387220 | -629817 | 20 | 22 | 387220 | -1629817
1 | 31 | 19 | 2 | 34.11 | 0 | 93.4203 | 42.9897 | 0 | 0 | 25.2654 | 19.0363 | 0 | 0 | 0 | 7.2 | 222.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58300.1 | 0 | 58300.1 | 309454 | -676478 | 19 | 20 | 309454 | -1676478
1 | 31 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 13.9002 | 0 | 5.9429 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41694.6 | 0 | 41694.6 | 176371 | -11898.2 | 18 | 19 | 176371 | -1011898.2
1 | 31 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 14.0083 | 0 | 5.9467 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36998.9 | 0 | 36998.9 | 182002 | -33135.3 | 17 | 18 | 182002 | -1033135.3
1 | 31 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.1909 | 0 | 5.9256 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22685.1 | 0 | 22685.1 | 163232 | -62681.9 | 16 | 17 | 163232 | -1062681.9
1 | 31 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.0876 | 0 | 5.9096 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12182.6 | 0 | 12182.6 | 148872 | -87298.2 | 15 | 16 | 148872 | -1087298.2
1 | 31 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.4552 | 0 | 5.9037 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10595.4 | 0 | 10595.4 | 142503 | -114541 | 14 | 15 | 142503 | -1114541
2 | 1 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.1223 | 0 | 5.9015 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.7 | 0 | 11033.7 | 139978 | -147244 | 12 | 13 | 139978 | -1147244
2 | 1 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9146 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.6 | 0 | 11036.6 | 138426 | -165123 | 11 | 12 | 138426 | -1165123
2 | 1 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.6968 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.4 | 0 | 11039.4 | 137130 | -187398 | 9 | 11 | 137130 | -1187398
2 | 1 | 4 | 3 | 10.8489 | 0 | 42.3304 | 11.9907 | 0 | 0 | 9.4495 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.7834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.8 | 0 | 11041.8 | 140187 | -206851 | 8 | 9 | 140187 | -1206851
2 | 1 | 5 | 3 | 11.8202 | 0 | 44.8242 | 12.7022 | 0 | 0 | 10.1066 | 17.5105 | 0 | 0 | 0 | 4.8 | 101.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12271.8 | 0 | 12271.8 | 137768 | -210273 | 7 | 8 | 137768 | -1210273
2 | 1 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.1841 | 0 | 5.9529 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29897.3 | 0 | 29897.3 | 187813 | -199934 | 6 | 7 | 187813 | -1199934
2 | 1 | 7 | 3 | 49.0171 | 0 | 140.608 | 63.7363 | 0 | 0 | 25.2106 | 19.3088 | 0 | 0 | 0 | 1.2 | 299.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88732.9 | 0 | 88732.9 | 316831 | -1136890 | 5 | 6 | 316831 | -2136890
2 | 1 | 8 | 3 | 52.5645 | 0 | 168.222 | 59.148 | 0 | 0 | 25.2073 | 19.1439 | 0 | 0 | 0 | 0 | 324.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107783 | 0 | 107783 | 378867 | -1076740 | 5 | 6 | 378867 | -2076740
2 | 1 | 9 | 3 | 44.7097 | 0 | 173.795 | 52.8494 | 0 | 0 | 25.2102 | 19.0703 | 0 | 0 | 0 | 0 | 315.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149221 | 0 | 149221 | 398224 | -971093 | 5 | 6 | 398224 | -1971093
2 | 1 | 10 | 3 | 41.9572 | 0 | 172.186 | 51.7983 | 0 | 0 | 25.2137 | 19.0363 | 0 | 0 | 0 | 0 | 310.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175600 | 0 | 175600 | 396007 | -933426 | 7 | 8 | 396007 | -1933426
2 | 1 | 11 | 3 | 42.5911 | 0 | 163.102 | 55.4681 | 0 | 0 | 25.2145 | 19.0363 | 0 | 0 | 0 | 0 | 305.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179362 | 0 | 179362 | 382410 | -964456 | 7 | 8 | 382410 | -1964456
2 | 1 | 12 | 3 | 41.3783 | 0 | 149.692 | 51.8792 | 0 | 0 | 25.2255 | 19.0363 | 0 | 0 | 0 | 0 | 287.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179361 | 0 | 179361 | 358276 | -871061 | 8 | 9 | 358276 | -1871061
2 | 1 | 13 | 3 | 39.9353 | 0 | 150.207 | 51.7379 | 0 | 0 | 25.2232 | 19.0363 | 0 | 0 | 0 | 0 | 286.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179359 | 0 | 179359 | 350532 | -881903 | 8 | 9 | 350532 | -1881903
2 | 1 | 14 | 3 | 42.2386 | 0 | 165.698 | 44.4546 | 0 | 0 | 25.221 | 19.0363 | 0 | 0 | 0 | 0 | 296.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179356 | 0 | 179356 | 383549 | -814621 | 9 | 10 | 383549 | -1814621
2 | 1 | 15 | 3 | 41.4568 | 0 | 172.702 | 42.9397 | 0 | 0 | 25.2241 | 19.0363 | 0 | 0 | 0 | 0 | 301.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177037 | 0 | 177037 | 402373 | -802117 | 9 | 10 | 402373 | -1802117
2 | 1 | 16 | 3 | 42.0029 | 0 | 173.986 | 43.2209 | 0 | 0 | 25.2265 | 19.0363 | 0 | 0 | 0 | 0 | 303.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160933 | 0 | 160933 | 405519 | -798260 | 10 | 11 | 405519 | -1798260
2 | 1 | 17 | 3 | 50.243 | 0 | 169.782 | 46.1145 | 0 | 0 | 25.2254 | 19.0363 | 0 | 0 | 0 | 0 | 310.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131343 | 0 | 131343 | 395586 | -832473 | 9 | 11 | 395586 | -1832473
2 | 1 | 18 | 3 | 49.7227 | 0 | 152.497 | 51.0995 | 0 | 0 | 25.2255 | 19.0363 | 0 | 0 | 0 | 2 | 299.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98467.4 | 0 | 98467.4 | 371851 | -878132 | 10 | 11 | 371851 | -1878132
2 | 1 | 19 | 3 | 34.11 | 0 | 93.4203 | 55.9727 | 0 | 0 | 25.2335 | 19.0363 | 0 | 0 | 0 | 5.6 | 233.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60919.4 | 0 | 60919.4 | 302423 | -882929 | 9 | 11 | 302423 | -1882929
2 | 1 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 15.8874 | 0 | 6.0049 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43551.2 | 0 | 43551.2 | 210700 | -19393.2 | 9 | 11 | 210700 | -1019393.2
2 | 1 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.2235 | 0 | 5.9341 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38639.8 | 0 | 38639.8 | 177147 | -87821.9 | 9 | 10 | 177147 | -1087821.9
2 | 1 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 11.9859 | 0 | 5.9135 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23671.3 | 0 | 23671.3 | 160863 | -139490 | 9 | 10 | 160863 | -1139490
2 | 1 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.0628 | 0 | 5.9032 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12687.9 | 0 | 12687.9 | 147569 | -173966 | 9 | 10 | 147569 | -1173966
2 | 1 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.6069 | 0 | 5.9073 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.3 | 0 | 11028.3 | 151880 | -196382 | 9 | 10 | 151880 | -1196382
2 | 2 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.0162 | 0 | 5.9011 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11032.6 | 0 | 11032.6 | 139915 | -178993 | 9 | 10 | 139915 | -1178993
2 | 2 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.3249 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11035.9 | 0 | 11035.9 | 143351 | -197786 | 10 | 11 | 143351 | -1197786
2 | 2 | 3 | 4 | 10.73 | 0 | 42.3304 | 11.3539 | 0 | 0 | 8.9532 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038 | 0 | 11038 | 137370 | -198006 | 11 | 12 | 137370 | -1198006
2 | 2 | 4 | 4 | 10.73 | 0 | 42.3304 | 12.6047 | 0 | 0 | 10.1023 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040 | 0 | 11040 | 141389 | -228215 | 11 | 12 | 141389 | -1228215
2 | 2 | 5 | 4 | 11.8202 | 0 | 44.8242 | 13.7325 | 0 | 0 | 11.227 | 17.5105 | 0 | 0 | 0 | 4.8 | 103.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12269.3 | 0 | 12269.3 | 138447 | -225941 | 11 | 13 | 138447 | -1225941
2 | 2 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 13.821 | 0 | 5.946 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29895.1 | 0 | 29895.1 | 185138 | -190549 | 11 | 13 | 185138 | -1190549
2 | 2 | 7 | 4 | 49.0171 | 0 | 140.608 | 62.9358 | 0 | 0 | 25.2074 | 19.3639 | 0 | 0 | 0 | 1.2 | 298.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88731.1 | 0 | 88731.1 | 317828 | -1096370 | 11 | 13 | 317828 | -2096370
2 | 2 | 8 | 4 | 52.0409 | 0 | 168.222 | 54.9814 | 0 | 0 | 25.2103 | 19.1605 | 0 | 0 | 0 | 0 | 319.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107780 | 0 | 107780 | 379732 | -980488 | 11 | 14 | 379732 | -1980488
2 | 2 | 9 | 4 | 43.473 | 0 | 173.795 | 47.6483 | 0 | 0 | 25.2199 | 19.0567 | 0 | 0 | 0 | 0 | 309.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149217 | 0 | 149217 | 399360 | -857148 | 13 | 14 | 399360 | -1857148
2 | 2 | 10 | 4 | 41.6908 | 0 | 172.186 | 44.8722 | 0 | 0 | 25.2283 | 19.0363 | 0 | 0 | 0 | 0 | 303.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175595 | 0 | 175595 | 397047 | -798472 | 15 | 16 | 397047 | -1798472
2 | 2 | 11 | 4 | 42.0339 | 0 | 163.102 | 44.9508 | 0 | 0 | 25.235 | 19.0363 | 0 | 0 | 0 | 0 | 294.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179357 | 0 | 179357 | 378677 | -776041 | 16 | 18 | 378677 | -1776041
2 | 2 | 12 | 4 | 41.2897 | 0 | 149.692 | 41.2485 | 0 | 0 | 25.2531 | 19.0363 | 0 | 0 | 0 | 0 | 276.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179356 | 0 | 179356 | 365769 | -685103 | 18 | 20 | 365769 | -1685103
2 | 2 | 13 | 4 | 39.904 | 0 | 150.207 | 39.4515 | 0 | 0 | 25.2547 | 19.0363 | 0 | 0 | 0 | 0 | 273.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179354 | 0 | 179354 | 352112 | -668601 | 19 | 20 | 352112 | -1668601
2 | 2 | 14 | 4 | 42.0933 | 0 | 165.698 | 33.7686 | 0 | 0 | 25.2523 | 19.0363 | 0 | 0 | 0 | 0 | 285.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179351 | 0 | 179351 | 385161 | -614378 | 19 | 20 | 385161 | -1614378
2 | 2 | 15 | 4 | 41.3679 | 0 | 172.702 | 30.6518 | 0 | 0 | 25.2542 | 19.0363 | 0 | 0 | 0 | 0 | 289.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177031 | 0 | 177031 | 403836 | -584106 | 20 | 21 | 403836 | -1584106
2 | 2 | 16 | 4 | 41.6773 | 0 | 173.986 | 32.1594 | 0 | 0 | 25.2514 | 19.0363 | 0 | 0 | 0 | 0 | 292.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160927 | 0 | 160927 | 406854 | -610130 | 19 | 20 | 406854 | -1610130
2 | 2 | 17 | 4 | 50.243 | 0 | 169.782 | 34.7716 | 0 | 0 | 25.2563 | 19.0363 | 0 | 0 | 0 | 0 | 299.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131337 | 0 | 131337 | 397285 | -634131 | 19 | 20 | 397285 | -1634131
2 | 2 | 18 | 4 | 49.7131 | 0 | 152.497 | 39.4921 | 0 | 0 | 25.2533 | 19.0363 | 0 | 0 | 0 | 2 | 287.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98461.5 | 0 | 98461.5 | 385795 | -681693 | 19 | 20 | 385795 | -1681693
2 | 2 | 19 | 4 | 34.11 | 0 | 93.4203 | 43.6962 | 0 | 0 | 25.2654 | 19.0363 | 0 | 0 | 0 | 5.6 | 221.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60913.2 | 0 | 60913.2 | 308474 | -697181 | 19 | 19 | 308474 | -1697181
2 | 2 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.0817 | 0 | 5.9468 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43544.9 | 0 | 43544.9 | 178460 | -12121.9 | 18 | 19 | 178460 | -1012121.9
2 | 2 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.4142 | 0 | 5.9544 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38633.4 | 0 | 38633.4 | 184651 | -32223.2 | 18 | 19 | 184651 | -1032223.2
2 | 2 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.4417 | 0 | 5.9298 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23662.3 | 0 | 23662.3 | 165962 | -56947.2 | 18 | 19 | 165962 | -1056947.2
2 | 2 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.4675 | 0 | 5.9135 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.8221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12677.4 | 0 | 12677.4 | 151718 | -77180.9 | 18 | 19 | 151718 | -1077180.9
2 | 2 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 12.0618 | 0 | 5.9082 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.9384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11016.7 | 0 | 11016.7 | 145391 | -94322.2 | 19 | 20 | 145391 | -1094322.2
2 | 3 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.5636 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020 | 0 | 11020 | 143064 | -111812 | 19 | 20 | 143064 | -1111812
2 | 3 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.2193 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.6 | 0 | 11022.6 | 141594 | -141268 | 18 | 19 | 141594 | -1141268
2 | 3 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9868 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.7 | 0 | 11024.7 | 140226 | -156076 | 15 | 16 | 140226 | -1156076
2 | 3 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.8113 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.4 | 0 | 11027.4 | 139055 | -182516 | 13 | 14 | 139055 | -1182516
2 | 3 | 5 | 5 | 11.8202 | 0 | 44.8242 | 11.8176 | 0 | 0 | 9.2326 | 17.5105 | 0 | 0 | 0 | 4.8 | 100.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12257.6 | 0 | 12257.6 | 140604 | -212742 | 9 | 10 | 140604 | -1212742
2 | 3 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.8144 | 0 | 5.9454 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29883.4 | 0 | 29883.4 | 186653 | -207702 | 4 | 5 | 186653 | -1207702
2 | 3 | 7 | 5 | 49.0171 | 0 | 140.608 | 65.8038 | 0 | 0 | 25.2167 | 19.2863 | 0 | 0 | 0 | 1.2 | 301.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88719.6 | 0 | 88719.6 | 317944 | -1202780 | -2 | -1 | 317944 | -2202780
2 | 3 | 8 | 5 | 49.0028 | 0 | 168.222 | 60.6677 | 0 | 0 | 25.2083 | 19.1485 | 0 | 0 | 0 | 0 | 322.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107770 | 0 | 107770 | 379954 | -1128090 | -2 | 0 | 379954 | -2128090
2 | 3 | 9 | 5 | 41.6178 | 0 | 173.795 | 51.8276 | 0 | 0 | 25.2113 | 19.0363 | 0 | 0 | 0 | 0 | 311.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149210 | 0 | 149210 | 399604 | -967579 | 0 | 1 | 399604 | -1967579
2 | 3 | 10 | 5 | 41.1185 | 0 | 172.186 | 49.3551 | 0 | 0 | 25.2152 | 19.0363 | 0 | 0 | 0 | 0 | 306.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175590 | 0 | 175590 | 397153 | -913459 | 1 | 3 | 397153 | -1913459
2 | 3 | 11 | 5 | 41.26 | 0 | 163.102 | 48.5499 | 0 | 0 | 25.2165 | 19.0363 | 0 | 0 | 0 | 0 | 297.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 378125 | -905470 | 2 | 4 | 378125 | -1905470
2 | 3 | 12 | 5 | 40.8009 | 0 | 149.692 | 42.3624 | 0 | 0 | 25.2257 | 19.0363 | 0 | 0 | 0 | 0 | 277.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 351143 | -792684 | 3 | 5 | 351143 | -1792684
2 | 3 | 13 | 5 | 39.856 | 0 | 150.207 | 40.5706 | 0 | 0 | 6.6849 | 19.0363 | 0 | 0 | 0 | 0 | 256.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179351 | 0 | 179351 | 351438 | -768989 | 5 | 7 | 351438 | -1768989
2 | 3 | 14 | 5 | 41.3393 | 0 | 165.698 | 36.0795 | 0 | 0 | 6.2309 | 19.0363 | 0 | 0 | 0 | 0 | 268.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179348 | 0 | 179348 | 384288 | -716437 | 6 | 8 | 384288 | -1716437
2 | 3 | 15 | 5 | 40.8126 | 0 | 172.702 | 36.873 | 0 | 0 | 6.236 | 19.0363 | 0 | 0 | 0 | 0 | 275.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177029 | 0 | 177029 | 403164 | -728923 | 5 | 7 | 403164 | -1728923
2 | 3 | 16 | 5 | 41.3374 | 0 | 173.986 | 38.8798 | 0 | 0 | 6.2334 | 19.0363 | 0 | 0 | 0 | 0 | 279.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160925 | 0 | 160925 | 406144 | -764881 | 4 | 6 | 406144 | -1764881
2 | 3 | 17 | 5 | 42.7231 | 0 | 169.782 | 43.6239 | 0 | 0 | 6.2223 | 19.0363 | 0 | 0 | 0 | 0 | 281.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131336 | 0 | 131336 | 396069 | -854666 | 2 | 4 | 396069 | -1854666
2 | 3 | 18 | 5 | 49.3079 | 0 | 152.497 | 51.9324 | 0 | 0 | 6.208 | 19.0363 | 0 | 0 | 0 | 2 | 280.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98461 | 0 | 98461 | 376155 | -1013050 | -2 | -1 | 376155 | -2013050
2 | 3 | 19 | 5 | 34.11 | 0 | 93.4203 | 59.4776 | 0 | 0 | 25.2211 | 19.0363 | 0 | 0 | 0 | 5.6 | 236.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60913.6 | 0 | 60913.6 | 314969 | -991704 | 1 | 2 | 314969 | -1991704
2 | 3 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 15.3075 | 0 | 5.9933 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43546.1 | 0 | 43546.1 | 209820 | -19523.8 | -3 | -2 | 209820 | -1019523.8
2 | 3 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.7343 | 0 | 5.9286 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38633.9 | 0 | 38633.9 | 176699 | -122289 | -2 | -1 | 176699 | -1122289
2 | 3 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.069 | 0 | 5.9319 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23665.7 | 0 | 23665.7 | 176922 | -188613 | -4 | -3 | 176922 | -1188613
2 | 3 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.4177 | 0 | 5.9049 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.7636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12682.7 | 0 | 12682.7 | 147066 | -188231 | -6 | -5 | 147066 | -1188231
2 | 3 | 24 | 5 | 10.3176 | 0 | 42.5403 | 13.1955 | 0 | 0 | 10.3758 | 17.5105 | 0 | 0 | 0 | 5.6 | 99.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.5 | 0 | 11023.5 | 148914 | -230708 | -7 | -6 | 148914 | -1230708
2 | 4 | 1 | 6 | 6.3817 | 0 | 42.7453 | 14.3943 | 0 | 0 | 11.663 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.9 | 0 | 11026.9 | 138620 | -236599 | -7 | -6 | 138620 | -1236599
2 | 4 | 2 | 6 | 6.3817 | 0 | 42.7453 | 17.5832 | 0 | 0 | 15.8303 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.7 | 0 | 11029.7 | 165651 | -306325 | -10 | -9 | 165651 | -1306325
2 | 4 | 3 | 6 | 6.3817 | 0 | 42.7453 | 16.4296 | 0 | 0 | 13.9655 | 17.3638 | 0 | 0 | 0 | 4.8 | 101.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11032.7 | 0 | 11032.7 | 135291 | -260399 | -11 | -10 | 135291 | -1260399
2 | 4 | 4 | 6 | 6.3817 | 0 | 42.7453 | 17.7932 | 0 | 0 | 16.1408 | 17.3638 | 0 | 0 | 0 | 4.8 | 105.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.5 | 0 | 11036.5 | 147310 | -300646 | -12 | -12 | 147310 | -1300646
2 | 4 | 5 | 6 | 6.3817 | 0 | 42.7453 | 17.5114 | 0 | 0 | 15.6733 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.4 | 0 | 11038.4 | 132948 | -281025 | -11 | -10 | 132948 | -1281025
2 | 4 | 6 | 6 | 6.3817 | 0 | 42.7453 | 18.9718 | 0 | 0 | 18.1975 | 17.3638 | 0 | 0 | 0 | 3.6 | 107.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040.6 | 0 | 11040.6 | 139043 | -313489 | -13 | -13 | 139043 | -1313489
2 | 4 | 7 | 6 | 6.3817 | 0 | 42.7453 | 19.2016 | 0 | 0 | 18.6137 | 17.3638 | 0 | 0 | 0 | 1.2 | 105.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.6 | 0 | 11042.6 | 130768 | -307791 | -13 | -13 | 130768 | -1307791
2 | 4 | 8 | 6 | 5.952 | 0 | 42.7453 | 88.8739 | 0 | 0 | 25.2093 | 20.1714 | 0 | 0 | 0 | 0 | 182.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.4 | 0 | 11044.4 | 119939 | -1407170 | -15 | -14 | 119939 | -2407170
2 | 4 | 9 | 6 | 5.1534 | 0 | 42.7453 | 77.3261 | 0 | 0 | 25.2097 | 19.3713 | 0 | 0 | 0 | 0 | 169.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045.8 | 0 | 11045.8 | 119357 | -1186540 | -9 | -8 | 119357 | -2186540
2 | 4 | 10 | 6 | 5.5565 | 0 | 42.7453 | 64.1436 | 0 | 0 | 25.2187 | 18.9658 | 0 | 0 | 0 | 0 | 156.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.9 | 0 | 11029.9 | 118758 | -1000320 | -5 | -4 | 118758 | -2000320
2 | 4 | 11 | 6 | 5.4771 | 0 | 42.7453 | 57.8052 | 0 | 0 | 25.2245 | 18.8896 | 0 | 0 | 0 | 0 | 150.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.3 | 0 | 11027.3 | 118234 | -908960 | -1 | 0 | 118234 | -1908960
2 | 4 | 12 | 6 | 5.478 | 0 | 42.7453 | 52.2864 | 0 | 0 | 25.2291 | 18.8896 | 0 | 0 | 0 | 0 | 144.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.1 | 0 | 11025.1 | 117769 | -844597 | 1 | 3 | 117769 | -1844597
2 | 4 | 13 | 6 | 5.4783 | 0 | 42.7453 | 47.95 | 0 | 0 | 7.4439 | 18.8896 | 0 | 0 | 0 | 0 | 122.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.9 | 0 | 11023.9 | 117398 | -779806 | 6 | 8 | 117398 | -1779806
2 | 4 | 14 | 6 | 5.4751 | 0 | 42.7453 | 42.0843 | 0 | 0 | 6.2393 | 18.8896 | 0 | 0 | 0 | 0 | 115.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.1 | 0 | 11023.1 | 117165 | -706952 | 10 | 13 | 117165 | -1706952
2 | 4 | 15 | 6 | 5.4774 | 0 | 42.7453 | 0 | 13.59 | 0 | 5.9355 | 17.3638 | 0 | 0 | 0 | 0 | 85.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.7 | 0 | 11022.7 | 173984 | -19523.7 | 12 | 15 | 173984 | -1019523.7
2 | 4 | 16 | 6 | 5.4804 | 0 | 42.7453 | 0 | 11.2644 | 0 | 5.9016 | 17.3638 | 0 | 0 | 0 | 0 | 82.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.3 | 0 | 11022.3 | 137078 | -50045.3 | 14 | 17 | 137078 | -1050045.3
2 | 4 | 17 | 6 | 7.6042 | 0 | 42.7453 | 0 | 11.5419 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 0 | 85.1591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.7 | 0 | 11027.7 | 141766 | -79293.2 | 12 | 14 | 141766 | -1079293.2
2 | 4 | 18 | 6 | 8.7827 | 0 | 42.7453 | 0 | 10.8348 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 2 | 87.6254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.7 | 0 | 11031.7 | 130539 | -99863.1 | 15 | 18 | 130539 | -1099863.1
2 | 4 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.4102 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.8142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.3 | 0 | 11034.3 | 129083 | -133462 | 15 | 18 | 129083 | -1133462
2 | 4 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.0939 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.1 | 0 | 11037.1 | 127998 | -164043 | 15 | 17 | 127998 | -1164043
2 | 4 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.9659 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 91.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.1 | 0 | 11039.1 | 127377 | -179562 | 14 | 17 | 127377 | -1179562
2 | 4 | 22 | 6 | 8.7973 | 0 | 42.7453 | 11.3663 | 0 | 0 | 8.7778 | 17.3638 | 0 | 0 | 0 | 7.2 | 96.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.1 | 0 | 11042.1 | 127013 | -204860 | 15 | 15 | 127013 | -1204860
2 | 4 | 23 | 6 | 8.7973 | 0 | 42.7453 | 12.0134 | 0 | 0 | 9.3851 | 17.3638 | 0 | 0 | 0 | 6.4 | 96.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.6 | 0 | 11044.6 | 126299 | -212746 | 14 | 15 | 126299 | -1212746
2 | 4 | 24 | 6 | 8.7973 | 0 | 42.7453 | 12.6495 | 0 | 0 | 10.0205 | 17.3638 | 0 | 0 | 0 | 5.6 | 97.1763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047 | 0 | 11047 | 126923 | -222831 | 14 | 15 | 126923 | -1222831
2 | 5 | 1 | 7 | 5.1054 | 0 | 42.7453 | 13.1838 | 0 | 0 | 10.3391 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.5374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.03 | 0 | 4119.03 | 125211 | -232700 | 14 | 14 | 125211 | -1232700
2 | 5 | 2 | 7 | 5.1054 | 0 | 42.7453 | 14.0738 | 0 | 0 | 11.1571 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.2453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.39 | 0 | 4121.39 | 124703 | -249927 | 13 | 14 | 124703 | -1249927
2 | 5 | 3 | 7 | 5.1054 | 0 | 42.7453 | 14.4463 | 0 | 0 | 11.6399 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.76 | 0 | 4123.76 | 124298 | -259215 | 13 | 14 | 124298 | -1259215
2 | 5 | 4 | 7 | 5.1054 | 0 | 42.7453 | 15.2623 | 0 | 0 | 12.7454 | 17.3638 | 0 | 0 | 0 | 4.8 | 98.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.93 | 0 | 4125.93 | 123907 | -268684 | 13 | 14 | 123907 | -1268684
2 | 5 | 5 | 7 | 5.1054 | 0 | 42.7453 | 15.4878 | 0 | 0 | 13.0935 | 17.3638 | 0 | 0 | 0 | 4.8 | 98.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.2 | 0 | 4128.2 | 123636 | -275189 | 14 | 15 | 123636 | -1275189
2 | 5 | 6 | 7 | 5.1054 | 0 | 42.7453 | 15.436 | 0 | 0 | 13.0368 | 17.3638 | 0 | 0 | 0 | 3.6 | 97.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.3 | 0 | 4130.3 | 123326 | -272826 | 15 | 15 | 123326 | -1272826
2 | 5 | 7 | 7 | 5.1054 | 0 | 42.7453 | 16.4504 | 0 | 0 | 14.3344 | 17.3638 | 0 | 0 | 0 | 1.2 | 97.1992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.34 | 0 | 4132.34 | 131946 | -279745 | 15 | 16 | 131946 | -1279745
2 | 5 | 8 | 7 | 5.003 | 0 | 42.7453 | 14.4924 | 0 | 0 | 11.6233 | 17.3638 | 0 | 0 | 0 | 0 | 91.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.31 | 0 | 4134.31 | 122858 | -248758 | 17 | 18 | 122858 | -1248758
2 | 5 | 9 | 7 | 4.8848 | 0 | 42.7453 | 15.113 | 0 | 0 | 12.5991 | 17.3638 | 0 | 0 | 0 | 0 | 92.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.16 | 0 | 4136.16 | 128147 | -270127 | 17 | 18 | 128147 | -1270127
2 | 5 | 10 | 7 | 4.9197 | 0 | 42.7453 | 13.7231 | 0 | 0 | 10.9039 | 17.3638 | 0 | 0 | 0 | 0 | 89.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.33 | 0 | 4137.33 | 122709 | -235944 | 19 | 20 | 122709 | -1235944
2 | 5 | 11 | 7 | 4.5904 | 0 | 42.7453 | 13.2421 | 0 | 0 | 10.4107 | 17.3638 | 0 | 0 | 0 | 0 | 88.3522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.14 | 0 | 4139.14 | 126392 | -231828 | 20 | 21 | 126392 | -1231828
2 | 5 | 12 | 7 | 4.5722 | 0 | 42.7453 | 12.4134 | 0 | 0 | 9.6001 | 17.3638 | 0 | 0 | 0 | 0 | 86.6948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.66 | 0 | 4140.66 | 122724 | -210853 | 21 | 22 | 122724 | -1210853
2 | 5 | 13 | 7 | 4.5031 | 0 | 42.7453 | 12.1362 | 0 | 0 | 9.3456 | 17.3638 | 0 | 0 | 0 | 0 | 86.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.88 | 0 | 4141.88 | 125020 | -210810 | 21 | 22 | 125020 | -1210810
2 | 5 | 14 | 7 | 4.6114 | 0 | 42.7453 | 11.7479 | 0 | 0 | 8.9255 | 17.3638 | 0 | 0 | 0 | 0 | 85.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142.98 | 0 | 4142.98 | 122626 | -203694 | 21 | 23 | 122626 | -1203694
2 | 5 | 15 | 7 | 4.6409 | 0 | 42.7453 | 11.8978 | 0 | 0 | 6.2026 | 17.3638 | 0 | 0 | 0 | 0 | 82.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.02 | 0 | 4144.02 | 124023 | -209879 | 21 | 22 | 124023 | -1209879
2 | 5 | 16 | 7 | 4.9403 | 0 | 42.7453 | 12.425 | 0 | 0 | 5.8811 | 17.3638 | 0 | 0 | 0 | 0 | 83.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4145.04 | 0 | 4145.04 | 122363 | -219682 | 20 | 22 | 122363 | -1219682
2 | 5 | 17 | 7 | 5.7477 | 0 | 42.7453 | 13.6451 | 0 | 0 | 10.614 | 17.3638 | 0 | 0 | 0 | 0 | 90.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4146.03 | 0 | 4146.03 | 123007 | -241674 | 20 | 21 | 123007 | -1241674
2 | 5 | 18 | 7 | 6.6387 | 0 | 42.7453 | 14.4534 | 0 | 0 | 11.8033 | 17.3638 | 0 | 0 | 0 | 2 | 95.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.02 | 0 | 4147.02 | 121918 | -251982 | 18 | 20 | 121918 | -1251982
2 | 5 | 19 | 7 | 6.6633 | 0 | 42.7453 | 15.2146 | 0 | 0 | 12.7891 | 17.3638 | 0 | 0 | 0 | 5.6 | 100.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4148.01 | 0 | 4148.01 | 122491 | -266010 | 17 | 19 | 122491 | -1266010
2 | 5 | 20 | 7 | 6.6633 | 0 | 42.7453 | 15.6692 | 0 | 0 | 13.4404 | 17.3638 | 0 | 0 | 0 | 7.2 | 103.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149 | 0 | 4149 | 121505 | -273356 | 16 | 18 | 121505 | -1273356
2 | 5 | 21 | 7 | 6.6633 | 0 | 42.7453 | 16.3327 | 0 | 0 | 14.5467 | 17.3638 | 0 | 0 | 0 | 7.2 | 104.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149.96 | 0 | 4149.96 | 121192 | -286991 | 15 | 16 | 121192 | -1286991
2 | 5 | 22 | 7 | 6.6633 | 0 | 42.7453 | 16.6733 | 0 | 0 | 15.1799 | 17.3638 | 0 | 0 | 0 | 7.2 | 105.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4150.9 | 0 | 4150.9 | 121043 | -292751 | 15 | 16 | 121043 | -1292751
2 | 5 | 23 | 7 | 6.6633 | 0 | 42.7453 | 17.1446 | 0 | 0 | 15.9991 | 17.3638 | 0 | 0 | 0 | 6.4 | 106.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151.8 | 0 | 4151.8 | 121783 | -300914 | 14 | 16 | 121783 | -1300914
2 | 5 | 24 | 7 | 6.6633 | 0 | 42.7453 | 17.2341 | 0 | 0 | 16.209 | 17.3638 | 0 | 0 | 0 | 5.6 | 105.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4152.69 | 0 | 4152.69 | 120693 | -302077 | 14 | 16 | 120693 | -1302077
2 | 6 | 1 | 1 | 10.8489 | 0 | 42.3304 | 18.1619 | 0 | 0 | 18.98 | 17.3638 | 0 | 0 | 0 | 4.8 | 112.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11083.8 | 0 | 11083.8 | 121799 | -313332 | 14 | 15 | 121799 | -1313332
2 | 6 | 2 | 1 | 10.8489 | 0 | 42.3304 | 18.0862 | 0 | 0 | 18.2238 | 17.3638 | 0 | 0 | 0 | 4.8 | 111.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11084.7 | 0 | 11084.7 | 120829 | -314298 | 14 | 15 | 120829 | -1314298
2 | 6 | 3 | 1 | 10.8489 | 0 | 42.3304 | 18.3474 | 0 | 0 | 18.8107 | 17.3638 | 0 | 0 | 0 | 4.8 | 112.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11084.9 | 0 | 11084.9 | 120760 | -319645 | 14 | 15 | 120760 | -1319645
2 | 6 | 4 | 1 | 10.8489 | 0 | 42.3304 | 18.6701 | 0 | 0 | 19.5169 | 17.3638 | 0 | 0 | 0 | 4.8 | 113.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11085.5 | 0 | 11085.5 | 120557 | -325076 | 13 | 14 | 120557 | -1325076
2 | 6 | 5 | 1 | 11.8202 | 0 | 44.8242 | 18.7334 | 0 | 0 | 19.6196 | 17.5105 | 0 | 0 | 0 | 4.8 | 117.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12313.8 | 0 | 12313.8 | 123516 | -324971 | 13 | 15 | 123516 | -1324971
2 | 6 | 6 | 1 | 24.3093 | 0 | 69.9783 | 16.3147 | 0 | 0 | 14.882 | 17.5105 | 0 | 0 | 0 | 3.6 | 146.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29937.6 | 0 | 29937.6 | 174603 | -284361 | 13 | 15 | 174603 | -1284361
2 | 6 | 7 | 1 | 49.0171 | 0 | 140.608 | 74.3046 | 0 | 0 | 25.2133 | 19.8759 | 0 | 0 | 0 | 1.2 | 310.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88772.1 | 0 | 88772.1 | 306871 | -1269270 | 11 | 13 | 306871 | -2269270
2 | 6 | 8 | 1 | 52.339 | 0 | 168.222 | 64.1514 | 0 | 0 | 25.2074 | 19.4185 | 0 | 0 | 0 | 0 | 329.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107822 | 0 | 107822 | 369511 | -1129050 | 11 | 13 | 369511 | -2129050
2 | 6 | 9 | 1 | 41.6048 | 0 | 173.795 | 53.6866 | 0 | 0 | 25.2108 | 19.1458 | 0 | 0 | 0 | 0 | 313.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149245 | 0 | 149245 | 389078 | -971649 | 11 | 13 | 389078 | -1971649
2 | 6 | 10 | 1 | 40.691 | 0 | 172.186 | 47.6801 | 0 | 0 | 25.2175 | 19.0363 | 0 | 0 | 0 | 0 | 304.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175624 | 0 | 175624 | 387599 | -865701 | 13 | 15 | 387599 | -1865701
2 | 6 | 11 | 1 | 41.2526 | 0 | 163.102 | 44.8082 | 0 | 0 | 25.2252 | 19.0363 | 0 | 0 | 0 | 0 | 293.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179385 | 0 | 179385 | 369666 | -798935 | 15 | 17 | 369666 | -1798935
2 | 6 | 12 | 1 | 40.7849 | 0 | 149.692 | 40.4263 | 0 | 0 | 25.2386 | 19.0363 | 0 | 0 | 0 | 0 | 275.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179383 | 0 | 179383 | 344639 | -695720 | 16 | 19 | 344639 | -1695720
2 | 6 | 13 | 1 | 39.8376 | 0 | 150.207 | 37.5678 | 0 | 0 | 25.2469 | 19.0363 | 0 | 0 | 0 | 0 | 271.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179380 | 0 | 179380 | 344133 | -648478 | 18 | 21 | 344133 | -1648478
2 | 6 | 14 | 1 | 41.3263 | 0 | 165.698 | 31.569 | 0 | 0 | 25.2558 | 19.0363 | 0 | 0 | 0 | 0 | 282.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179377 | 0 | 179377 | 377513 | -583478 | 19 | 22 | 377513 | -1583478
2 | 6 | 15 | 1 | 40.724 | 0 | 172.702 | 31.34 | 0 | 0 | 25.2571 | 19.0363 | 0 | 0 | 0 | 0 | 289.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177056 | 0 | 177056 | 396270 | -593191 | 17 | 20 | 396270 | -1593191
2 | 6 | 16 | 1 | 40.9862 | 0 | 173.986 | 32.5472 | 0 | 0 | 25.2549 | 19.0363 | 0 | 0 | 0 | 0 | 291.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160951 | 0 | 160951 | 399657 | -614734 | 16 | 19 | 399657 | -1614734
2 | 6 | 17 | 1 | 42.134 | 0 | 169.782 | 37.1985 | 0 | 0 | 25.2423 | 19.0363 | 0 | 0 | 0 | 0 | 293.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131361 | 0 | 131361 | 390433 | -692549 | 15 | 18 | 390433 | -1692549
2 | 6 | 18 | 1 | 49.1283 | 0 | 152.497 | 47.4395 | 0 | 0 | 25.2256 | 19.0363 | 0 | 0 | 0 | 2 | 295.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98484.5 | 0 | 98484.5 | 383796 | -841260 | 11 | 13 | 383796 | -1841260
2 | 6 | 19 | 1 | 34.11 | 0 | 93.4203 | 57.0246 | 0 | 0 | 25.2275 | 19.0363 | 0 | 0 | 0 | 5.6 | 234.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60936 | 0 | 60936 | 309390 | -923161 | 6 | 8 | 309390 | -1923161
2 | 6 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 15.8004 | 0 | 5.9971 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43568.2 | 0 | 43568.2 | 204688 | -19524.7 | 4 | 5 | 204688 | -1019524.7
2 | 6 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 13.0141 | 0 | 5.9281 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38656.7 | 0 | 38656.7 | 170999 | -91628.1 | 3 | 4 | 170999 | -1091628.1
2 | 6 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.0856 | 0 | 5.9287 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23688.7 | 0 | 23688.7 | 171350 | -152138 | 3 | 4 | 171350 | -1152138
2 | 6 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.3156 | 0 | 5.9029 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12704.6 | 0 | 12704.6 | 141814 | -165956 | 2 | 3 | 141814 | -1165956
2 | 6 | 24 | 1 | 10.3176 | 0 | 42.5403 | 12.5413 | 0 | 0 | 9.8673 | 17.5105 | 0 | 0 | 0 | 5.6 | 98.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045.2 | 0 | 11045.2 | 144066 | -217421 | -4 | -3 | 144066 | -1217421
2 | 7 | 1 | 2 | 10.424 | 0 | 42.3304 | 13.8167 | 0 | 0 | 11.1966 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.9315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048.4 | 0 | 11048.4 | 134031 | -225214 | -6 | -5 | 134031 | -1225214
2 | 7 | 2 | 2 | 10.424 | 0 | 42.3304 | 14.7849 | 0 | 0 | 12.2666 | 17.3638 | 0 | 0 | 0 | 4.8 | 101.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11050.9 | 0 | 11050.9 | 137054 | -249372 | -6 | -5 | 137054 | -1249372
2 | 7 | 3 | 2 | 10.424 | 0 | 42.3304 | 15.7311 | 0 | 0 | 13.5326 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053 | 0 | 11053 | 131680 | -257741 | -8 | -7 | 131680 | -1257741
2 | 7 | 4 | 2 | 10.424 | 0 | 42.3304 | 16.8852 | 0 | 0 | 15.3672 | 17.3638 | 0 | 0 | 0 | 4.8 | 107.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11054.7 | 0 | 11054.7 | 132913 | -280781 | -11 | -10 | 132913 | -1280781
2 | 7 | 5 | 2 | 11.8202 | 0 | 44.8242 | 18.1467 | 0 | 0 | 17.4186 | 17.5105 | 0 | 0 | 0 | 4.8 | 114.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12284 | 0 | 12284 | 132227 | -292650 | -10 | -10 | 132227 | -1292650
2 | 7 | 6 | 2 | 24.3093 | 0 | 69.9783 | 18.1139 | 0 | 0 | 17.0431 | 17.5105 | 0 | 0 | 0 | 3.6 | 150.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29908.7 | 0 | 29908.7 | 177941 | -286176 | -14 | -13 | 177941 | -1286176
2 | 7 | 7 | 2 | 49.0171 | 0 | 140.608 | 76.6458 | 0 | 0 | 25.253 | 19.5741 | 0 | 0 | 0 | 1.2 | 312.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88743.9 | 0 | 88743.9 | 312126 | -1434880 | -15 | -15 | 312126 | -2434880
2 | 7 | 8 | 2 | 49.0022 | 0 | 168.222 | 73.8761 | 0 | 0 | 25.2262 | 19.3195 | 0 | 0 | 0 | 0 | 335.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107793 | 0 | 107793 | 374518 | -1372490 | -14 | -13 | 374518 | -2372490
2 | 7 | 9 | 2 | 40.9714 | 0 | 173.795 | 57.6209 | 0 | 0 | 25.2076 | 19.0408 | 0 | 0 | 0 | 0 | 316.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149229 | 0 | 149229 | 394793 | -1067310 | -6 | -5 | 394793 | -2067310
2 | 7 | 10 | 2 | 40.9375 | 0 | 172.186 | 52.0964 | 0 | 0 | 25.2119 | 19.0363 | 0 | 0 | 0 | 0 | 309.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175610 | 0 | 175610 | 392583 | -963697 | -2 | -1 | 392583 | -1963697
2 | 7 | 11 | 2 | 41.2397 | 0 | 163.102 | 49.5081 | 0 | 0 | 25.2151 | 19.0363 | 0 | 0 | 0 | 0 | 298.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179371 | 0 | 179371 | 373684 | -914390 | 1 | 2 | 373684 | -1914390
2 | 7 | 12 | 2 | 40.7874 | 0 | 149.692 | 41.9419 | 0 | 0 | 25.2299 | 19.0363 | 0 | 0 | 0 | 0 | 276.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179370 | 0 | 179370 | 347062 | -756872 | 5 | 6 | 347062 | -1756872
2 | 7 | 13 | 2 | 39.8421 | 0 | 150.207 | 37.1524 | 0 | 0 | 25.2464 | 19.0363 | 0 | 0 | 0 | 0 | 271.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179368 | 0 | 179368 | 348002 | -667098 | 10 | 13 | 348002 | -1667098
2 | 7 | 14 | 2 | 41.3241 | 0 | 165.698 | 28.7376 | 0 | 0 | 25.2589 | 19.0363 | 0 | 0 | 0 | 0 | 280.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179364 | 0 | 179364 | 381260 | -566429 | 14 | 17 | 381260 | -1566429
2 | 7 | 15 | 2 | 40.7211 | 0 | 172.702 | 26.7484 | 0 | 0 | 6.2677 | 19.0363 | 0 | 0 | 0 | 0 | 265.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177043 | 0 | 177043 | 400209 | -529680 | 15 | 19 | 400209 | -1529680
2 | 7 | 16 | 2 | 40.6748 | 0 | 173.986 | 27.1631 | 0 | 0 | 6.2693 | 19.0363 | 0 | 0 | 0 | 0 | 267.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160938 | 0 | 160938 | 403410 | -533735 | 16 | 20 | 403410 | -1533735
2 | 7 | 17 | 2 | 41.4371 | 0 | 169.782 | 30.8142 | 0 | 0 | 6.2579 | 19.0363 | 0 | 0 | 0 | 0 | 267.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131348 | 0 | 131348 | 396502 | -601209 | 15 | 19 | 396502 | -1601209
2 | 7 | 18 | 2 | 49.0597 | 0 | 152.497 | 39.5391 | 0 | 0 | 25.2398 | 19.0363 | 0 | 0 | 0 | 2 | 287.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98470.7 | 0 | 98470.7 | 386446 | -746549 | 10 | 13 | 386446 | -1746549
2 | 7 | 19 | 2 | 34.11 | 0 | 93.4203 | 51.9403 | 0 | 0 | 25.237 | 19.0363 | 0 | 0 | 0 | 5.6 | 229.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60922.1 | 0 | 60922.1 | 335483 | -868594 | 3 | 4 | 335483 | -1868594
2 | 7 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.7055 | 0 | 5.9828 | 17.5105 | 0 | 0 | 0 | 7.2 | 132.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43554.5 | 0 | 43554.5 | 209256 | -8479.99 | 5 | 6 | 209256 | -1008479.99
2 | 7 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.9354 | 0 | 5.9307 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38642.9 | 0 | 38642.9 | 176704 | -55674.5 | 4 | 5 | 176704 | -1055674.5
2 | 7 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 12.421 | 0 | 5.9166 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23671.7 | 0 | 23671.7 | 159995 | -92220.2 | 2 | 3 | 159995 | -1092220.2
2 | 7 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 11.7733 | 0 | 5.9066 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12686.6 | 0 | 12686.6 | 146072 | -129157 | -1 | 0 | 146072 | -1129157
2 | 7 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.626 | 0 | 5.9041 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.6 | 0 | 11025.6 | 140425 | -157329 | -2 | -1 | 140425 | -1157329
2 | 8 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5364 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.8 | 0 | 11028.8 | 138207 | -172802 | -1 | -1 | 138207 | -1172802
2 | 8 | 2 | 3 | 10.8489 | 0 | 42.3304 | 12.2865 | 0 | 0 | 9.2477 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031 | 0 | 11031 | 136529 | -198790 | -8 | -7 | 136529 | -1198790
2 | 8 | 3 | 3 | 10.8489 | 0 | 42.3304 | 13.1874 | 0 | 0 | 10.0352 | 17.3638 | 0 | 0 | 0 | 4.8 | 98.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033 | 0 | 11033 | 135266 | -216071 | -8 | -7 | 135266 | -1216071
2 | 8 | 4 | 3 | 10.8489 | 0 | 42.3304 | 13.7873 | 0 | 0 | 10.667 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.7 | 0 | 11034.7 | 134254 | -222820 | -6 | -5 | 134254 | -1222820
2 | 8 | 5 | 3 | 11.8202 | 0 | 44.8242 | 14.478 | 0 | 0 | 11.3326 | 17.5105 | 0 | 0 | 0 | 4.8 | 104.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12263.9 | 0 | 12263.9 | 136114 | -234454 | -4 | -4 | 136114 | -1234454
2 | 8 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.862 | 0 | 5.9592 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29888.5 | 0 | 29888.5 | 182541 | -210692 | -3 | -2 | 182541 | -1210692
2 | 8 | 7 | 3 | 49.0171 | 0 | 140.608 | 62.5488 | 0 | 0 | 25.2191 | 19.2086 | 0 | 0 | 0 | 1.2 | 297.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88723.6 | 0 | 88723.6 | 315048 | -1191810 | -6 | -5 | 315048 | -2191810
2 | 8 | 8 | 3 | 48.578 | 0 | 168.222 | 60.6616 | 0 | 0 | 25.2087 | 19.1619 | 0 | 0 | 0 | 0 | 321.833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107773 | 0 | 107773 | 377231 | -1142080 | -3 | -3 | 377231 | -2142080
2 | 8 | 9 | 3 | 40.634 | 0 | 173.795 | 49.0947 | 0 | 0 | 25.2143 | 19.0363 | 0 | 0 | 0 | 0 | 307.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149216 | 0 | 149216 | 396975 | -921578 | 0 | 1 | 396975 | -1921578
2 | 8 | 10 | 3 | 40.8255 | 0 | 172.186 | 44.3224 | 0 | 0 | 25.2223 | 19.0363 | 0 | 0 | 0 | 0 | 301.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175596 | 0 | 175596 | 394818 | -828332 | 4 | 5 | 394818 | -1828332
2 | 8 | 11 | 3 | 41.2354 | 0 | 163.102 | 40.7326 | 0 | 0 | 25.2281 | 19.0363 | 0 | 0 | 0 | 0 | 289.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179358 | 0 | 179358 | 376070 | -772633 | 6 | 8 | 376070 | -1772633
2 | 8 | 12 | 3 | 40.7862 | 0 | 149.692 | 35.593 | 0 | 0 | 6.2443 | 19.0363 | 0 | 0 | 0 | 0 | 251.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179357 | 0 | 179357 | 353849 | -666326 | 8 | 10 | 353849 | -1666326
2 | 8 | 13 | 3 | 39.8366 | 0 | 150.207 | 33.9781 | 0 | 0 | 6.2519 | 19.0363 | 0 | 0 | 0 | 0 | 249.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179355 | 0 | 179355 | 349785 | -632990 | 11 | 13 | 349785 | -1632990
2 | 8 | 14 | 3 | 41.3158 | 0 | 165.698 | 27.9987 | 0 | 0 | 6.2569 | 19.0363 | 0 | 0 | 0 | 0 | 260.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179351 | 0 | 179351 | 383015 | -558742 | 13 | 15 | 383015 | -1558742
2 | 8 | 15 | 3 | 40.7048 | 0 | 172.702 | 25.8585 | 0 | 0 | 6.2709 | 19.0363 | 0 | 0 | 0 | 0 | 264.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177030 | 0 | 177030 | 401940 | -513372 | 15 | 18 | 401940 | -1513372
2 | 8 | 16 | 3 | 40.6131 | 0 | 173.986 | 28.4788 | 0 | 0 | 6.2645 | 19.0363 | 0 | 0 | 0 | 0 | 268.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160925 | 0 | 160925 | 404939 | -563309 | 13 | 16 | 404939 | -1563309
2 | 8 | 17 | 3 | 42.1083 | 0 | 169.782 | 35.1667 | 0 | 0 | 6.2432 | 19.0363 | 0 | 0 | 0 | 0 | 272.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131334 | 0 | 131334 | 398702 | -691544 | 10 | 12 | 398702 | -1691544
2 | 8 | 18 | 3 | 49.0825 | 0 | 152.497 | 41.6682 | 0 | 0 | 6.2309 | 19.0363 | 0 | 0 | 0 | 2 | 270.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98458.6 | 0 | 98458.6 | 377942 | -790285 | 8 | 10 | 377942 | -1790285
2 | 8 | 19 | 3 | 34.11 | 0 | 93.4203 | 48.0085 | 0 | 0 | 25.2444 | 19.0363 | 0 | 0 | 0 | 5.6 | 225.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60911 | 0 | 60911 | 315381 | -807664 | 8 | 9 | 315381 | -1807664
2 | 8 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 15.1477 | 0 | 5.9918 | 17.5105 | 0 | 0 | 0 | 7.2 | 132.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43543.5 | 0 | 43543.5 | 211073 | -9498.12 | 5 | 6 | 211073 | -1009498.12
2 | 8 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.6159 | 0 | 5.9397 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38632.3 | 0 | 38632.3 | 178602 | -49795.1 | 7 | 8 | 178602 | -1049795.1
2 | 8 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.4171 | 0 | 5.9175 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23661.1 | 0 | 23661.1 | 161962 | -83668.7 | 5 | 6 | 161962 | -1083668.7
2 | 8 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.9822 | 0 | 5.9085 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12676.4 | 0 | 12676.4 | 147851 | -120995 | 1 | 2 | 147851 | -1120995
2 | 8 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.6578 | 0 | 5.9047 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.3 | 0 | 11015.3 | 141984 | -149534 | -1 | 0 | 141984 | -1149534
2 | 9 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.755 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.8 | 0 | 11018.8 | 139719 | -171725 | -4 | -3 | 139719 | -1171725
2 | 9 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6796 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.3 | 0 | 11021.3 | 138099 | -190005 | -6 | -6 | 138099 | -1190005
2 | 9 | 3 | 4 | 10.73 | 0 | 42.3304 | 12.5674 | 0 | 0 | 9.3181 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.1097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.4 | 0 | 11023.4 | 136661 | -209071 | -8 | -7 | 136661 | -1209071
2 | 9 | 4 | 4 | 10.73 | 0 | 42.3304 | 13.5791 | 0 | 0 | 10.2695 | 17.3638 | 0 | 0 | 0 | 4.8 | 99.0728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.3 | 0 | 11025.3 | 135464 | -223861 | -8 | -8 | 135464 | -1223861
2 | 9 | 5 | 4 | 11.8202 | 0 | 44.8242 | 14.7358 | 0 | 0 | 11.5331 | 17.5105 | 0 | 0 | 0 | 4.8 | 105.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12254.7 | 0 | 12254.7 | 136982 | -240704 | -9 | -8 | 136982 | -1240704
2 | 9 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.9363 | 0 | 5.9601 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29879.6 | 0 | 29879.6 | 182991 | -230798 | -11 | -10 | 182991 | -1230798
2 | 9 | 7 | 4 | 49.0171 | 0 | 140.608 | 63.326 | 0 | 0 | 25.2209 | 19.2049 | 0 | 0 | 0 | 1.2 | 298.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88714.9 | 0 | 88714.9 | 315769 | -1217250 | -9 | -8 | 315769 | -2217250
2 | 9 | 8 | 4 | 47.8388 | 0 | 168.222 | 60.5041 | 0 | 0 | 25.2091 | 19.1434 | 0 | 0 | 0 | 0 | 320.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107764 | 0 | 107764 | 377597 | -1152290 | -6 | -5 | 377597 | -2152290
2 | 9 | 9 | 4 | 41.2426 | 0 | 173.795 | 49.1775 | 0 | 0 | 25.2137 | 19.0363 | 0 | 0 | 0 | 0 | 308.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149209 | 0 | 149209 | 397481 | -931964 | -2 | -1 | 397481 | -1931964
2 | 9 | 10 | 4 | 41.2248 | 0 | 172.186 | 45.4939 | 0 | 0 | 25.2217 | 19.0363 | 0 | 0 | 0 | 0 | 303.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175589 | 0 | 175589 | 395016 | -862909 | 0 | 1 | 395016 | -1862909
2 | 9 | 11 | 4 | 41.3478 | 0 | 163.102 | 40.6971 | 0 | 0 | 25.2274 | 19.0363 | 0 | 0 | 0 | 0 | 289.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179351 | 0 | 179351 | 376356 | -774805 | 5 | 7 | 376356 | -1774805
2 | 9 | 12 | 4 | 40.7975 | 0 | 149.692 | 34.6485 | 0 | 0 | 25.2543 | 19.0363 | 0 | 0 | 0 | 0 | 269.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179352 | 0 | 179352 | 354719 | -637371 | 10 | 12 | 354719 | -1637371
2 | 9 | 13 | 4 | 39.8475 | 0 | 150.207 | 31.0852 | 0 | 0 | 25.2702 | 19.0363 | 0 | 0 | 0 | 0 | 265.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179349 | 0 | 179349 | 350471 | -564560 | 15 | 18 | 350471 | -1564560
2 | 9 | 14 | 4 | 41.3311 | 0 | 165.698 | 0 | 25.3252 | 0 | 6.2789 | 19.0363 | 0 | 0 | 0 | 0 | 257.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179344 | 0 | 179344 | 383750 | -475087 | 17 | 21 | 383750 | -1475087
2 | 9 | 15 | 4 | 40.7079 | 0 | 172.702 | 0 | 26.1025 | 0 | 6.2864 | 19.0363 | 0 | 0 | 0 | 0 | 264.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177023 | 0 | 177023 | 402212 | -454365 | 17 | 22 | 402212 | -1454365
2 | 9 | 16 | 4 | 40.5973 | 0 | 173.986 | 0 | 25.7895 | 0 | 6.2783 | 19.0363 | 0 | 0 | 0 | 0 | 265.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160917 | 0 | 160917 | 405657 | -488130 | 17 | 21 | 405657 | -1488130
2 | 9 | 17 | 4 | 42.6575 | 0 | 169.782 | 30.2544 | 0 | 0 | 6.2612 | 19.0363 | 0 | 0 | 0 | 0 | 267.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131327 | 0 | 131327 | 401949 | -588732 | 15 | 19 | 401949 | -1588732
2 | 9 | 18 | 4 | 49.259 | 0 | 152.497 | 37.5485 | 0 | 0 | 6.2488 | 19.0363 | 0 | 0 | 0 | 2 | 266.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98450.6 | 0 | 98450.6 | 390824 | -692142 | 14 | 17 | 390824 | -1692142
2 | 9 | 19 | 4 | 34.11 | 0 | 93.4203 | 43.0956 | 0 | 0 | 25.259 | 19.0363 | 0 | 0 | 0 | 5.6 | 220.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60902.4 | 0 | 60902.4 | 309006 | -711681 | 14 | 17 | 309006 | -1711681
2 | 9 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 16.6659 | 0 | 6.024 | 17.5105 | 0 | 0 | 0 | 7.2 | 134.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43535.2 | 0 | 43535.2 | 213389 | -19393.4 | 14 | 17 | 213389 | -1019393.4
2 | 9 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.1842 | 0 | 5.9487 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38624.1 | 0 | 38624.1 | 180833 | -49362 | 15 | 17 | 180833 | -1049362
2 | 9 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 12.7468 | 0 | 5.9214 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23654.6 | 0 | 23654.6 | 163917 | -82979.1 | 15 | 17 | 163917 | -1082979.1
2 | 9 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.6707 | 0 | 5.9071 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12670.5 | 0 | 12670.5 | 149895 | -112894 | 17 | 18 | 149895 | -1112894
2 | 9 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.1702 | 0 | 5.9027 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11010.4 | 0 | 11010.4 | 143898 | -128067 | 19 | 20 | 143898 | -1128067
2 | 10 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.0992 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014.9 | 0 | 11014.9 | 143673 | -143412 | 20 | 21 | 143673 | -1143412
2 | 10 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9238 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.2 | 0 | 11018.2 | 140618 | -145075 | 21 | 22 | 140618 | -1145075
2 | 10 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9096 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.4 | 0 | 11021.4 | 140322 | -154313 | 22 | 23 | 140322 | -1154313
2 | 10 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.8225 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024 | 0 | 11024 | 138525 | -156843 | 23 | 24 | 138525 | -1156843
2 | 10 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.0387 | 0 | 5.9014 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.8951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12254 | 0 | 12254 | 141052 | -155626 | 25 | 26 | 141052 | -1155626
2 | 10 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.7603 | 0 | 5.9666 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29879.4 | 0 | 29879.4 | 194047 | -126967 | 25 | 26 | 194047 | -1126967
2 | 10 | 7 | 5 | 49.0171 | 0 | 140.608 | 46.4531 | 0 | 0 | 25.2249 | 19.1341 | 0 | 0 | 0 | 1.2 | 281.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88715.1 | 0 | 88715.1 | 319700 | -823073 | 26 | 27 | 319700 | -1823073
2 | 10 | 8 | 5 | 51.7118 | 0 | 168.222 | 41.27 | 0 | 0 | 25.2412 | 19.0511 | 0 | 0 | 0 | 0 | 305.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107765 | 0 | 107765 | 381886 | -728731 | 27 | 27 | 381886 | -1728731
2 | 10 | 9 | 5 | 44.2539 | 0 | 173.795 | 35.4095 | 0 | 0 | 25.249 | 19.0363 | 0 | 0 | 0 | 0 | 297.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149205 | 0 | 149205 | 400143 | -657165 | 24 | 25 | 400143 | -1657165
2 | 10 | 10 | 5 | 40.6964 | 0 | 172.186 | 33.7257 | 0 | 0 | 25.2589 | 19.0363 | 0 | 0 | 0 | 0 | 290.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175583 | 0 | 175583 | 397770 | -616290 | 21 | 24 | 397770 | -1616290
2 | 10 | 11 | 5 | 41.199 | 0 | 163.102 | 34.9357 | 0 | 0 | 25.2592 | 19.0363 | 0 | 0 | 0 | 0 | 283.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179345 | 0 | 179345 | 388586 | -639057 | 20 | 23 | 388586 | -1639057
2 | 10 | 12 | 5 | 40.7965 | 0 | 149.692 | 33.6794 | 0 | 0 | 6.264 | 19.0363 | 0 | 0 | 0 | 0 | 249.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179344 | 0 | 179344 | 371269 | -599572 | 18 | 21 | 371269 | -1599572
2 | 10 | 13 | 5 | 39.8305 | 0 | 150.207 | 31.3492 | 0 | 0 | 6.265 | 19.0363 | 0 | 0 | 0 | 0 | 246.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179343 | 0 | 179343 | 352998 | -571457 | 17 | 20 | 352998 | -1571457
2 | 10 | 14 | 5 | 41.3294 | 0 | 165.698 | 27.2146 | 0 | 0 | 6.2662 | 19.0363 | 0 | 0 | 0 | 0 | 259.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179341 | 0 | 179341 | 385971 | -530860 | 17 | 20 | 385971 | -1530860
2 | 10 | 15 | 5 | 40.7232 | 0 | 172.702 | 26.1224 | 0 | 0 | 6.2712 | 19.0363 | 0 | 0 | 0 | 0 | 264.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177021 | 0 | 177021 | 404606 | -517280 | 17 | 20 | 404606 | -1517280
2 | 10 | 16 | 5 | 40.9119 | 0 | 173.986 | 27.5582 | 0 | 0 | 6.2665 | 19.0363 | 0 | 0 | 0 | 0 | 267.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160918 | 0 | 160918 | 407538 | -546052 | 16 | 19 | 407538 | -1546052
2 | 10 | 17 | 5 | 41.7361 | 0 | 169.782 | 32.3015 | 0 | 0 | 6.2516 | 19.0363 | 0 | 0 | 0 | 0 | 269.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131329 | 0 | 131329 | 399782 | -636522 | 14 | 16 | 399782 | -1636522
2 | 10 | 18 | 5 | 48.326 | 0 | 152.497 | 40.9459 | 0 | 0 | 6.2331 | 19.0363 | 0 | 0 | 0 | 2 | 269.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98453.4 | 0 | 98453.4 | 384797 | -766729 | 10 | 13 | 384797 | -1766729
2 | 10 | 19 | 5 | 34.11 | 0 | 93.4203 | 49.2191 | 0 | 0 | 25.2415 | 19.0363 | 0 | 0 | 0 | 5.6 | 226.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60906.2 | 0 | 60906.2 | 318073 | -827437 | 9 | 11 | 318073 | -1827437
2 | 10 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 16.0255 | 0 | 6.0103 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43538.8 | 0 | 43538.8 | 213004 | -19458.4 | 5 | 7 | 213004 | -1019458.4
2 | 10 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.3956 | 0 | 5.938 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38627.8 | 0 | 38627.8 | 180023 | -72661.4 | 5 | 6 | 180023 | -1072661.4
2 | 10 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.1723 | 0 | 5.9306 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23658.4 | 0 | 23658.4 | 172792 | -126285 | 4 | 5 | 172792 | -1126285
2 | 10 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.8579 | 0 | 5.9083 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12675.1 | 0 | 12675.1 | 149527 | -139329 | 3 | 4 | 149527 | -1139329
2 | 10 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.8625 | 0 | 5.9079 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.6 | 0 | 11015.6 | 148714 | -165143 | 3 | 4 | 148714 | -1165143
2 | 11 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3949 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11019.1 | 0 | 11019.1 | 141151 | -179727 | 2 | 3 | 141151 | -1179727
2 | 11 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4752 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.8 | 0 | 11021.8 | 142147 | -191109 | 4 | 5 | 142147 | -1191109
2 | 11 | 3 | 6 | 6.3817 | 0 | 42.7453 | 11.644 | 0 | 0 | 8.6443 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.7 | 0 | 11024.7 | 138251 | -196365 | 6 | 7 | 138251 | -1196365
2 | 11 | 4 | 6 | 6.3817 | 0 | 42.7453 | 11.3575 | 0 | 0 | 8.5717 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.2199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.9 | 0 | 11026.9 | 136986 | -205424 | 7 | 8 | 136986 | -1205424
2 | 11 | 5 | 6 | 6.3817 | 0 | 42.7453 | 13.3575 | 0 | 0 | 10.4511 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.0994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.9 | 0 | 11028.9 | 140934 | -244495 | 7 | 8 | 140934 | -1244495
2 | 11 | 6 | 6 | 6.3817 | 0 | 42.7453 | 13.5691 | 0 | 0 | 10.7152 | 17.3638 | 0 | 0 | 0 | 3.6 | 94.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11030.8 | 0 | 11030.8 | 134736 | -238205 | 7 | 9 | 134736 | -1238205
2 | 11 | 7 | 6 | 6.3817 | 0 | 42.7453 | 14.2048 | 0 | 0 | 11.4639 | 17.3638 | 0 | 0 | 0 | 1.2 | 93.3595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.9 | 0 | 11033.9 | 137833 | -256833 | 10 | 12 | 137833 | -1256833
2 | 11 | 8 | 6 | 5.5904 | 0 | 42.7453 | 76.0376 | 0 | 0 | 25.2109 | 19.7976 | 0 | 0 | 0 | 0 | 169.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.4 | 0 | 11036.4 | 122089 | -1180130 | 10 | 12 | 122089 | -2180130
2 | 11 | 9 | 6 | 5.042 | 0 | 42.7453 | 63.3586 | 0 | 0 | 25.2293 | 19.229 | 0 | 0 | 0 | 0 | 155.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.9 | 0 | 11038.9 | 121543 | -970573 | 14 | 17 | 121543 | -1970573
2 | 11 | 10 | 6 | 5.5449 | 0 | 42.7453 | 47.2831 | 0 | 0 | 25.2408 | 18.8999 | 0 | 0 | 0 | 0 | 139.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.3 | 0 | 11025.3 | 121288 | -763256 | 19 | 22 | 121288 | -1763256
2 | 11 | 11 | 6 | 5.4789 | 0 | 42.7453 | 37.1999 | 0 | 0 | 8.0804 | 18.8896 | 0 | 0 | 0 | 0 | 112.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022 | 0 | 11022 | 122444 | -626786 | 26 | 29 | 122444 | -1626786
2 | 11 | 12 | 6 | 5.4781 | 0 | 42.7453 | 31.6318 | 0 | 0 | 6.2604 | 18.8896 | 0 | 0 | 0 | 0 | 105.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11019.9 | 0 | 11019.9 | 122024 | -543949 | 28 | 32 | 122024 | -1543949
2 | 11 | 13 | 6 | 5.479 | 0 | 42.7453 | 27.6152 | 0 | 0 | 6.2726 | 18.8896 | 0 | 0 | 0 | 0 | 101.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.7 | 0 | 11018.7 | 140959 | -485331 | 31 | 36 | 140959 | -1485331
2 | 11 | 14 | 6 | 5.4797 | 0 | 42.7453 | 25.3754 | 0 | 0 | 6.2736 | 18.8896 | 0 | 0 | 0 | 0 | 98.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017.9 | 0 | 11017.9 | 157154 | -454200 | 33 | 38 | 157154 | -1454200
2 | 11 | 15 | 6 | 5.4799 | 0 | 42.7453 | 0 | 10.1032 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 77.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017.3 | 0 | 11017.3 | 119818 | -14040.6 | 34 | 40 | 119818 | -1014040.6
2 | 11 | 16 | 6 | 5.5197 | 0 | 42.7453 | 0 | 9.7152 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 76.7055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017 | 0 | 11017 | 119758 | -18319.5 | 35 | 40 | 119758 | -1018319.5
2 | 11 | 17 | 6 | 5.6578 | 0 | 42.7453 | 0 | 10.7774 | 0 | 5.8989 | 15.3158 | 0 | 0 | 0 | 0 | 80.3952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.8 | 0 | 11020.8 | 132524 | -26052.6 | 35 | 39 | 132524 | -1026052.6
2 | 11 | 18 | 6 | 8.5412 | 0 | 42.7453 | 0 | 11.8806 | 0 | 5.9064 | 17.3638 | 0 | 0 | 0 | 2 | 88.4373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.6 | 0 | 11022.6 | 143835 | -34538 | 31 | 33 | 143835 | -1034538
2 | 11 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.14 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.5477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.8 | 0 | 11024.8 | 138471 | -40189.9 | 31 | 33 | 138471 | -1040189.9
2 | 11 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.1317 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.4 | 0 | 11027.4 | 135821 | -59019.8 | 28 | 28 | 135821 | -1059019.8
2 | 11 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9182 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.6 | 0 | 11029.6 | 134244 | -66371.1 | 32 | 33 | 134244 | -1066371.1
2 | 11 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0277 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.9 | 0 | 11031.9 | 135889 | -79817.5 | 31 | 32 | 135889 | -1079817.5
2 | 11 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.746 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.1 | 0 | 11034.1 | 131693 | -83675.6 | 30 | 31 | 131693 | -1083675.6
2 | 11 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.25 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.3 | 0 | 11036.3 | 137177 | -95191.7 | 30 | 30 | 137177 | -1095191.7
2 | 12 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8434 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4107.91 | 0 | 4107.91 | 129909 | -90141.5 | 29 | 29 | 129909 | -1090141.5
2 | 12 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9543 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4109.83 | 0 | 4109.83 | 131382 | -107105 | 28 | 28 | 131382 | -1107105
2 | 12 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.801 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.36 | 0 | 4111.36 | 128752 | -116124 | 25 | 25 | 128752 | -1116124
2 | 12 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8267 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4112.85 | 0 | 4112.85 | 129009 | -130235 | 22 | 22 | 129009 | -1130235
2 | 12 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7445 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4114.25 | 0 | 4114.25 | 127649 | -143931 | 18 | 18 | 127649 | -1143931
2 | 12 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7757 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.6 | 0 | 4115.6 | 127895 | -145860 | 19 | 19 | 127895 | -1145860
2 | 12 | 7 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7341 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 1.2 | 83.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.88 | 0 | 4116.88 | 127113 | -147636 | 21 | 21 | 127113 | -1147636
2 | 12 | 8 | 7 | 4.8811 | 0 | 42.7453 | 0 | 10.6705 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 0 | 81.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.08 | 0 | 4118.08 | 127100 | -150009 | 21 | 21 | 127100 | -1150009
2 | 12 | 9 | 7 | 4.4556 | 0 | 42.7453 | 0 | 10.4641 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.9263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.22 | 0 | 4119.22 | 126560 | -139175 | 22 | 22 | 126560 | -1139175
2 | 12 | 10 | 7 | 4.7449 | 0 | 42.7453 | 0 | 10.2204 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 80.9715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.32 | 0 | 4120.32 | 126553 | -120513 | 23 | 23 | 126553 | -1120513
2 | 12 | 11 | 7 | 4.5606 | 0 | 42.7453 | 0 | 9.9111 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.4776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.37 | 0 | 4121.37 | 126413 | -103280 | 26 | 26 | 126413 | -1103280
2 | 12 | 12 | 7 | 4.1497 | 0 | 42.7453 | 0 | 9.8639 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.32 | 0 | 4122.32 | 127657 | -74346.5 | 28 | 28 | 127657 | -1074346.5
2 | 12 | 13 | 7 | 4.1491 | 0 | 42.7453 | 0 | 9.6294 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 79.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.19 | 0 | 4123.19 | 128780 | -65716.2 | 30 | 31 | 128780 | -1065716.2
2 | 12 | 14 | 7 | 4.1487 | 0 | 42.7453 | 0 | 9.2593 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 79.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.98 | 0 | 4123.98 | 130121 | -51051.1 | 35 | 39 | 130121 | -1051051.1
2 | 12 | 15 | 7 | 4.15 | 0 | 42.7453 | 0 | 9.0305 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 79.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.74 | 0 | 4123.74 | 131264 | -42796.5 | 38 | 42 | 131264 | -1042796.5
2 | 12 | 16 | 7 | 4.1524 | 0 | 42.7453 | 0 | 8.9379 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 79.0961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.99 | 0 | 4123.99 | 131324 | -42960.4 | 36 | 39 | 131324 | -1042960.4
2 | 12 | 17 | 7 | 4.309 | 0 | 42.7453 | 0 | 8.9411 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 79.2559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.84 | 0 | 4123.84 | 130645 | -46522.2 | 35 | 38 | 130645 | -1046522.2
2 | 12 | 18 | 7 | 6.4928 | 0 | 42.7453 | 0 | 9.0071 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 2 | 83.5057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.03 | 0 | 4124.03 | 129092 | -60013.7 | 31 | 33 | 129092 | -1060013.7
2 | 12 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.0096 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.48 | 0 | 4124.48 | 127984 | -65914.2 | 31 | 33 | 127984 | -1065914.2
2 | 12 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.1033 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 7.2 | 88.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.27 | 0 | 4125.27 | 126586 | -80578.2 | 26 | 26 | 126586 | -1080578.2
2 | 12 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.1267 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 7.2 | 88.9959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4126.24 | 0 | 4126.24 | 126041 | -97100 | 26 | 26 | 126041 | -1097100
2 | 12 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.2229 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4127.12 | 0 | 4127.12 | 125444 | -117036 | 21 | 21 | 125444 | -1117036
2 | 12 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.2996 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.12 | 0 | 4128.12 | 125267 | -130043 | 20 | 20 | 125267 | -1130043
2 | 12 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.3439 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.89 | 0 | 4128.89 | 124944 | -139519 | 18 | 19 | 124944 | -1139519
2 | 13 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3623 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11060 | 0 | 11060 | 124965 | -143422 | 17 | 17 | 124965 | -1143422
2 | 13 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3936 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11060.7 | 0 | 11060.7 | 124972 | -144764 | 19 | 19 | 124972 | -1144764
2 | 13 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3588 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.5987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11060.6 | 0 | 11060.6 | 124817 | -146263 | 20 | 20 | 124817 | -1146263
2 | 13 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3413 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061 | 0 | 11061 | 124726 | -145256 | 22 | 22 | 124726 | -1145256
2 | 13 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.5957 | 0 | 5.8967 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.4474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12289 | 0 | 12289 | 127757 | -148414 | 22 | 22 | 127757 | -1148414
2 | 13 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.6473 | 0 | 5.9261 | 17.5105 | 0 | 0 | 0 | 3.6 | 133.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29912.6 | 0 | 29912.6 | 175371 | -124372 | 23 | 23 | 175371 | -1124372
2 | 13 | 7 | 1 | 49.0171 | 0 | 140.608 | 50.0547 | 0 | 0 | 25.2159 | 19.1397 | 0 | 0 | 0 | 1.2 | 285.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88746.7 | 0 | 88746.7 | 309944 | -870102 | 24 | 24 | 309944 | -1870102
2 | 13 | 8 | 1 | 51.5181 | 0 | 168.222 | 45.1091 | 0 | 0 | 25.23 | 19.0622 | 0 | 0 | 0 | 0 | 309.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107795 | 0 | 107795 | 372486 | -796667 | 25 | 25 | 372486 | -1796667
2 | 13 | 9 | 1 | 42.0255 | 0 | 173.795 | 37.2415 | 0 | 0 | 25.2482 | 19.0363 | 0 | 0 | 0 | 0 | 297.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149231 | 0 | 149231 | 391613 | -673952 | 25 | 25 | 391613 | -1673952
2 | 13 | 10 | 1 | 41.9636 | 0 | 172.186 | 34.5694 | 0 | 0 | 25.2609 | 19.0363 | 0 | 0 | 0 | 0 | 293.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175608 | 0 | 175608 | 390131 | -619478 | 26 | 26 | 390131 | -1619478
2 | 13 | 11 | 1 | 42.114 | 0 | 163.102 | 34.9768 | 0 | 0 | 25.2669 | 19.0363 | 0 | 0 | 0 | 0 | 284.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179369 | 0 | 179369 | 378751 | -608925 | 27 | 27 | 378751 | -1608925
2 | 13 | 12 | 1 | 41.1368 | 0 | 149.692 | 33.2033 | 0 | 0 | 25.2761 | 19.0363 | 0 | 0 | 0 | 0 | 268.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179367 | 0 | 179367 | 364155 | -563566 | 27 | 27 | 364155 | -1563566
2 | 13 | 13 | 1 | 39.9301 | 0 | 150.207 | 33.3033 | 0 | 0 | 25.2659 | 19.0363 | 0 | 0 | 0 | 0 | 267.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179365 | 0 | 179365 | 346113 | -589445 | 25 | 26 | 346113 | -1589445
2 | 13 | 14 | 1 | 42.0744 | 0 | 165.698 | 29.3374 | 0 | 0 | 25.2609 | 19.0363 | 0 | 0 | 0 | 0 | 281.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179362 | 0 | 179362 | 379562 | -559076 | 23 | 25 | 379562 | -1559076
2 | 13 | 15 | 1 | 41.3539 | 0 | 172.702 | 27.3967 | 0 | 0 | 6.2684 | 19.0363 | 0 | 0 | 0 | 0 | 266.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177041 | 0 | 177041 | 398495 | -542664 | 23 | 25 | 398495 | -1542664
2 | 13 | 16 | 1 | 41.7196 | 0 | 173.986 | 28.193 | 0 | 0 | 6.2566 | 19.0363 | 0 | 0 | 0 | 0 | 269.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160937 | 0 | 160937 | 401666 | -556512 | 23 | 25 | 401666 | -1556512
2 | 13 | 17 | 1 | 45.9128 | 0 | 169.782 | 33.2383 | 0 | 0 | 6.2584 | 19.0363 | 0 | 0 | 0 | 0 | 274.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131347 | 0 | 131347 | 394437 | -618954 | 21 | 23 | 394437 | -1618954
2 | 13 | 18 | 1 | 49.0771 | 0 | 152.497 | 37.7692 | 0 | 0 | 25.2551 | 19.0363 | 0 | 0 | 0 | 2 | 285.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98470.6 | 0 | 98470.6 | 379704 | -673581 | 20 | 22 | 379704 | -1673581
2 | 13 | 19 | 1 | 34.11 | 0 | 93.4203 | 43.0002 | 0 | 0 | 25.2649 | 19.0363 | 0 | 0 | 0 | 5.6 | 220.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60922.7 | 0 | 60922.7 | 299273 | -695022 | 20 | 22 | 299273 | -1695022
2 | 13 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 14.0134 | 0 | 5.9431 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43554.7 | 0 | 43554.7 | 174511 | -16675.5 | 19 | 21 | 174511 | -1016675.5
2 | 13 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 13.9718 | 0 | 5.9439 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38643.8 | 0 | 38643.8 | 178677 | -46233.8 | 17 | 19 | 178677 | -1046233.8
2 | 13 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 12.5405 | 0 | 5.9178 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23673.5 | 0 | 23673.5 | 160338 | -86089.9 | 17 | 18 | 160338 | -1086089.9
2 | 13 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.5258 | 0 | 5.9052 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12689.5 | 0 | 12689.5 | 146436 | -112754 | 16 | 18 | 146436 | -1112754
2 | 13 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.9222 | 0 | 5.9085 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.6 | 0 | 11029.6 | 149514 | -134576 | 16 | 18 | 149514 | -1134576
2 | 14 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3531 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.7 | 0 | 11033.7 | 138740 | -125955 | 16 | 18 | 138740 | -1125955
2 | 14 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.5384 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.8 | 0 | 11036.8 | 140768 | -152114 | 15 | 16 | 140768 | -1152114
2 | 14 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.9548 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.7 | 0 | 11038.7 | 136314 | -153930 | 14 | 15 | 136314 | -1153930
2 | 14 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 12.0053 | 0 | 5.9094 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040.5 | 0 | 11040.5 | 150499 | -179604 | 14 | 15 | 150499 | -1179604
2 | 14 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.3116 | 0 | 5.9019 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.1685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12269.6 | 0 | 12269.6 | 137530 | -159683 | 14 | 15 | 137530 | -1159683
2 | 14 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 15.4486 | 0 | 5.9792 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29895.2 | 0 | 29895.2 | 195323 | -155760 | 14 | 15 | 195323 | -1155760
2 | 14 | 7 | 2 | 49.0171 | 0 | 140.608 | 54.1147 | 0 | 0 | 25.2082 | 19.2024 | 0 | 0 | 0 | 1.2 | 289.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88730.1 | 0 | 88730.1 | 316827 | -985036 | 14 | 15 | 316827 | -1985036
2 | 14 | 8 | 2 | 49.6687 | 0 | 168.222 | 52.2675 | 0 | 0 | 25.2112 | 19.0963 | 0 | 0 | 0 | 0 | 314.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107779 | 0 | 107779 | 378851 | -954415 | 12 | 13 | 378851 | -1954415
2 | 14 | 9 | 2 | 41.0467 | 0 | 173.795 | 46.1726 | 0 | 0 | 25.2198 | 19.0363 | 0 | 0 | 0 | 0 | 305.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149218 | 0 | 149218 | 397991 | -856191 | 12 | 13 | 397991 | -1856191
2 | 14 | 10 | 2 | 41.4655 | 0 | 172.186 | 43.9884 | 0 | 0 | 25.2269 | 19.0363 | 0 | 0 | 0 | 0 | 301.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175597 | 0 | 175597 | 396036 | -805529 | 13 | 15 | 396036 | -1805529
2 | 14 | 11 | 2 | 41.7577 | 0 | 163.102 | 45.7809 | 0 | 0 | 25.2295 | 19.0363 | 0 | 0 | 0 | 0 | 294.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179359 | 0 | 179359 | 380172 | -816736 | 14 | 15 | 380172 | -1816736
2 | 14 | 12 | 2 | 41.1159 | 0 | 149.692 | 41.9383 | 0 | 0 | 25.2467 | 19.0363 | 0 | 0 | 0 | 0 | 277.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179358 | 0 | 179358 | 361072 | -716082 | 16 | 18 | 361072 | -1716082
2 | 14 | 13 | 2 | 39.8605 | 0 | 150.207 | 39.9644 | 0 | 0 | 25.249 | 19.0363 | 0 | 0 | 0 | 0 | 274.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179356 | 0 | 179356 | 351222 | -695888 | 17 | 19 | 351222 | -1695888
2 | 14 | 14 | 2 | 41.2957 | 0 | 165.698 | 29.5264 | 0 | 0 | 25.2571 | 19.0363 | 0 | 0 | 0 | 0 | 280.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 384205 | -570285 | 17 | 19 | 384205 | -1570285
2 | 14 | 15 | 2 | 40.701 | 0 | 172.702 | 27.0393 | 0 | 0 | 25.2716 | 19.0363 | 0 | 0 | 0 | 0 | 284.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177034 | 0 | 177034 | 403105 | -526048 | 19 | 21 | 403105 | -1526048
2 | 14 | 16 | 2 | 40.7763 | 0 | 173.986 | 27.6387 | 0 | 0 | 25.2683 | 19.0363 | 0 | 0 | 0 | 0 | 286.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160930 | 0 | 160930 | 405980 | -544665 | 18 | 21 | 405980 | -1544665
2 | 14 | 17 | 2 | 40.9706 | 0 | 169.782 | 32.6031 | 0 | 0 | 25.2575 | 19.0363 | 0 | 0 | 0 | 0 | 287.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131340 | 0 | 131340 | 400935 | -622924 | 18 | 20 | 400935 | -1622924
2 | 14 | 18 | 2 | 47.949 | 0 | 152.497 | 39.5738 | 0 | 0 | 25.2431 | 19.0363 | 0 | 0 | 0 | 2 | 286.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98463.7 | 0 | 98463.7 | 389243 | -714367 | 16 | 18 | 389243 | -1714367
2 | 14 | 19 | 2 | 34.11 | 0 | 93.4203 | 45.5165 | 0 | 0 | 25.2542 | 19.0363 | 0 | 0 | 0 | 5.6 | 222.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60915.6 | 0 | 60915.6 | 311179 | -740801 | 15 | 17 | 311179 | -1740801
2 | 14 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 15.7508 | 0 | 5.9867 | 15.4625 | 0 | 0 | 0 | 7.2 | 131.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43548 | 0 | 43548 | 194537 | -14704 | 13 | 14 | 194537 | -1014704
2 | 14 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 14.6197 | 0 | 5.9558 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38636.7 | 0 | 38636.7 | 182140 | -44635.4 | 12 | 13 | 182140 | -1044635.4
2 | 14 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.2942 | 0 | 5.927 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23666.7 | 0 | 23666.7 | 163794 | -77667.4 | 11 | 12 | 163794 | -1077667.4
2 | 14 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.2471 | 0 | 5.911 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.5992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12682.2 | 0 | 12682.2 | 149684 | -109007 | 10 | 10 | 149684 | -1109007
2 | 14 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.8637 | 0 | 5.9064 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.6 | 0 | 11021.6 | 143822 | -134020 | 10 | 11 | 143822 | -1134020
2 | 15 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.2791 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.2 | 0 | 11025.2 | 141652 | -143511 | 11 | 12 | 141652 | -1143511
2 | 15 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 12.4024 | 0 | 5.9148 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.7 | 0 | 11027.7 | 156836 | -174594 | 10 | 11 | 156836 | -1174594
2 | 15 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3757 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.9 | 0 | 11029.9 | 138747 | -164309 | 8 | 8 | 138747 | -1164309
2 | 15 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.7253 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11032.9 | 0 | 11032.9 | 143977 | -191477 | 6 | 7 | 143977 | -1191477
2 | 15 | 5 | 3 | 11.8202 | 0 | 44.8242 | 11.9531 | 0 | 0 | 8.9896 | 17.5105 | 0 | 0 | 0 | 4.8 | 99.8977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12262.1 | 0 | 12262.1 | 139398 | -196625 | 6 | 7 | 139398 | -1196625
2 | 15 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.1615 | 0 | 5.9511 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29887 | 0 | 29887 | 185779 | -189852 | 4 | 5 | 185779 | -1189852
2 | 15 | 7 | 3 | 49.0171 | 0 | 140.608 | 61.6439 | 0 | 0 | 25.211 | 19.2358 | 0 | 0 | 0 | 1.2 | 296.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88722.3 | 0 | 88722.3 | 317711 | -1131990 | 3 | 4 | 317711 | -2131990
2 | 15 | 8 | 3 | 50.6981 | 0 | 168.222 | 54.7685 | 0 | 0 | 25.2081 | 19.1172 | 0 | 0 | 0 | 0 | 318.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107772 | 0 | 107772 | 380057 | -1007810 | 7 | 8 | 380057 | -2007810
2 | 15 | 9 | 3 | 40.368 | 0 | 173.795 | 46.3248 | 0 | 0 | 25.2192 | 19.0431 | 0 | 0 | 0 | 0 | 304.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149212 | 0 | 149212 | 399277 | -857289 | 10 | 11 | 399277 | -1857289
2 | 15 | 10 | 3 | 41.6056 | 0 | 172.186 | 43.2787 | 0 | 0 | 25.2298 | 19.0363 | 0 | 0 | 0 | 0 | 301.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175591 | 0 | 175591 | 397416 | -785941 | 14 | 15 | 397416 | -1785941
2 | 15 | 11 | 3 | 42.2034 | 0 | 163.102 | 42.747 | 0 | 0 | 25.2404 | 19.0363 | 0 | 0 | 0 | 0 | 292.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 379013 | -745949 | 18 | 20 | 379013 | -1745949
2 | 15 | 12 | 3 | 41.2257 | 0 | 149.692 | 36.9748 | 0 | 0 | 25.2656 | 19.0363 | 0 | 0 | 0 | 0 | 272.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179352 | 0 | 179352 | 366256 | -631096 | 22 | 24 | 366256 | -1631096
2 | 15 | 13 | 3 | 39.8666 | 0 | 150.207 | 34.5836 | 0 | 0 | 6.2649 | 19.0363 | 0 | 0 | 0 | 0 | 249.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179350 | 0 | 179350 | 352636 | -606061 | 23 | 25 | 352636 | -1606061
2 | 15 | 14 | 3 | 41.6813 | 0 | 165.698 | 29.4018 | 0 | 0 | 6.2607 | 19.0363 | 0 | 0 | 0 | 0 | 262.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179347 | 0 | 179347 | 385639 | -554505 | 23 | 25 | 385639 | -1554505
2 | 15 | 15 | 3 | 41.3182 | 0 | 172.702 | 27.567 | 0 | 0 | 6.2602 | 19.0363 | 0 | 0 | 0 | 0 | 266.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177026 | 0 | 177026 | 404301 | -541299 | 23 | 25 | 404301 | -1541299
2 | 15 | 16 | 3 | 41.3738 | 0 | 173.986 | 27.6845 | 0 | 0 | 6.2598 | 19.0363 | 0 | 0 | 0 | 0 | 268.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160922 | 0 | 160922 | 407190 | -543696 | 23 | 25 | 407190 | -1543696
2 | 15 | 17 | 3 | 46.3177 | 0 | 169.782 | 32.1203 | 0 | 0 | 6.2632 | 19.0363 | 0 | 0 | 0 | 0 | 273.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131332 | 0 | 131332 | 401277 | -595705 | 23 | 24 | 401277 | -1595705
2 | 15 | 18 | 3 | 48.805 | 0 | 152.497 | 35.729 | 0 | 0 | 14.6874 | 19.0363 | 0 | 0 | 0 | 2 | 272.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98456.1 | 0 | 98456.1 | 386052 | -633359 | 24 | 24 | 386052 | -1633359
2 | 15 | 19 | 3 | 34.11 | 0 | 93.4203 | 39.9621 | 0 | 0 | 25.2743 | 19.0363 | 0 | 0 | 0 | 5.6 | 217.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60908.2 | 0 | 60908.2 | 303344 | -647673 | 23 | 24 | 303344 | -1647673
2 | 15 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.6978 | 0 | 5.9572 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43540.2 | 0 | 43540.2 | 180563 | -16864.3 | 24 | 24 | 180563 | -1016864.3
2 | 15 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.4358 | 0 | 5.956 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38629.4 | 0 | 38629.4 | 186382 | -22531.4 | 24 | 24 | 186382 | -1022531.4
2 | 15 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 13.2087 | 0 | 5.9279 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23659 | 0 | 23659 | 167256 | -56584.8 | 24 | 24 | 167256 | -1056584.8
2 | 15 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.0874 | 0 | 5.911 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.4395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12674 | 0 | 12674 | 152927 | -75971.3 | 25 | 25 | 152927 | -1075971.3
2 | 15 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.6947 | 0 | 5.9066 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014.2 | 0 | 11014.2 | 147834 | -92438.2 | 26 | 26 | 147834 | -1092438.2
2 | 16 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.8288 | 0 | 5.9072 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.2 | 0 | 11018.2 | 147252 | -104464 | 26 | 26 | 147252 | -1104464
2 | 16 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6637 | 0 | 5.905 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.5 | 0 | 11021.5 | 142892 | -103142 | 27 | 27 | 142892 | -1103142
2 | 16 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.4187 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.2 | 0 | 11024.2 | 141682 | -118314 | 26 | 26 | 141682 | -1118314
2 | 16 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.2694 | 0 | 5.9025 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026 | 0 | 11026 | 141471 | -137213 | 25 | 25 | 141471 | -1137213
2 | 16 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.3374 | 0 | 5.9032 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.1955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12255.4 | 0 | 12255.4 | 142789 | -143408 | 24 | 24 | 142789 | -1143408
2 | 16 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.9451 | 0 | 5.9977 | 17.5105 | 0 | 0 | 0 | 3.6 | 137.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29880.8 | 0 | 29880.8 | 205189 | -122033 | 25 | 26 | 205189 | -1122033
2 | 16 | 7 | 4 | 49.0171 | 0 | 140.608 | 44.769 | 0 | 0 | 25.224 | 19.0962 | 0 | 0 | 0 | 1.2 | 279.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88716.5 | 0 | 88716.5 | 320759 | -799714 | 24 | 26 | 320759 | -1799714
2 | 16 | 8 | 4 | 46.0836 | 0 | 168.222 | 42.164 | 0 | 0 | 25.239 | 19.0481 | 0 | 0 | 0 | 0 | 300.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107766 | 0 | 107766 | 382735 | -743195 | 24 | 26 | 382735 | -1743195
2 | 16 | 9 | 4 | 40.4436 | 0 | 173.795 | 30.0904 | 0 | 0 | 25.2563 | 19.0363 | 0 | 0 | 0 | 0 | 288.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149206 | 0 | 149206 | 401691 | -562174 | 26 | 28 | 401691 | -1562174
2 | 16 | 10 | 4 | 40.6932 | 0 | 172.186 | 0 | 26.5282 | 0 | 6.2781 | 19.0363 | 0 | 0 | 0 | 0 | 264.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175584 | 0 | 175584 | 399650 | -476165 | 27 | 30 | 399650 | -1476165
2 | 16 | 11 | 4 | 41.2119 | 0 | 163.102 | 29.6267 | 0 | 0 | 25.2831 | 19.0363 | 0 | 0 | 0 | 0 | 278.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179346 | 0 | 179346 | 396158 | -517710 | 26 | 29 | 396158 | -1517710
2 | 16 | 12 | 4 | 40.7497 | 0 | 149.692 | 0 | 26.1784 | 0 | 6.2977 | 19.0363 | 0 | 0 | 0 | 0 | 241.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179345 | 0 | 179345 | 372720 | -434904 | 27 | 30 | 372720 | -1434904
2 | 16 | 13 | 4 | 39.8365 | 0 | 150.207 | 0 | 24.4684 | 0 | 6.3025 | 19.0363 | 0 | 0 | 0 | 0 | 239.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179343 | 0 | 179343 | 354799 | -404255 | 27 | 31 | 354799 | -1404255
2 | 16 | 14 | 4 | 41.3194 | 0 | 165.698 | 0 | 24.7125 | 0 | 6.2793 | 19.0363 | 0 | 0 | 0 | 0 | 257.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179340 | 0 | 179340 | 387294 | -460501 | 22 | 22 | 387294 | -1460501
2 | 16 | 15 | 4 | 40.7149 | 0 | 172.702 | 0 | 25.7978 | 0 | 6.3105 | 19.0363 | 0 | 0 | 0 | 0 | 264.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177021 | 0 | 177021 | 406227 | -344937 | 28 | 32 | 406227 | -1344937
2 | 16 | 16 | 4 | 40.7073 | 0 | 173.986 | 0 | 25.9862 | 0 | 25.3134 | 19.0363 | 0 | 0 | 0 | 0 | 285.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160917 | 0 | 160917 | 409022 | -351503 | 28 | 32 | 409022 | -1351503
2 | 16 | 17 | 4 | 41.1658 | 0 | 169.782 | 0 | 26.055 | 0 | 25.3028 | 19.0363 | 0 | 0 | 0 | 0 | 281.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131325 | 0 | 131325 | 403081 | -405967 | 26 | 30 | 403081 | -1405967
2 | 16 | 18 | 4 | 47.3925 | 0 | 152.497 | 29.4838 | 0 | 0 | 6.2792 | 19.0363 | 0 | 0 | 0 | 2 | 256.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98448.1 | 0 | 98448.1 | 395820 | -537688 | 23 | 25 | 395820 | -1537688
2 | 16 | 19 | 4 | 34.11 | 0 | 93.4203 | 36.3908 | 0 | 0 | 25.2822 | 19.0363 | 0 | 0 | 0 | 5.6 | 213.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60899.6 | 0 | 60899.6 | 314404 | -598864 | 21 | 23 | 314404 | -1598864
2 | 16 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.5147 | 0 | 5.9545 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43532.9 | 0 | 43532.9 | 180526 | -17272 | 21 | 23 | 180526 | -1017272
2 | 16 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 15.4696 | 0 | 5.9783 | 17.5105 | 0 | 0 | 0 | 7.2 | 119.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38622.2 | 0 | 38622.2 | 193007 | -27435.2 | 16 | 17 | 193007 | -1027435.2
2 | 16 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.6883 | 0 | 5.9347 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23651.9 | 0 | 23651.9 | 169372 | -43206.6 | 16 | 17 | 169372 | -1043206.6
2 | 16 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.7709 | 0 | 5.9174 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12667.3 | 0 | 12667.3 | 154887 | -68917.6 | 16 | 17 | 154887 | -1068917.6
2 | 16 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.9462 | 0 | 5.9083 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11007.1 | 0 | 11007.1 | 148107 | -84086.7 | 17 | 18 | 148107 | -1084086.7
2 | 17 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.7478 | 0 | 5.9189 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11010.6 | 0 | 11010.6 | 159094 | -121405 | 15 | 15 | 159094 | -1121405
2 | 17 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.309 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11013.5 | 0 | 11013.5 | 143602 | -110715 | 15 | 16 | 143602 | -1110715
2 | 17 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.7242 | 0 | 5.9193 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.9866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11016.8 | 0 | 11016.8 | 160497 | -147471 | 14 | 14 | 160497 | -1147471
2 | 17 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.5363 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.7 | 0 | 11018.7 | 140852 | -138926 | 12 | 12 | 140852 | -1138926
2 | 17 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 12.1783 | 0 | 5.9103 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12249.3 | 0 | 12249.3 | 149572 | -167599 | 10 | 11 | 149572 | -1167599
2 | 17 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 15.1632 | 0 | 5.9696 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29874.1 | 0 | 29874.1 | 189499 | -137824 | 10 | 11 | 189499 | -1137824
2 | 17 | 7 | 5 | 49.0171 | 0 | 140.608 | 51.3055 | 0 | 0 | 25.2082 | 19.1159 | 0 | 0 | 0 | 1.2 | 286.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88709.6 | 0 | 88709.6 | 320446 | -959189 | 12 | 12 | 320446 | -1959189
2 | 17 | 8 | 5 | 48.4564 | 0 | 168.222 | 48.7167 | 0 | 0 | 25.2167 | 19.0771 | 0 | 0 | 0 | 0 | 309.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107759 | 0 | 107759 | 382230 | -892088 | 14 | 14 | 382230 | -1892088
2 | 17 | 9 | 5 | 41.8273 | 0 | 173.795 | 42.1622 | 0 | 0 | 25.2305 | 19.0363 | 0 | 0 | 0 | 0 | 302.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149202 | 0 | 149202 | 401176 | -775800 | 16 | 16 | 401176 | -1775800
2 | 17 | 10 | 5 | 40.6866 | 0 | 172.186 | 35.8189 | 0 | 0 | 25.2515 | 19.0363 | 0 | 0 | 0 | 0 | 292.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175581 | 0 | 175581 | 399255 | -645852 | 20 | 22 | 399255 | -1645852
2 | 17 | 11 | 5 | 41.2129 | 0 | 163.102 | 35.4441 | 0 | 0 | 25.2635 | 19.0363 | 0 | 0 | 0 | 0 | 284.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179343 | 0 | 179343 | 387045 | -623692 | 23 | 25 | 387045 | -1623692
2 | 17 | 12 | 5 | 41.1887 | 0 | 149.692 | 30.3817 | 0 | 0 | 25.2831 | 19.0363 | 0 | 0 | 0 | 0 | 265.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179342 | 0 | 179342 | 371723 | -527886 | 26 | 29 | 371723 | -1527886
2 | 17 | 13 | 5 | 39.9301 | 0 | 150.207 | 27.289 | 0 | 0 | 6.2777 | 19.0363 | 0 | 0 | 0 | 0 | 242.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179340 | 0 | 179340 | 354515 | -499561 | 28 | 31 | 354515 | -1499561
2 | 17 | 14 | 5 | 41.2898 | 0 | 165.698 | 0 | 25.4427 | 0 | 6.3085 | 19.0363 | 0 | 0 | 0 | 0 | 257.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179337 | 0 | 179337 | 387959 | -341505 | 31 | 35 | 387959 | -1341505
2 | 17 | 15 | 5 | 40.686 | 0 | 172.702 | 0 | 27.4083 | 0 | 6.3273 | 19.0363 | 0 | 0 | 0 | 0 | 266.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177018 | 0 | 177018 | 422316 | -295059 | 33 | 39 | 422316 | -1295059
2 | 17 | 16 | 5 | 40.5949 | 0 | 173.986 | 0 | 28.6399 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160912 | 0 | 160912 | 435343 | -285937 | 34 | 40 | 435343 | -1285937
2 | 17 | 17 | 5 | 40.7035 | 0 | 169.782 | 0 | 26.4211 | 0 | 6.3187 | 19.0363 | 0 | 0 | 0 | 0 | 262.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131320 | 0 | 131320 | 411188 | -328914 | 32 | 37 | 411188 | -1328914
2 | 17 | 18 | 5 | 47.7173 | 0 | 152.497 | 0 | 25.756 | 0 | 6.3069 | 19.0363 | 0 | 0 | 0 | 2 | 253.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98442.5 | 0 | 98442.5 | 386818 | -378460 | 31 | 36 | 386818 | -1378460
2 | 17 | 19 | 5 | 34.11 | 0 | 93.4203 | 26.57 | 0 | 0 | 25.2972 | 19.0363 | 0 | 0 | 0 | 5.6 | 204.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60893.8 | 0 | 60893.8 | 306869 | -449481 | 30 | 35 | 306869 | -1449481
2 | 17 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 13.4641 | 0 | 5.9409 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43526 | 0 | 43526 | 181456 | -10595.2 | 30 | 35 | 181456 | -1010595.2
2 | 17 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 11.9947 | 0 | 5.9142 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38615.5 | 0 | 38615.5 | 162289 | -15527.1 | 31 | 35 | 162289 | -1015527.1
2 | 17 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.8636 | 0 | 5.9413 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23644.8 | 0 | 23644.8 | 177033 | -21516.3 | 31 | 35 | 177033 | -1021516.3
2 | 17 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.574 | 0 | 5.9183 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12658.8 | 0 | 12658.8 | 160684 | -26491.6 | 34 | 38 | 160684 | -1026491.6
2 | 17 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 12.5289 | 0 | 5.9148 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10998.5 | 0 | 10998.5 | 153765 | -31895.5 | 34 | 38 | 153765 | -1031895.5
2 | 18 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.0309 | 0 | 5.9096 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11002.3 | 0 | 11002.3 | 150223 | -36156.4 | 35 | 38 | 150223 | -1036156.4
2 | 18 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.0554 | 0 | 5.909 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11005.1 | 0 | 11005.1 | 148114 | -42500.2 | 35 | 38 | 148114 | -1042500.2
2 | 18 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.8718 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.2 | 0 | 11008.2 | 146137 | -46881.2 | 35 | 37 | 146137 | -1046881.2
2 | 18 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.9026 | 0 | 5.907 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11010.7 | 0 | 11010.7 | 144971 | -55698 | 35 | 36 | 144971 | -1055698
2 | 18 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.1462 | 0 | 5.9092 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11013 | 0 | 11013 | 146962 | -63415.5 | 35 | 36 | 146962 | -1063415.5
2 | 18 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.6243 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 3.6 | 86.6152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.2 | 0 | 11015.2 | 142419 | -58380.8 | 35 | 37 | 142419 | -1058380.8
2 | 18 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.8224 | 0 | 5.9061 | 17.3638 | 0 | 0 | 0 | 1.2 | 85.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017.2 | 0 | 11017.2 | 143668 | -79451.3 | 33 | 34 | 143668 | -1079451.3
2 | 18 | 8 | 6 | 5.3216 | 0 | 42.7453 | 44.7249 | 0 | 0 | 25.2494 | 19.0143 | 0 | 0 | 0 | 0 | 137.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.8 | 0 | 11018.8 | 127212 | -750719 | 32 | 32 | 127212 | -1750719
2 | 18 | 9 | 6 | 4.9836 | 0 | 42.7453 | 40.2945 | 0 | 0 | 25.2546 | 18.8896 | 0 | 0 | 0 | 0 | 132.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.6 | 0 | 11020.6 | 164941 | -650650 | 33 | 34 | 164941 | -1650650
2 | 18 | 10 | 6 | 5.4766 | 0 | 42.7453 | 28.8086 | 0 | 0 | 25.2648 | 18.8896 | 0 | 0 | 0 | 0 | 121.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014.6 | 0 | 11014.6 | 144435 | -486523 | 34 | 36 | 144435 | -1486523
2 | 18 | 11 | 6 | 5.4748 | 0 | 42.7453 | 26.4427 | 0 | 0 | 25.2632 | 18.8896 | 0 | 0 | 0 | 0 | 118.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11011 | 0 | 11011 | 178473 | -456051 | 36 | 39 | 178473 | -1456051
2 | 18 | 12 | 6 | 5.4743 | 0 | 42.7453 | 24.3617 | 0 | 0 | 25.2618 | 18.8896 | 0 | 0 | 0 | 0 | 116.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11009.7 | 0 | 11009.7 | 174765 | -428902 | 37 | 40 | 174765 | -1428902
2 | 18 | 13 | 6 | 5.7399 | 0 | 42.7453 | 24.3263 | 0 | 0 | 25.2544 | 18.8896 | 0 | 0 | 0 | 0 | 116.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.9 | 0 | 11008.9 | 168665 | -443410 | 36 | 39 | 168665 | -1443410
2 | 18 | 14 | 6 | 6.0929 | 0 | 42.7453 | 24.2438 | 0 | 0 | 6.2493 | 18.8896 | 0 | 0 | 0 | 0 | 98.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.6 | 0 | 11008.6 | 169137 | -451152 | 36 | 39 | 169137 | -1451152
2 | 18 | 15 | 6 | 6.1701 | 0 | 42.7453 | 0 | 9.2814 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 76.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.5 | 0 | 11008.5 | 124796 | -9853.59 | 36 | 39 | 124796 | -1009853.59
2 | 18 | 16 | 6 | 6.4096 | 0 | 42.7453 | 0 | 8.7585 | 0 | 5.8975 | 12.8287 | 0 | 0 | 0 | 0 | 76.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.6 | 0 | 11008.6 | 122453 | -11663.3 | 35 | 38 | 122453 | -1011663.3
2 | 18 | 17 | 6 | 5.9708 | 0 | 42.7453 | 0 | 10.4681 | 0 | 5.8987 | 14.8767 | 0 | 0 | 0 | 0 | 79.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11010.7 | 0 | 11010.7 | 136942 | -17889 | 33 | 36 | 136942 | -1017889
2 | 18 | 18 | 6 | 8.1766 | 0 | 42.7453 | 0 | 11.0339 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 2 | 87.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11013.6 | 0 | 11013.6 | 142623 | -28425.2 | 31 | 33 | 142623 | -1028425.2
2 | 18 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.5287 | 0 | 5.9034 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.9384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.6 | 0 | 11015.6 | 139816 | -43624.2 | 27 | 28 | 139816 | -1043624.2
2 | 18 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2952 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.3 | 0 | 11018.3 | 137613 | -59832.6 | 28 | 29 | 137613 | -1059832.6
2 | 18 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.7905 | 0 | 5.9055 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021 | 0 | 11021 | 142323 | -79000.9 | 26 | 26 | 142323 | -1079000.9
2 | 18 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3848 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.5 | 0 | 11023.5 | 134526 | -82090.3 | 24 | 24 | 134526 | -1082090.3
2 | 18 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.8895 | 0 | 5.9066 | 17.3638 | 0 | 0 | 0 | 6.4 | 93.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.9 | 0 | 11025.9 | 144322 | -105049 | 25 | 25 | 144322 | -1105049
2 | 18 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2285 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.7 | 0 | 11027.7 | 132973 | -96558 | 23 | 24 | 132973 | -1096558
2 | 19 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.2677 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4099.69 | 0 | 4099.69 | 134298 | -118021 | 22 | 23 | 134298 | -1118021
2 | 19 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.2066 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.1186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4101.05 | 0 | 4101.05 | 131416 | -122764 | 22 | 23 | 131416 | -1122764
2 | 19 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7201 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4102.73 | 0 | 4102.73 | 133536 | -145780 | 21 | 22 | 133536 | -1145780
2 | 19 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.6853 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4104.19 | 0 | 4104.19 | 130084 | -153059 | 19 | 20 | 130084 | -1153059
2 | 19 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7872 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4106.56 | 0 | 4106.56 | 129470 | -153197 | 19 | 20 | 129470 | -1153197
2 | 19 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4656 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.59 | 0 | 4108.59 | 128906 | -167055 | 18 | 19 | 128906 | -1167055
2 | 19 | 7 | 7 | 5.1054 | 0 | 42.7453 | 10.9141 | 0 | 0 | 8.3404 | 17.3638 | 0 | 0 | 0 | 1.2 | 85.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4109.95 | 0 | 4109.95 | 129942 | -199905 | 17 | 17 | 129942 | -1199905
2 | 19 | 8 | 7 | 4.1884 | 0 | 42.7453 | 10.4018 | 0 | 0 | 8.0093 | 17.3638 | 0 | 0 | 0 | 0 | 82.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.41 | 0 | 4111.41 | 127892 | -174511 | 20 | 21 | 127892 | -1174511
2 | 19 | 9 | 7 | 3.8517 | 0 | 42.7453 | 0 | 10.3623 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 80.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.73 | 0 | 4113.73 | 132263 | -140415 | 23 | 26 | 132263 | -1140415
2 | 19 | 10 | 7 | 4.1511 | 0 | 42.7453 | 0 | 10.2642 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.74 | 0 | 4115.74 | 129073 | -102655 | 24 | 28 | 129073 | -1102655
2 | 19 | 11 | 7 | 4.1519 | 0 | 42.7453 | 0 | 10.5893 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 0 | 80.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4117.77 | 0 | 4117.77 | 132674 | -89961.9 | 26 | 31 | 132674 | -1089961.9
2 | 19 | 12 | 7 | 4.1506 | 0 | 42.7453 | 0 | 10.7268 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 80.8851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.01 | 0 | 4119.01 | 131996 | -83101.7 | 26 | 32 | 131996 | -1083101.7
2 | 19 | 13 | 7 | 4.152 | 0 | 42.7453 | 0 | 10.9435 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 0 | 81.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.77 | 0 | 4119.77 | 132668 | -67710.4 | 28 | 35 | 132668 | -1067710.4
2 | 19 | 14 | 7 | 4.1524 | 0 | 42.7453 | 0 | 11.2014 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 0 | 81.3638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.41 | 0 | 4120.41 | 135931 | -60165.9 | 30 | 38 | 135931 | -1060165.9
2 | 19 | 15 | 7 | 4.1534 | 0 | 42.7453 | 0 | 10.569 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 80.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.68 | 0 | 4120.68 | 134306 | -52636.4 | 31 | 39 | 134306 | -1052636.4
2 | 19 | 16 | 7 | 4.1798 | 0 | 42.7453 | 0 | 10.4274 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 80.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.83 | 0 | 4120.83 | 134977 | -47964.9 | 32 | 40 | 134977 | -1047964.9
2 | 19 | 17 | 7 | 4.2368 | 0 | 42.7453 | 0 | 10.1195 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.01 | 0 | 4121.01 | 133968 | -46948 | 32 | 40 | 133968 | -1046948
2 | 19 | 18 | 7 | 6.168 | 0 | 42.7453 | 0 | 10.11 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 2 | 84.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.35 | 0 | 4121.35 | 132247 | -58165.2 | 28 | 32 | 132247 | -1058165.2
2 | 19 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.0127 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.2822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.93 | 0 | 4121.93 | 130454 | -67382.5 | 27 | 31 | 130454 | -1067382.5
2 | 19 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.9771 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.8 | 0 | 4122.8 | 128925 | -77054.6 | 26 | 28 | 128925 | -1077054.6
2 | 19 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.9333 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.96 | 0 | 4123.96 | 127411 | -91187.4 | 24 | 26 | 127411 | -1091187.4
2 | 19 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5659 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.04 | 0 | 4125.04 | 126668 | -106222 | 25 | 27 | 126668 | -1106222
2 | 19 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4434 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4126.13 | 0 | 4126.13 | 128241 | -135702 | 24 | 26 | 128241 | -1135702
2 | 19 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2615 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4127.16 | 0 | 4127.16 | 125899 | -143510 | 24 | 26 | 125899 | -1143510
2 | 20 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.991 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.06 | 0 | 4129.06 | 133884 | -161089 | 24 | 25 | 133884 | -1161089
2 | 20 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.1595 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.63 | 0 | 4130.63 | 125099 | -147634 | 23 | 24 | 125099 | -1147634
2 | 20 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.2993 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.21 | 0 | 4132.21 | 128303 | -166433 | 25 | 26 | 128303 | -1166433
2 | 20 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.2452 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.03 | 0 | 4133.03 | 124777 | -165439 | 26 | 27 | 124777 | -1165439
2 | 20 | 5 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.3635 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.73 | 0 | 4134.73 | 124616 | -156698 | 27 | 28 | 124616 | -1156698
2 | 20 | 6 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.4855 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.15 | 0 | 4136.15 | 125631 | -166803 | 25 | 26 | 125631 | -1166803
2 | 20 | 7 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.4124 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.98 | 0 | 4136.98 | 124151 | -169744 | 24 | 25 | 124151 | -1169744
2 | 20 | 8 | 8 | 4.2304 | 0 | 42.7453 | 0 | 10.4673 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.91 | 0 | 4137.91 | 124635 | -161809 | 25 | 26 | 124635 | -1161809
2 | 20 | 9 | 8 | 3.8133 | 0 | 42.7453 | 0 | 10.1279 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 79.9472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4138.73 | 0 | 4138.73 | 124301 | -122906 | 27 | 29 | 124301 | -1122906
2 | 20 | 10 | 8 | 4.1501 | 0 | 42.7453 | 0 | 11.2437 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 0 | 81.4043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.5 | 0 | 4139.5 | 137286 | -103320 | 33 | 37 | 137286 | -1103320
2 | 20 | 11 | 8 | 4.1492 | 0 | 42.7453 | 0 | 9.44 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 79.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.1 | 0 | 4140.1 | 127201 | -66342.3 | 35 | 40 | 127201 | -1066342.3
2 | 20 | 12 | 8 | 4.1475 | 0 | 42.7453 | 0 | 10.9604 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 0 | 81.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.26 | 0 | 4141.26 | 132320 | -67847.7 | 36 | 42 | 132320 | -1067847.7
2 | 20 | 13 | 8 | 4.1489 | 0 | 42.7453 | 0 | 9.7866 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 79.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.73 | 0 | 4140.73 | 127807 | -57228.1 | 38 | 44 | 127807 | -1057228.1
2 | 20 | 14 | 8 | 4.5442 | 0 | 42.7453 | 0 | 10.1451 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 80.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.11 | 0 | 4141.11 | 129309 | -57574.1 | 38 | 44 | 129309 | -1057574.1
2 | 20 | 15 | 8 | 4.5805 | 0 | 42.7453 | 0 | 9.6038 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 80.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.51 | 0 | 4141.51 | 126943 | -58027.3 | 37 | 43 | 126943 | -1058027.3
2 | 20 | 16 | 8 | 4.9491 | 0 | 42.7453 | 0 | 9.8196 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142.05 | 0 | 4142.05 | 126608 | -66946.9 | 37 | 43 | 126608 | -1066946.9
2 | 20 | 17 | 8 | 5.6204 | 0 | 42.7453 | 0 | 9.8843 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 81.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142.69 | 0 | 4142.69 | 125998 | -73029.3 | 37 | 42 | 125998 | -1073029.3
2 | 20 | 18 | 8 | 6.5429 | 0 | 42.7453 | 0 | 10.3078 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 2 | 84.8572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4143.32 | 0 | 4143.32 | 128406 | -82799.7 | 35 | 40 | 128406 | -1082799.7
2 | 20 | 19 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.5261 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.15 | 0 | 4144.15 | 125217 | -88055.8 | 36 | 40 | 125217 | -1088055.8
2 | 20 | 20 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.5311 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.95 | 0 | 4144.95 | 125121 | -102246 | 35 | 37 | 125121 | -1102246
2 | 20 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.3884 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4145.58 | 0 | 4145.58 | 125042 | -114436 | 36 | 36 | 125042 | -1114436
2 | 20 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.5686 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4146.13 | 0 | 4146.13 | 124784 | -119374 | 36 | 36 | 124784 | -1119374
2 | 20 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.4167 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.04 | 0 | 4147.04 | 124658 | -114472 | 36 | 36 | 124658 | -1114472
2 | 20 | 24 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.4578 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.91 | 0 | 4147.91 | 126132 | -131488 | 36 | 36 | 126132 | -1131488
2 | 21 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3711 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11078.6 | 0 | 11078.6 | 124783 | -126378 | 36 | 37 | 124783 | -1126378
2 | 21 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3555 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11079.6 | 0 | 11079.6 | 124951 | -134305 | 35 | 36 | 124951 | -1134305
2 | 21 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3455 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11079.7 | 0 | 11079.7 | 124837 | -136623 | 35 | 36 | 124837 | -1136623
2 | 21 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3227 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11080.2 | 0 | 11080.2 | 124735 | -141779 | 34 | 36 | 124735 | -1141779
2 | 21 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 10.5619 | 0 | 5.8978 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12308.4 | 0 | 12308.4 | 128175 | -144109 | 34 | 36 | 128175 | -1144109
2 | 21 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.0004 | 0 | 5.942 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29932.1 | 0 | 29932.1 | 175959 | -112645 | 34 | 36 | 175959 | -1112645
2 | 21 | 7 | 2 | 49.0171 | 0 | 140.608 | 47.2845 | 0 | 0 | 25.2305 | 19.2156 | 0 | 0 | 0 | 1.2 | 282.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88766.4 | 0 | 88766.4 | 311484 | -801421 | 34 | 35 | 311484 | -1801421
2 | 21 | 8 | 2 | 51.1101 | 0 | 168.222 | 41.7363 | 0 | 0 | 25.2459 | 19.108 | 0 | 0 | 0 | 0 | 305.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107815 | 0 | 107815 | 374034 | -713077 | 34 | 34 | 374034 | -1713077
2 | 21 | 9 | 2 | 44.7435 | 0 | 173.795 | 30.2693 | 0 | 0 | 25.2572 | 19.0363 | 0 | 0 | 0 | 0 | 293.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149242 | 0 | 149242 | 393062 | -562725 | 35 | 35 | 393062 | -1562725
2 | 21 | 10 | 2 | 42.1949 | 0 | 172.186 | 29.1365 | 0 | 0 | 25.2687 | 19.0363 | 0 | 0 | 0 | 0 | 287.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175619 | 0 | 175619 | 396175 | -529087 | 35 | 35 | 396175 | -1529087
2 | 21 | 11 | 2 | 41.9939 | 0 | 163.102 | 28.0006 | 0 | 0 | 25.2847 | 19.0363 | 0 | 0 | 0 | 0 | 277.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179379 | 0 | 179379 | 380638 | -486428 | 36 | 36 | 380638 | -1486428
2 | 21 | 12 | 2 | 41.0448 | 0 | 149.692 | 0 | 25.8473 | 0 | 6.2819 | 19.0363 | 0 | 0 | 0 | 0 | 241.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179377 | 0 | 179377 | 374207 | -444790 | 35 | 36 | 374207 | -1444790
2 | 21 | 13 | 2 | 39.8692 | 0 | 150.207 | 24.9715 | 0 | 0 | 25.2786 | 19.0363 | 0 | 0 | 0 | 0 | 259.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179374 | 0 | 179374 | 348041 | -454420 | 34 | 34 | 348041 | -1454420
2 | 21 | 14 | 2 | 41.6832 | 0 | 165.698 | 0 | 24.1843 | 0 | 6.2733 | 19.0363 | 0 | 0 | 0 | 0 | 256.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179371 | 0 | 179371 | 381206 | -430387 | 32 | 32 | 381206 | -1430387
2 | 21 | 15 | 2 | 41.1873 | 0 | 172.702 | 0 | 25.3768 | 0 | 6.2823 | 19.0363 | 0 | 0 | 0 | 0 | 264.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177050 | 0 | 177050 | 400045 | -421196 | 32 | 32 | 400045 | -1421196
2 | 21 | 16 | 2 | 41.3856 | 0 | 173.986 | 0 | 25.5909 | 0 | 6.2868 | 19.0363 | 0 | 0 | 0 | 0 | 266.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160945 | 0 | 160945 | 403221 | -421753 | 33 | 33 | 403221 | -1421753
2 | 21 | 17 | 2 | 45.1031 | 0 | 169.782 | 0 | 25.4787 | 0 | 6.2823 | 19.0363 | 0 | 0 | 0 | 0 | 265.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131354 | 0 | 131354 | 396408 | -452344 | 33 | 33 | 396408 | -1452344
2 | 21 | 18 | 2 | 47.7656 | 0 | 152.497 | 27.0946 | 0 | 0 | 25.2852 | 19.0363 | 0 | 0 | 0 | 2 | 273.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98476.5 | 0 | 98476.5 | 379078 | -473417 | 34 | 34 | 379078 | -1473417
2 | 21 | 19 | 2 | 34.11 | 0 | 93.4203 | 31.7882 | 0 | 0 | 25.2893 | 19.0363 | 0 | 0 | 0 | 5.6 | 209.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60927.2 | 0 | 60927.2 | 294434 | -523649 | 33 | 33 | 294434 | -1523649
2 | 21 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 13.2622 | 0 | 5.9351 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43558.7 | 0 | 43558.7 | 176499 | -11103.3 | 33 | 33 | 176499 | -1011103.3
2 | 21 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.2558 | 0 | 5.9142 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38648.4 | 0 | 38648.4 | 157586 | -17864.7 | 33 | 33 | 157586 | -1017864.7
2 | 21 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.5317 | 0 | 5.9311 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23678.3 | 0 | 23678.3 | 166940 | -31814.2 | 33 | 33 | 166940 | -1031814.2
2 | 21 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.3504 | 0 | 5.9124 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.7039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12692.8 | 0 | 12692.8 | 151384 | -51584.5 | 33 | 33 | 151384 | -1051584.5
2 | 21 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.775 | 0 | 5.9061 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11032.5 | 0 | 11032.5 | 144608 | -65568.6 | 32 | 32 | 144608 | -1065568.6
2 | 22 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.488 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.1 | 0 | 11036.1 | 141669 | -78961.7 | 31 | 31 | 141669 | -1078961.7
2 | 22 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3179 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.8 | 0 | 11038.8 | 140084 | -94560.8 | 29 | 30 | 140084 | -1094560.8
2 | 22 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.2078 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.4 | 0 | 11041.4 | 139028 | -106233 | 29 | 30 | 139028 | -1106233
2 | 22 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.1026 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11043.5 | 0 | 11043.5 | 138115 | -118219 | 28 | 30 | 138115 | -1118219
2 | 22 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.2571 | 0 | 5.9023 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12273.1 | 0 | 12273.1 | 140581 | -129259 | 27 | 29 | 140581 | -1129259
2 | 22 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.565 | 0 | 5.9585 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29898.1 | 0 | 29898.1 | 187721 | -117098 | 25 | 26 | 187721 | -1117098
2 | 22 | 7 | 3 | 49.0171 | 0 | 140.608 | 49.2052 | 0 | 0 | 25.2198 | 19.1727 | 0 | 0 | 0 | 1.2 | 284.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88733.6 | 0 | 88733.6 | 319242 | -861558 | 24 | 25 | 319242 | -1861558
2 | 22 | 8 | 3 | 42.7876 | 0 | 168.222 | 45.69 | 0 | 0 | 25.2308 | 19.0533 | 0 | 0 | 0 | 0 | 300.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107783 | 0 | 107783 | 381266 | -790802 | 22 | 24 | 381266 | -1790802
2 | 22 | 9 | 3 | 40.249 | 0 | 173.795 | 35.2064 | 0 | 0 | 25.2418 | 19.0363 | 0 | 0 | 0 | 0 | 293.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149222 | 0 | 149222 | 400093 | -647939 | 21 | 23 | 400093 | -1647939
2 | 22 | 10 | 3 | 40.956 | 0 | 172.186 | 32.2055 | 0 | 0 | 25.2608 | 19.0363 | 0 | 0 | 0 | 0 | 289.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175599 | 0 | 175599 | 398157 | -576444 | 22 | 24 | 398157 | -1576444
2 | 22 | 11 | 3 | 41.2533 | 0 | 163.102 | 33.2502 | 0 | 0 | 25.2658 | 19.0363 | 0 | 0 | 0 | 0 | 281.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179361 | 0 | 179361 | 387915 | -577907 | 22 | 24 | 387915 | -1577907
2 | 22 | 12 | 3 | 40.774 | 0 | 149.692 | 30.3637 | 0 | 0 | 25.2882 | 19.0363 | 0 | 0 | 0 | 0 | 265.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179360 | 0 | 179360 | 372595 | -508816 | 22 | 25 | 372595 | -1508816
2 | 22 | 13 | 3 | 39.8453 | 0 | 150.207 | 27.6537 | 0 | 0 | 25.2893 | 19.0363 | 0 | 0 | 0 | 0 | 262.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179358 | 0 | 179358 | 353339 | -483720 | 23 | 26 | 353339 | -1483720
2 | 22 | 14 | 3 | 41.3279 | 0 | 165.698 | 0 | 25.2063 | 0 | 6.2872 | 19.0363 | 0 | 0 | 0 | 0 | 257.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179355 | 0 | 179355 | 386384 | -436667 | 22 | 26 | 386384 | -1436667
2 | 22 | 15 | 3 | 40.7222 | 0 | 172.702 | 0 | 25.6797 | 0 | 6.2891 | 19.0363 | 0 | 0 | 0 | 0 | 264.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177035 | 0 | 177035 | 404958 | -429370 | 22 | 26 | 404958 | -1429370
2 | 22 | 16 | 3 | 40.8977 | 0 | 173.986 | 0 | 25.8583 | 0 | 6.2846 | 19.0363 | 0 | 0 | 0 | 0 | 266.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160931 | 0 | 160931 | 407745 | -454225 | 21 | 25 | 407745 | -1454225
2 | 22 | 17 | 3 | 41.2973 | 0 | 169.782 | 27.0822 | 0 | 0 | 6.276 | 19.0363 | 0 | 0 | 0 | 0 | 263.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131341 | 0 | 131341 | 401277 | -521881 | 20 | 23 | 401277 | -1521881
2 | 22 | 18 | 3 | 45.2195 | 0 | 152.497 | 35.1266 | 0 | 0 | 19.0747 | 19.0363 | 0 | 0 | 0 | 2 | 272.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98464.8 | 0 | 98464.8 | 394991 | -650986 | 17 | 19 | 394991 | -1650986
2 | 22 | 19 | 3 | 34.11 | 0 | 93.4203 | 44.0304 | 0 | 0 | 25.2573 | 19.0363 | 0 | 0 | 0 | 5.6 | 221.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60916.9 | 0 | 60916.9 | 314812 | -712323 | 15 | 17 | 314812 | -1712323
2 | 22 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.0056 | 0 | 5.9463 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43549.7 | 0 | 43549.7 | 179154 | -19394.8 | 15 | 17 | 179154 | -1019394.8
2 | 22 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.0629 | 0 | 5.949 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38638.6 | 0 | 38638.6 | 184131 | -45883.2 | 15 | 17 | 184131 | -1045883.2
2 | 22 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.6791 | 0 | 5.9218 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23668.6 | 0 | 23668.6 | 165843 | -85524.5 | 13 | 15 | 165843 | -1085524.5
2 | 22 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.6414 | 0 | 5.9191 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12684.7 | 0 | 12684.7 | 161468 | -113293 | 13 | 15 | 161468 | -1113293
2 | 22 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.7353 | 0 | 5.9061 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.9 | 0 | 11024.9 | 145290 | -117612 | 12 | 13 | 145290 | -1117612
2 | 23 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.9132 | 0 | 5.9077 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.2 | 0 | 11029.2 | 147026 | -142807 | 10 | 11 | 147026 | -1142807
2 | 23 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.5795 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.7 | 0 | 11031.7 | 141449 | -151075 | 10 | 10 | 141449 | -1151075
2 | 23 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6361 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.9 | 0 | 11033.9 | 142100 | -165752 | 9 | 10 | 142100 | -1165752
2 | 23 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.4427 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11035.7 | 0 | 11035.7 | 138930 | -172165 | 8 | 9 | 138930 | -1172165
2 | 23 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.5468 | 0 | 5.9037 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12265 | 0 | 12265 | 140691 | -189908 | 7 | 8 | 140691 | -1189908
2 | 23 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.353 | 0 | 5.9548 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29889.8 | 0 | 29889.8 | 187102 | -173445 | 6 | 7 | 187102 | -1173445
2 | 23 | 7 | 4 | 48.9905 | 0 | 140.608 | 60.6337 | 0 | 0 | 25.2092 | 19.2319 | 0 | 0 | 0 | 1.2 | 295.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88725 | 0 | 88725 | 318687 | -1102950 | 5 | 6 | 318687 | -2102950
2 | 23 | 8 | 4 | 42.2299 | 0 | 168.222 | 53.7463 | 0 | 0 | 25.2095 | 19.0804 | 0 | 0 | 0 | 0 | 308.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107774 | 0 | 107774 | 380954 | -978222 | 8 | 9 | 380954 | -1978222
2 | 23 | 9 | 4 | 40.44 | 0 | 173.795 | 41.1199 | 0 | 0 | 25.2253 | 19.0363 | 0 | 0 | 0 | 0 | 299.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149214 | 0 | 149214 | 400202 | -766913 | 10 | 12 | 400202 | -1766913
2 | 23 | 10 | 4 | 40.857 | 0 | 172.186 | 36.0684 | 0 | 0 | 25.2413 | 19.0363 | 0 | 0 | 0 | 0 | 293.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175593 | 0 | 175593 | 398036 | -672534 | 12 | 15 | 398036 | -1672534
2 | 23 | 11 | 4 | 41.2329 | 0 | 163.102 | 36.8678 | 0 | 0 | 25.246 | 19.0363 | 0 | 0 | 0 | 0 | 285.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179355 | 0 | 179355 | 383987 | -664061 | 14 | 17 | 383987 | -1664061
2 | 23 | 12 | 4 | 40.7693 | 0 | 149.692 | 34.5269 | 0 | 0 | 25.2651 | 19.0363 | 0 | 0 | 0 | 0 | 269.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179355 | 0 | 179355 | 368180 | -596993 | 15 | 18 | 368180 | -1596993
2 | 23 | 13 | 4 | 39.8421 | 0 | 150.207 | 33.255 | 0 | 0 | 25.2682 | 19.0363 | 0 | 0 | 0 | 0 | 267.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 352818 | -580711 | 16 | 19 | 352818 | -1580711
2 | 23 | 14 | 4 | 41.324 | 0 | 165.698 | 27.8252 | 0 | 0 | 25.2716 | 19.0363 | 0 | 0 | 0 | 0 | 279.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179350 | 0 | 179350 | 385908 | -521708 | 16 | 20 | 385908 | -1521708
2 | 23 | 15 | 4 | 40.7177 | 0 | 172.702 | 26.532 | 0 | 0 | 25.2751 | 19.0363 | 0 | 0 | 0 | 0 | 284.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177030 | 0 | 177030 | 404300 | -513308 | 15 | 20 | 404300 | -1513308
2 | 23 | 16 | 4 | 40.7687 | 0 | 173.986 | 27.6758 | 0 | 0 | 25.2712 | 19.0363 | 0 | 0 | 0 | 0 | 286.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160926 | 0 | 160926 | 407855 | -532438 | 16 | 20 | 407855 | -1532438
2 | 23 | 17 | 4 | 41.111 | 0 | 169.782 | 31.9841 | 0 | 0 | 25.2593 | 19.0363 | 0 | 0 | 0 | 0 | 287.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131337 | 0 | 131337 | 400246 | -609107 | 15 | 18 | 400246 | -1609107
2 | 23 | 18 | 4 | 44.8895 | 0 | 152.497 | 40.528 | 0 | 0 | 25.2429 | 19.0363 | 0 | 0 | 0 | 2 | 284.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98460.6 | 0 | 98460.6 | 385958 | -737161 | 11 | 14 | 385958 | -1737161
2 | 23 | 19 | 4 | 34.11 | 0 | 93.4203 | 49.8276 | 0 | 0 | 25.2425 | 19.0363 | 0 | 0 | 0 | 5.6 | 227.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60913 | 0 | 60913 | 320290 | -804260 | 10 | 12 | 320290 | -1804260
2 | 23 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 16.2646 | 0 | 6.0162 | 17.5105 | 0 | 0 | 0 | 7.2 | 134.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43545.5 | 0 | 43545.5 | 213913 | -19591.6 | 9 | 11 | 213913 | -1019591.6
2 | 23 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.6369 | 0 | 5.9416 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38634.3 | 0 | 38634.3 | 181033 | -66963.8 | 8 | 9 | 181033 | -1066963.8
2 | 23 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.7631 | 0 | 5.9411 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23664.9 | 0 | 23664.9 | 178406 | -109159 | 8 | 9 | 178406 | -1109159
2 | 23 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.1289 | 0 | 5.9104 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681.3 | 0 | 12681.3 | 150142 | -115492 | 7 | 8 | 150142 | -1115492
2 | 23 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 12.1722 | 0 | 5.9105 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.6 | 0 | 11021.6 | 149946 | -146569 | 7 | 8 | 149946 | -1146569
2 | 24 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.6899 | 0 | 5.9049 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.9 | 0 | 11024.9 | 142196 | -153924 | 5 | 6 | 142196 | -1153924
2 | 24 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.7418 | 0 | 5.9054 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.3 | 0 | 11027.3 | 143053 | -179185 | 5 | 6 | 143053 | -1179185
2 | 24 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.0002 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.4 | 0 | 11029.4 | 139261 | -189953 | 4 | 5 | 139261 | -1189953
2 | 24 | 4 | 5 | 10.8489 | 0 | 42.3304 | 12.3574 | 0 | 0 | 9.7998 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.2 | 0 | 11031.2 | 144115 | -227305 | 3 | 4 | 144115 | -1227305
2 | 24 | 5 | 5 | 11.8202 | 0 | 44.8242 | 13.9972 | 0 | 0 | 11.3309 | 17.5105 | 0 | 0 | 0 | 4.8 | 104.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12260.5 | 0 | 12260.5 | 139553 | -233416 | 3 | 4 | 139553 | -1233416
2 | 24 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 15.9594 | 0 | 5.9991 | 17.5105 | 0 | 0 | 0 | 3.6 | 137.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29886.8 | 0 | 29886.8 | 209526 | -238151 | 3 | 4 | 209526 | -1238151
2 | 24 | 7 | 5 | 49.0171 | 0 | 140.608 | 65.3953 | 0 | 0 | 25.2135 | 19.2877 | 0 | 0 | 0 | 1.2 | 300.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88723 | 0 | 88723 | 317965 | -1179550 | 3 | 4 | 317965 | -2179550
2 | 24 | 8 | 5 | 42.4446 | 0 | 168.222 | 61.943 | 0 | 0 | 25.208 | 19.1472 | 0 | 0 | 0 | 0 | 316.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107774 | 0 | 107774 | 379999 | -1128220 | 4 | 5 | 379999 | -2128220
2 | 24 | 9 | 5 | 40.1197 | 0 | 173.795 | 47.969 | 0 | 0 | 25.2137 | 19.0363 | 0 | 0 | 0 | 0 | 306.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149212 | 0 | 149212 | 399561 | -893625 | 7 | 9 | 399561 | -1893625
2 | 24 | 10 | 5 | 40.7601 | 0 | 172.186 | 42.4404 | 0 | 0 | 25.2249 | 19.0363 | 0 | 0 | 0 | 0 | 299.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175591 | 0 | 175591 | 397438 | -785875 | 10 | 13 | 397438 | -1785875
2 | 24 | 11 | 5 | 41.2196 | 0 | 163.102 | 41.3066 | 0 | 0 | 25.2328 | 19.0363 | 0 | 0 | 0 | 0 | 289.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 378862 | -746435 | 13 | 16 | 378862 | -1746435
2 | 24 | 12 | 5 | 40.7445 | 0 | 149.692 | 37.0794 | 0 | 0 | 25.2495 | 19.0363 | 0 | 0 | 0 | 0 | 271.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179353 | 0 | 179353 | 362458 | -650843 | 15 | 18 | 362458 | -1650843
2 | 24 | 13 | 5 | 39.8127 | 0 | 150.207 | 33.7601 | 0 | 0 | 25.2576 | 19.0363 | 0 | 0 | 0 | 0 | 268.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179351 | 0 | 179351 | 352404 | -611676 | 17 | 20 | 352404 | -1611676
2 | 24 | 14 | 5 | 41.2984 | 0 | 165.698 | 28.6477 | 0 | 0 | 6.2605 | 19.0363 | 0 | 0 | 0 | 0 | 260.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179348 | 0 | 179348 | 385435 | -555160 | 18 | 21 | 385435 | -1555160
2 | 24 | 15 | 5 | 40.6924 | 0 | 172.702 | 28.0576 | 0 | 0 | 6.265 | 19.0363 | 0 | 0 | 0 | 0 | 266.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177028 | 0 | 177028 | 404161 | -545548 | 18 | 22 | 404161 | -1545548
2 | 24 | 16 | 5 | 40.5921 | 0 | 173.986 | 27.9877 | 0 | 0 | 6.2664 | 19.0363 | 0 | 0 | 0 | 0 | 267.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160924 | 0 | 160924 | 407132 | -546161 | 18 | 22 | 407132 | -1546161
2 | 24 | 17 | 5 | 40.5136 | 0 | 169.782 | 32.7755 | 0 | 0 | 6.2525 | 19.0363 | 0 | 0 | 0 | 0 | 268.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131334 | 0 | 131334 | 402630 | -632203 | 16 | 20 | 402630 | -1632203
2 | 24 | 18 | 5 | 44.3372 | 0 | 152.497 | 40.6498 | 0 | 0 | 18.4379 | 19.0363 | 0 | 0 | 0 | 2 | 276.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98458 | 0 | 98458 | 394200 | -743575 | 14 | 17 | 394200 | -1743575
2 | 24 | 19 | 5 | 34.11 | 0 | 93.4203 | 48.3848 | 0 | 0 | 25.2461 | 19.0363 | 0 | 0 | 0 | 5.6 | 225.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60910.4 | 0 | 60910.4 | 313811 | -793742 | 12 | 14 | 313811 | -1793742
2 | 24 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 16.4109 | 0 | 6.0192 | 17.5105 | 0 | 0 | 0 | 7.2 | 134.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43542.9 | 0 | 43542.9 | 213923 | -19658.3 | 10 | 12 | 213923 | -1019658.3
2 | 24 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.7376 | 0 | 5.9428 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38631.9 | 0 | 38631.9 | 180885 | -56936.9 | 10 | 12 | 180885 | -1056936.9
2 | 24 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.1511 | 0 | 5.9285 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23662.4 | 0 | 23662.4 | 169502 | -98717.9 | 10 | 12 | 169502 | -1098717.9
2 | 24 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.0381 | 0 | 5.9097 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12678.7 | 0 | 12678.7 | 150191 | -120932 | 9 | 10 | 150191 | -1120932
2 | 24 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.9578 | 0 | 5.9084 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.9 | 0 | 11018.9 | 148238 | -147833 | 8 | 9 | 148238 | -1147833
2 | 25 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.5495 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.4 | 0 | 11022.4 | 141756 | -162294 | 7 | 8 | 141756 | -1162294
2 | 25 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.5946 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025 | 0 | 11025 | 142243 | -177477 | 7 | 8 | 142243 | -1177477
2 | 25 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3717 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027.9 | 0 | 11027.9 | 138726 | -185947 | 6 | 7 | 138726 | -1185947
2 | 25 | 4 | 6 | 6.3817 | 0 | 42.7453 | 11.8788 | 0 | 0 | 8.97 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11030 | 0 | 11030 | 138663 | -198809 | 5 | 6 | 138663 | -1198809
2 | 25 | 5 | 6 | 6.3817 | 0 | 42.7453 | 12.2623 | 0 | 0 | 9.2849 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11032 | 0 | 11032 | 136341 | -201985 | 6 | 7 | 136341 | -1201985
2 | 25 | 6 | 6 | 6.3817 | 0 | 42.7453 | 12.6861 | 0 | 0 | 9.6599 | 17.3638 | 0 | 0 | 0 | 3.6 | 92.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.8 | 0 | 11033.8 | 136034 | -209678 | 6 | 7 | 136034 | -1209678
2 | 25 | 7 | 6 | 6.3732 | 0 | 42.7453 | 12.9875 | 0 | 0 | 9.9285 | 17.3638 | 0 | 0 | 0 | 1.2 | 90.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11035.5 | 0 | 11035.5 | 134325 | -212375 | 6 | 7 | 134325 | -1212375
2 | 25 | 8 | 6 | 4.9799 | 0 | 42.7453 | 69.2811 | 0 | 0 | 25.2143 | 19.5242 | 0 | 0 | 0 | 0 | 161.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.1 | 0 | 11037.1 | 122273 | -1093670 | 7 | 8 | 122273 | -2093670
2 | 25 | 9 | 6 | 5.0639 | 0 | 42.7453 | 60.2333 | 0 | 0 | 25.2311 | 19.067 | 0 | 0 | 0 | 0 | 152.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.3 | 0 | 11038.3 | 121633 | -915963 | 9 | 11 | 121633 | -1915963
2 | 25 | 10 | 6 | 5.5277 | 0 | 42.7453 | 46.5379 | 0 | 0 | 25.244 | 18.8896 | 0 | 0 | 0 | 0 | 138.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.4 | 0 | 11026.4 | 121148 | -728680 | 13 | 16 | 121148 | -1728680
2 | 25 | 11 | 6 | 5.4783 | 0 | 42.7453 | 40.2303 | 0 | 0 | 25.249 | 18.8896 | 0 | 0 | 0 | 0 | 132.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.3 | 0 | 11023.3 | 120673 | -649813 | 15 | 18 | 120673 | -1649813
2 | 25 | 12 | 6 | 5.4761 | 0 | 42.7453 | 34.0084 | 0 | 0 | 25.2559 | 18.8896 | 0 | 0 | 0 | 0 | 126.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.3 | 0 | 11021.3 | 120321 | -566659 | 19 | 23 | 120321 | -1566659
2 | 25 | 13 | 6 | 5.4789 | 0 | 42.7453 | 30.6311 | 0 | 0 | 6.2623 | 18.8896 | 0 | 0 | 0 | 0 | 104.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.2 | 0 | 11020.2 | 119828 | -532910 | 19 | 24 | 119828 | -1532910
2 | 25 | 14 | 6 | 5.4797 | 0 | 42.7453 | 28.9929 | 0 | 0 | 6.2609 | 18.8896 | 0 | 0 | 0 | 0 | 102.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11019.5 | 0 | 11019.5 | 119568 | -510597 | 21 | 26 | 119568 | -1510597
2 | 25 | 15 | 6 | 5.4807 | 0 | 42.7453 | 0 | 10.1956 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 0 | 77.1471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.9 | 0 | 11018.9 | 122610 | -17195.7 | 20 | 26 | 122610 | -1017195.7
2 | 25 | 16 | 6 | 5.5063 | 0 | 42.7453 | 0 | 12.0092 | 0 | 5.9082 | 17.3638 | 0 | 0 | 0 | 0 | 83.5328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.7 | 0 | 11018.7 | 147121 | -34581.3 | 21 | 27 | 147121 | -1034581.3
2 | 25 | 17 | 6 | 5.5808 | 0 | 42.7453 | 0 | 11.6822 | 0 | 5.9051 | 17.3638 | 0 | 0 | 0 | 0 | 83.2772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.9 | 0 | 11021.9 | 143253 | -46527.5 | 21 | 26 | 143253 | -1046527.5
2 | 25 | 18 | 6 | 7.7593 | 0 | 42.7453 | 0 | 11.2763 | 0 | 5.9019 | 17.3638 | 0 | 0 | 0 | 2 | 87.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025 | 0 | 11025 | 138473 | -55996.7 | 17 | 21 | 138473 | -1055996.7
2 | 25 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.767 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 5.6 | 92.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028 | 0 | 11028 | 143275 | -77294.1 | 16 | 18 | 143275 | -1077294.1
2 | 25 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7351 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11030.6 | 0 | 11030.6 | 132612 | -83924.6 | 15 | 18 | 132612 | -1083924.6
2 | 25 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.9654 | 0 | 5.9084 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.9802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.4 | 0 | 11033.4 | 148471 | -118257 | 16 | 18 | 148471 | -1118257
2 | 25 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.343 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11035.3 | 0 | 11035.3 | 129699 | -117987 | 15 | 16 | 129699 | -1117987
2 | 25 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7777 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.2 | 0 | 11038.2 | 136893 | -153543 | 14 | 16 | 136893 | -1153543
2 | 25 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.1987 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.6023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.7 | 0 | 11039.7 | 128333 | -163501 | 13 | 14 | 128333 | -1163501
2 | 26 | 1 | 7 | 5.1054 | 0 | 42.7453 | 10.1804 | 0 | 0 | 7.8206 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4112.03 | 0 | 4112.03 | 127876 | -186693 | 12 | 13 | 127876 | -1186693
2 | 26 | 2 | 7 | 5.1054 | 0 | 42.7453 | 11.9059 | 0 | 0 | 8.8679 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.7882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4114.16 | 0 | 4114.16 | 133672 | -206219 | 10 | 11 | 133672 | -1206219
2 | 26 | 3 | 7 | 5.1054 | 0 | 42.7453 | 11.9698 | 0 | 0 | 8.874 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.54 | 0 | 4116.54 | 126258 | -198290 | 10 | 11 | 126258 | -1198290
2 | 26 | 4 | 7 | 5.1054 | 0 | 42.7453 | 12.382 | 0 | 0 | 9.3427 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.9 | 0 | 4118.9 | 125700 | -222047 | 9 | 10 | 125700 | -1222047
2 | 26 | 5 | 7 | 5.1054 | 0 | 42.7453 | 13.6016 | 0 | 0 | 10.6424 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.35 | 0 | 4120.35 | 126671 | -245928 | 10 | 11 | 126671 | -1245928
2 | 26 | 6 | 7 | 5.1054 | 0 | 42.7453 | 14.331 | 0 | 0 | 11.4865 | 17.3638 | 0 | 0 | 0 | 3.6 | 94.6319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.91 | 0 | 4121.91 | 124795 | -250756 | 11 | 12 | 124795 | -1250756
2 | 26 | 7 | 7 | 5.0994 | 0 | 42.7453 | 14.659 | 0 | 0 | 11.9661 | 17.3638 | 0 | 0 | 0 | 1.2 | 93.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.37 | 0 | 4124.37 | 124367 | -260963 | 12 | 13 | 124367 | -1260963
2 | 26 | 8 | 7 | 4.2776 | 0 | 42.7453 | 14.452 | 0 | 0 | 11.6897 | 17.3638 | 0 | 0 | 0 | 0 | 90.5282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4126.52 | 0 | 4126.52 | 124088 | -254712 | 14 | 15 | 124088 | -1254712
2 | 26 | 9 | 7 | 3.8229 | 0 | 42.7453 | 12.8481 | 0 | 0 | 10.044 | 17.3638 | 0 | 0 | 0 | 0 | 86.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.68 | 0 | 4128.68 | 124312 | -225337 | 17 | 19 | 124312 | -1225337
2 | 26 | 10 | 7 | 4.1503 | 0 | 42.7453 | 11.0245 | 0 | 0 | 8.4723 | 17.3638 | 0 | 0 | 0 | 0 | 83.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.77 | 0 | 4130.77 | 126341 | -186886 | 21 | 23 | 126341 | -1186886
2 | 26 | 11 | 7 | 4.1475 | 0 | 42.7453 | 0 | 9.7322 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 0 | 79.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.67 | 0 | 4132.67 | 124928 | -147379 | 26 | 29 | 124928 | -1147379
2 | 26 | 12 | 7 | 4.1471 | 0 | 42.7453 | 0 | 9.9337 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.34 | 0 | 4134.34 | 125933 | -126703 | 28 | 32 | 125933 | -1126703
2 | 26 | 13 | 7 | 4.149 | 0 | 42.7453 | 0 | 10.0746 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 80.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.59 | 0 | 4135.59 | 126048 | -105057 | 31 | 36 | 126048 | -1105057
2 | 26 | 14 | 7 | 4.1499 | 0 | 42.7453 | 0 | 10.4547 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 0 | 80.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.49 | 0 | 4136.49 | 129627 | -99335 | 32 | 37 | 129627 | -1099335
2 | 26 | 15 | 7 | 4.1493 | 0 | 42.7453 | 0 | 10.3268 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 80.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.3 | 0 | 4137.3 | 126519 | -88390 | 33 | 38 | 126519 | -1088390
2 | 26 | 16 | 7 | 4.3085 | 0 | 42.7453 | 0 | 10.4477 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.7628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.93 | 0 | 4137.93 | 127567 | -95511.4 | 34 | 39 | 127567 | -1095511.4
2 | 26 | 17 | 7 | 4.8507 | 0 | 42.7453 | 0 | 10.3418 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 81.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4138.56 | 0 | 4138.56 | 125531 | -99304.5 | 33 | 38 | 125531 | -1099304.5
2 | 26 | 18 | 7 | 5.9502 | 0 | 42.7453 | 0 | 10.3066 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 2 | 84.2629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.46 | 0 | 4139.46 | 125123 | -111303 | 33 | 37 | 125123 | -1111303
2 | 26 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2669 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.43 | 0 | 4140.43 | 124819 | -131517 | 32 | 36 | 124819 | -1131517
2 | 26 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2405 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.42 | 0 | 4141.42 | 124682 | -141696 | 32 | 35 | 124682 | -1141696
2 | 26 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2197 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142.49 | 0 | 4142.49 | 124533 | -149848 | 32 | 34 | 124533 | -1149848
2 | 26 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1943 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4143.5 | 0 | 4143.5 | 124389 | -156338 | 31 | 33 | 124389 | -1156338
2 | 26 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1513 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.5 | 0 | 4144.5 | 124274 | -160470 | 31 | 33 | 124274 | -1160470
2 | 26 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2047 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4145.47 | 0 | 4145.47 | 125033 | -166866 | 30 | 32 | 125033 | -1166866
2 | 27 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1336 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11076.7 | 0 | 11076.7 | 124331 | -162051 | 30 | 32 | 124331 | -1162051
2 | 27 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1682 | 0 | 5.8929 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.4042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11077.8 | 0 | 11077.8 | 125168 | -173459 | 30 | 31 | 125168 | -1173459
2 | 27 | 3 | 1 | 10.8489 | 0 | 42.3304 | 10.582 | 0 | 0 | 8.1379 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11077.9 | 0 | 11077.9 | 124243 | -176462 | 29 | 30 | 124243 | -1176462
2 | 27 | 4 | 1 | 10.8489 | 0 | 42.3304 | 10.7356 | 0 | 0 | 8.1959 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11078.6 | 0 | 11078.6 | 124117 | -180487 | 28 | 29 | 124117 | -1180487
2 | 27 | 5 | 1 | 11.8202 | 0 | 44.8242 | 11.2221 | 0 | 0 | 8.5244 | 17.5105 | 0 | 0 | 0 | 4.8 | 98.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12306.9 | 0 | 12306.9 | 131484 | -185581 | 27 | 27 | 131484 | -1185581
2 | 27 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.9777 | 0 | 5.9408 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29930.8 | 0 | 29930.8 | 174553 | -142782 | 25 | 25 | 174553 | -1142782
2 | 27 | 7 | 1 | 49.0171 | 0 | 140.608 | 55.6907 | 0 | 0 | 25.2125 | 19.3979 | 0 | 0 | 0 | 1.2 | 291.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88765.4 | 0 | 88765.4 | 309862 | -973525 | 24 | 24 | 309862 | -1973525
2 | 27 | 8 | 1 | 47.5684 | 0 | 168.222 | 47.7633 | 0 | 0 | 25.2275 | 19.163 | 0 | 0 | 0 | 0 | 307.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107814 | 0 | 107814 | 372611 | -830204 | 26 | 26 | 372611 | -1830204
2 | 27 | 9 | 1 | 40.3376 | 0 | 173.795 | 36.5251 | 0 | 0 | 25.2437 | 19.0363 | 0 | 0 | 0 | 0 | 294.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149240 | 0 | 149240 | 392036 | -667159 | 28 | 29 | 392036 | -1667159
2 | 27 | 10 | 1 | 41.2999 | 0 | 172.186 | 32.9965 | 0 | 0 | 25.2601 | 19.0363 | 0 | 0 | 0 | 0 | 290.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175618 | 0 | 175618 | 390578 | -594809 | 30 | 31 | 390578 | -1594809
2 | 27 | 11 | 1 | 41.9557 | 0 | 163.102 | 31.8125 | 0 | 0 | 25.2758 | 19.0363 | 0 | 0 | 0 | 0 | 281.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179377 | 0 | 179377 | 377577 | -546852 | 32 | 34 | 377577 | -1546852
2 | 27 | 12 | 1 | 41.0538 | 0 | 149.692 | 0 | 26.154 | 0 | 6.2799 | 19.0363 | 0 | 0 | 0 | 0 | 242.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179375 | 0 | 179375 | 372231 | -463496 | 34 | 37 | 372231 | -1463496
2 | 27 | 13 | 1 | 39.8222 | 0 | 150.207 | 0 | 24.5751 | 0 | 6.2833 | 19.0363 | 0 | 0 | 0 | 0 | 239.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179372 | 0 | 179372 | 361994 | -414118 | 36 | 39 | 361994 | -1414118
2 | 27 | 14 | 1 | 41.9726 | 0 | 165.698 | 0 | 27.6271 | 0 | 6.2957 | 19.0363 | 0 | 0 | 0 | 0 | 260.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179369 | 0 | 179369 | 416014 | -365213 | 37 | 41 | 416014 | -1365213
2 | 27 | 15 | 1 | 41.3539 | 0 | 172.702 | 0 | 30.0092 | 0 | 6.3071 | 19.0363 | 0 | 0 | 0 | 0 | 269.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177048 | 0 | 177048 | 444752 | -347741 | 38 | 42 | 444752 | -1347741
2 | 27 | 16 | 1 | 41.3606 | 0 | 173.986 | 0 | 29.3007 | 0 | 6.3123 | 19.0363 | 0 | 0 | 0 | 0 | 269.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160941 | 0 | 160941 | 439185 | -344055 | 37 | 41 | 439185 | -1344055
2 | 27 | 17 | 1 | 43.1825 | 0 | 169.782 | 0 | 28.1151 | 0 | 6.3052 | 19.0363 | 0 | 0 | 0 | 0 | 266.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131349 | 0 | 131349 | 425856 | -370060 | 36 | 40 | 425856 | -1370060
2 | 27 | 18 | 1 | 47.3252 | 0 | 152.497 | 0 | 25.1863 | 0 | 6.2969 | 19.0363 | 0 | 0 | 0 | 2 | 252.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98470.4 | 0 | 98470.4 | 379992 | -384558 | 36 | 39 | 379992 | -1384558
2 | 27 | 19 | 1 | 34.11 | 0 | 93.4203 | 27.899 | 0 | 0 | 25.2894 | 19.0363 | 0 | 0 | 0 | 5.6 | 205.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60920.8 | 0 | 60920.8 | 317265 | -474383 | 34 | 37 | 317265 | -1474383
2 | 27 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 12.7545 | 0 | 5.9317 | 12.9754 | 0 | 0 | 0 | 7.2 | 125.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43552.6 | 0 | 43552.6 | 179500 | -8801.2 | 35 | 38 | 179500 | -1008801.2
2 | 27 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 7.8005 | 0 | 5.897 | 12.9754 | 0 | 0 | 0 | 7.2 | 107.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38642.7 | 0 | 38642.7 | 157461 | -8403.49 | 35 | 37 | 157461 | -1008403.49
2 | 27 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.937 | 0 | 5.9123 | 15.0234 | 0 | 0 | 0 | 7.2 | 102.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23672.8 | 0 | 23672.8 | 159066 | -17698.1 | 37 | 39 | 159066 | -1017698.1
2 | 27 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.6731 | 0 | 5.9085 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12686.4 | 0 | 12686.4 | 153991 | -25073.6 | 36 | 38 | 153991 | -1025073.6
2 | 27 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.4166 | 0 | 5.9047 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.7 | 0 | 11025.7 | 146914 | -34233.5 | 35 | 37 | 146914 | -1034233.5
2 | 28 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.5315 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.1 | 0 | 11029.1 | 143782 | -49628 | 32 | 33 | 143782 | -1049628
2 | 28 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 12.0714 | 0 | 5.9084 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.8 | 0 | 11031.8 | 146128 | -56859.8 | 31 | 32 | 146128 | -1056859.8
2 | 28 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.547 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.1 | 0 | 11034.1 | 140480 | -55538.6 | 33 | 34 | 140480 | -1055538.6
2 | 28 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.4659 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.2832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.1 | 0 | 11036.1 | 139424 | -65125.1 | 33 | 34 | 139424 | -1065125.1
2 | 28 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 12.3804 | 0 | 5.9116 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12265.2 | 0 | 12265.2 | 148827 | -74627.1 | 34 | 37 | 148827 | -1074627.1
2 | 28 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.2574 | 0 | 5.9424 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29889.7 | 0 | 29889.7 | 189715 | -54344.5 | 32 | 34 | 189715 | -1054344.5
2 | 28 | 7 | 2 | 48.9175 | 0 | 140.608 | 38.0853 | 0 | 0 | 25.2444 | 19.0363 | 0 | 0 | 0 | 1.2 | 273.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88725.3 | 0 | 88725.3 | 320063 | -664877 | 31 | 32 | 320063 | -1664877
2 | 28 | 8 | 2 | 44.6149 | 0 | 168.222 | 31.3576 | 0 | 0 | 25.2707 | 19.0363 | 0 | 0 | 0 | 0 | 288.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107774 | 0 | 107774 | 405020 | -558700 | 34 | 38 | 405020 | -1558700
2 | 28 | 9 | 2 | 39.7614 | 0 | 173.795 | 0 | 25.5998 | 0 | 6.2752 | 19.0363 | 0 | 0 | 0 | 0 | 264.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149216 | 0 | 149216 | 400650 | -447239 | 32 | 35 | 400650 | -1447239
2 | 28 | 10 | 2 | 41.2196 | 0 | 172.186 | 0 | 25.6153 | 0 | 6.279 | 19.0363 | 0 | 0 | 0 | 0 | 264.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175592 | 0 | 175592 | 398623 | -449563 | 30 | 34 | 398623 | -1449563
2 | 28 | 11 | 2 | 42.2583 | 0 | 163.102 | 28.4746 | 0 | 0 | 25.2843 | 19.0363 | 0 | 0 | 0 | 0 | 278.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179354 | 0 | 179354 | 395166 | -500799 | 29 | 32 | 395166 | -1500799
2 | 28 | 12 | 2 | 41.5579 | 0 | 149.692 | 28.9167 | 0 | 0 | 25.2804 | 19.0363 | 0 | 0 | 0 | 0 | 264.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179352 | 0 | 179352 | 379953 | -511528 | 26 | 29 | 379953 | -1511528
2 | 28 | 13 | 2 | 39.8506 | 0 | 150.207 | 26.0994 | 0 | 0 | 25.2757 | 19.0363 | 0 | 0 | 0 | 0 | 260.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179350 | 0 | 179350 | 354014 | -491294 | 27 | 30 | 354014 | -1491294
2 | 28 | 14 | 2 | 42.0519 | 0 | 165.698 | 0 | 24.7142 | 0 | 6.2682 | 19.0363 | 0 | 0 | 0 | 0 | 257.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179348 | 0 | 179348 | 387053 | -467516 | 26 | 29 | 387053 | -1467516
2 | 28 | 15 | 2 | 41.0962 | 0 | 172.702 | 0 | 25.7117 | 0 | 6.2744 | 19.0363 | 0 | 0 | 0 | 0 | 264.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177027 | 0 | 177027 | 405626 | -449988 | 26 | 29 | 405626 | -1449988
2 | 28 | 16 | 2 | 40.5905 | 0 | 173.986 | 0 | 25.9047 | 0 | 6.283 | 19.0363 | 0 | 0 | 0 | 0 | 265.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160922 | 0 | 160922 | 408392 | -441091 | 26 | 29 | 408392 | -1441091
2 | 28 | 17 | 2 | 44.9612 | 0 | 169.782 | 26.5245 | 0 | 0 | 6.2746 | 19.0363 | 0 | 0 | 0 | 0 | 266.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131332 | 0 | 131332 | 405579 | -507314 | 26 | 28 | 405579 | -1507314
2 | 28 | 18 | 2 | 48.8347 | 0 | 152.497 | 30.5896 | 0 | 0 | 6.2725 | 19.0363 | 0 | 0 | 0 | 2 | 259.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98455.8 | 0 | 98455.8 | 387457 | -546338 | 26 | 28 | 387457 | -1546338
2 | 28 | 19 | 2 | 34.11 | 0 | 93.4203 | 35.7026 | 0 | 0 | 25.2837 | 19.0363 | 0 | 0 | 0 | 5.6 | 213.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60907.7 | 0 | 60907.7 | 305873 | -587179 | 25 | 27 | 305873 | -1587179
2 | 28 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.6312 | 0 | 5.9559 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43539.8 | 0 | 43539.8 | 180082 | -14570.4 | 24 | 26 | 180082 | -1014570.4
2 | 28 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 14.1555 | 0 | 5.9459 | 15.0234 | 0 | 0 | 0 | 7.2 | 115.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38629.4 | 0 | 38629.4 | 177842 | -23418.6 | 22 | 24 | 177842 | -1023418.6
2 | 28 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.3698 | 0 | 5.9304 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23659.1 | 0 | 23659.1 | 168779 | -44923 | 21 | 22 | 168779 | -1044923
2 | 28 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.2273 | 0 | 5.9126 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12674 | 0 | 12674 | 154363 | -77856.7 | 20 | 21 | 154363 | -1077856.7
2 | 28 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.6599 | 0 | 5.9063 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014.3 | 0 | 11014.3 | 147545 | -101897 | 19 | 20 | 147545 | -1101897
3 | 1 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3679 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.4 | 0 | 11053.4 | 144718 | -124043 | 16 | 18 | 144718 | -1124043
3 | 1 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.1504 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11056.9 | 0 | 11056.9 | 143005 | -150591 | 15 | 17 | 143005 | -1150591
3 | 1 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9826 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11060 | 0 | 11060 | 141523 | -170123 | 13 | 15 | 141523 | -1170123
3 | 1 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.8277 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11062.7 | 0 | 11062.7 | 140331 | -182246 | 13 | 16 | 140331 | -1182246
3 | 1 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 10.9248 | 0 | 5.9012 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12297.3 | 0 | 12297.3 | 142351 | -192190 | 14 | 17 | 142351 | -1192190
3 | 1 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.1097 | 0 | 5.9531 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29984.8 | 0 | 29984.8 | 189304 | -165950 | 16 | 19 | 189304 | -1165950
3 | 1 | 7 | 3 | 49.0171 | 0 | 140.608 | 54.5272 | 0 | 0 | 25.211 | 19.2216 | 0 | 0 | 0 | 1.2 | 289.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89027.9 | 0 | 89027.9 | 320376 | -955961 | 17 | 20 | 320376 | -1955961
3 | 1 | 8 | 3 | 43.259 | 0 | 168.222 | 48.1696 | 0 | 0 | 25.2227 | 19.0888 | 0 | 0 | 0 | 0 | 303.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108145 | 0 | 108145 | 382380 | -850947 | 18 | 22 | 382380 | -1850947
3 | 1 | 9 | 3 | 44.485 | 0 | 173.795 | 39.1314 | 0 | 0 | 25.2403 | 19.0363 | 0 | 0 | 0 | 0 | 301.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149730 | 0 | 149730 | 401287 | -711858 | 18 | 23 | 401287 | -1711858
3 | 1 | 10 | 3 | 40.8356 | 0 | 172.186 | 35.8115 | 0 | 0 | 25.2557 | 19.0363 | 0 | 0 | 0 | 0 | 293.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176201 | 0 | 176201 | 399542 | -641575 | 20 | 25 | 399542 | -1641575
3 | 1 | 11 | 3 | 41.176 | 0 | 163.102 | 32.5123 | 0 | 0 | 25.2718 | 19.0363 | 0 | 0 | 0 | 0 | 281.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179976 | 0 | 179976 | 384304 | -574272 | 22 | 28 | 384304 | -1574272
3 | 1 | 12 | 3 | 40.7095 | 0 | 149.692 | 26.4704 | 0 | 0 | 11.8067 | 19.0363 | 0 | 0 | 0 | 0 | 247.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179974 | 0 | 179974 | 371138 | -473639 | 24 | 30 | 371138 | -1473639
3 | 1 | 13 | 3 | 39.7774 | 0 | 150.207 | 0 | 24.4575 | 0 | 6.2914 | 19.0363 | 0 | 0 | 0 | 0 | 239.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179972 | 0 | 179972 | 354820 | -430821 | 26 | 31 | 354820 | -1430821
3 | 1 | 14 | 3 | 41.2715 | 0 | 165.698 | 0 | 25.0526 | 0 | 6.2954 | 19.0363 | 0 | 0 | 0 | 0 | 257.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 387993 | -379750 | 27 | 33 | 387993 | -1379750
3 | 1 | 15 | 3 | 40.6589 | 0 | 172.702 | 0 | 25.8078 | 0 | 11.7491 | 19.0363 | 0 | 0 | 0 | 0 | 269.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177641 | 0 | 177641 | 406350 | -341371 | 28 | 34 | 406350 | -1341371
3 | 1 | 16 | 3 | 40.5799 | 0 | 173.986 | 0 | 26.007 | 0 | 25.3116 | 19.0363 | 0 | 0 | 0 | 0 | 284.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161480 | 0 | 161480 | 409372 | -353335 | 28 | 34 | 409372 | -1353335
3 | 1 | 17 | 3 | 41.9148 | 0 | 169.782 | 0 | 25.8897 | 0 | 6.2935 | 19.0363 | 0 | 0 | 0 | 0 | 262.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131784 | 0 | 131784 | 404799 | -412805 | 28 | 33 | 404799 | -1412805
3 | 1 | 18 | 3 | 46.5307 | 0 | 152.497 | 0 | 26.4285 | 0 | 6.2868 | 19.0363 | 0 | 0 | 0 | 2 | 252.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98791.3 | 0 | 98791.3 | 388391 | -454881 | 28 | 33 | 388391 | -1454881
3 | 1 | 19 | 3 | 34.11 | 0 | 93.4203 | 28.4626 | 0 | 0 | 25.2952 | 19.0363 | 0 | 0 | 0 | 5.6 | 205.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61110.6 | 0 | 61110.6 | 299737 | -490069 | 28 | 33 | 299737 | -1490069
3 | 1 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.2301 | 0 | 5.9508 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43681.7 | 0 | 43681.7 | 181278 | -12687.3 | 28 | 32 | 181278 | -1012687.3
3 | 1 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 12.73 | 0 | 5.9204 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38753.9 | 0 | 38753.9 | 162114 | -18502.6 | 27 | 32 | 162114 | -1018502.6
3 | 1 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 14.0702 | 0 | 5.9427 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23731.3 | 0 | 23731.3 | 174960 | -26080 | 28 | 32 | 174960 | -1026080
3 | 1 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.8389 | 0 | 5.9197 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12707 | 0 | 12707 | 158453 | -40128.3 | 28 | 31 | 158453 | -1040128.3
3 | 1 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 12.2886 | 0 | 5.9119 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.1 | 0 | 11041.1 | 151382 | -57203.3 | 27 | 31 | 151382 | -1057203.3
3 | 2 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.0139 | 0 | 5.9088 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045 | 0 | 11045 | 148386 | -66086.3 | 27 | 30 | 148386 | -1066086.3
3 | 2 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.8342 | 0 | 5.907 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048 | 0 | 11048 | 146309 | -78093.3 | 27 | 30 | 146309 | -1078093.3
3 | 2 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6872 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11050.8 | 0 | 11050.8 | 144744 | -90591.4 | 26 | 29 | 144744 | -1090591.4
3 | 2 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.569 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.2 | 0 | 11053.2 | 143505 | -96929.2 | 26 | 29 | 143505 | -1096929.2
3 | 2 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.6947 | 0 | 5.9059 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12287.4 | 0 | 12287.4 | 145667 | -106581 | 26 | 29 | 145667 | -1106581
3 | 2 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.5335 | 0 | 5.9828 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29974.7 | 0 | 29974.7 | 197570 | -87386.1 | 26 | 29 | 197570 | -1087386.1
3 | 2 | 7 | 4 | 48.6548 | 0 | 140.608 | 37.1019 | 0 | 0 | 25.2427 | 19.0363 | 0 | 0 | 0 | 1.2 | 271.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89017.3 | 0 | 89017.3 | 322813 | -673012 | 28 | 31 | 322813 | -1673012
3 | 2 | 8 | 4 | 40.094 | 0 | 168.222 | 33.8453 | 0 | 0 | 25.2666 | 19.0363 | 0 | 0 | 0 | 0 | 286.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108134 | 0 | 108134 | 384853 | -599432 | 30 | 33 | 384853 | -1599432
3 | 2 | 9 | 4 | 39.704 | 0 | 173.795 | 0 | 26.0061 | 0 | 6.2801 | 19.0363 | 0 | 0 | 0 | 0 | 264.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149722 | 0 | 149722 | 403374 | -422891 | 32 | 35 | 403374 | -1422891
3 | 2 | 10 | 4 | 40.6794 | 0 | 172.186 | 0 | 27.2162 | 0 | 6.2945 | 19.0363 | 0 | 0 | 0 | 0 | 265.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176192 | 0 | 176192 | 418871 | -373573 | 34 | 38 | 418871 | -1373573
3 | 2 | 11 | 4 | 41.1863 | 0 | 163.102 | 0 | 28.1068 | 0 | 6.3259 | 19.0363 | 0 | 0 | 0 | 0 | 257.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179966 | 0 | 179966 | 419913 | -317288 | 36 | 40 | 419913 | -1317288
3 | 2 | 12 | 4 | 40.7312 | 0 | 149.692 | 0 | 29.1473 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179963 | 0 | 179963 | 427905 | -276424 | 37 | 43 | 427905 | -1276424
3 | 2 | 13 | 4 | 39.8028 | 0 | 150.207 | 0 | 26.7974 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 242.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179961 | 0 | 179961 | 397522 | -250076 | 37 | 43 | 397522 | -1250076
3 | 2 | 14 | 4 | 41.2955 | 0 | 165.698 | 0 | 29.7431 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179958 | 0 | 179958 | 438602 | -228710 | 37 | 42 | 438602 | -1228710
3 | 2 | 15 | 4 | 40.6816 | 0 | 172.702 | 0 | 31.6662 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177630 | 0 | 177630 | 462611 | -217785 | 36 | 42 | 462611 | -1217785
3 | 2 | 16 | 4 | 40.5865 | 0 | 173.986 | 0 | 30.2664 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161468 | 0 | 161468 | 452254 | -215694 | 35 | 40 | 452254 | -1215694
3 | 2 | 17 | 4 | 40.3641 | 0 | 169.782 | 0 | 28.7272 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131771 | 0 | 131771 | 433794 | -247661 | 34 | 39 | 433794 | -1247661
3 | 2 | 18 | 4 | 46.7756 | 0 | 152.497 | 0 | 24.6034 | 0 | 6.3218 | 19.0363 | 0 | 0 | 0 | 2 | 251.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98778.3 | 0 | 98778.3 | 385701 | -307642 | 33 | 37 | 385701 | -1307642
3 | 2 | 19 | 4 | 34.11 | 0 | 93.4203 | 0 | 21.8031 | 0 | 6.3059 | 19.0363 | 0 | 0 | 0 | 5.6 | 180.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61097.6 | 0 | 61097.6 | 317111 | -376621 | 33 | 37 | 317111 | -1376621
3 | 2 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.1151 | 0 | 5.4895 | 12.9754 | 0 | 0 | 0 | 7.2 | 121.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43669.3 | 0 | 43669.3 | 184394 | 0 | 32 | 36 | 184394 | -1000000
3 | 2 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 10.5516 | 0 | 5.9058 | 12.9754 | 0 | 0 | 0 | 7.2 | 109.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38741.5 | 0 | 38741.5 | 163743 | -9744.58 | 32 | 36 | 163743 | -1009744.58
3 | 2 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 10.992 | 0 | 5.9036 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.7912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23718 | 0 | 23718 | 150249 | -15353.9 | 31 | 35 | 150249 | -1015353.9
3 | 2 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.224 | 0 | 5.9179 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12692.8 | 0 | 12692.8 | 166741 | -18313 | 29 | 33 | 166741 | -1018313
3 | 2 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 12.2538 | 0 | 5.9139 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.1 | 0 | 11026.1 | 157116 | -29124 | 28 | 32 | 157116 | -1029124
3 | 3 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.4179 | 0 | 5.9137 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.8 | 0 | 11029.8 | 153383 | -38076.3 | 27 | 31 | 153383 | -1038076.3
3 | 3 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.2809 | 0 | 5.9115 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.1 | 0 | 11033.1 | 150527 | -53210 | 26 | 29 | 150527 | -1053210
3 | 3 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.0204 | 0 | 5.9088 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.1 | 0 | 11036.1 | 148211 | -64096.7 | 24 | 28 | 148211 | -1064096.7
3 | 3 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.804 | 0 | 5.9068 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.8 | 0 | 11038.8 | 146421 | -78983.2 | 23 | 27 | 146421 | -1078983.2
3 | 3 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.8755 | 0 | 5.9078 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12273.4 | 0 | 12273.4 | 148083 | -97836.2 | 22 | 25 | 148083 | -1097836.2
3 | 3 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 15.1272 | 0 | 5.9736 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29961.1 | 0 | 29961.1 | 195144 | -91021 | 21 | 24 | 195144 | -1091021
3 | 3 | 7 | 5 | 48.6432 | 0 | 140.608 | 41.3883 | 0 | 0 | 25.228 | 19.0363 | 0 | 0 | 0 | 1.2 | 276.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89004.3 | 0 | 89004.3 | 323782 | -762285 | 21 | 24 | 323782 | -1762285
3 | 3 | 8 | 5 | 40.1993 | 0 | 168.222 | 40.0131 | 0 | 0 | 25.2431 | 19.0363 | 0 | 0 | 0 | 0 | 292.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108122 | 0 | 108122 | 384709 | -716007 | 20 | 24 | 384709 | -1716007
3 | 3 | 9 | 5 | 39.8938 | 0 | 173.795 | 29.6428 | 0 | 0 | 25.2539 | 19.0363 | 0 | 0 | 0 | 0 | 287.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149713 | 0 | 149713 | 403280 | -565492 | 20 | 24 | 403280 | -1565492
3 | 3 | 10 | 5 | 40.6906 | 0 | 172.186 | 27.4848 | 0 | 0 | 25.2747 | 19.0363 | 0 | 0 | 0 | 0 | 284.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176185 | 0 | 176185 | 401474 | -512350 | 21 | 25 | 401474 | -1512350
3 | 3 | 11 | 5 | 41.1919 | 0 | 163.102 | 28.1257 | 0 | 0 | 25.2853 | 19.0363 | 0 | 0 | 0 | 0 | 276.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179961 | 0 | 179961 | 394854 | -507491 | 22 | 26 | 394854 | -1507491
3 | 3 | 12 | 5 | 40.7419 | 0 | 149.692 | 0 | 27.6435 | 0 | 6.3036 | 19.0363 | 0 | 0 | 0 | 0 | 243.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179961 | 0 | 179961 | 384729 | -448296 | 22 | 27 | 384729 | -1448296
3 | 3 | 13 | 5 | 39.8198 | 0 | 150.207 | 0 | 24.7469 | 0 | 6.3002 | 19.0363 | 0 | 0 | 0 | 0 | 240.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179959 | 0 | 179959 | 356122 | -423850 | 23 | 28 | 356122 | -1423850
3 | 3 | 14 | 5 | 41.2984 | 0 | 165.698 | 0 | 25.0732 | 0 | 6.2995 | 19.0363 | 0 | 0 | 0 | 0 | 257.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179957 | 0 | 179957 | 389082 | -380610 | 23 | 28 | 389082 | -1380610
3 | 3 | 15 | 5 | 40.6834 | 0 | 172.702 | 0 | 25.8695 | 0 | 25.3107 | 19.0363 | 0 | 0 | 0 | 0 | 283.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177630 | 0 | 177630 | 407464 | -358168 | 23 | 29 | 407464 | -1358168
3 | 3 | 16 | 5 | 40.5946 | 0 | 173.986 | 0 | 26.043 | 0 | 25.3023 | 19.0363 | 0 | 0 | 0 | 0 | 284.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161469 | 0 | 161469 | 410255 | -394381 | 23 | 27 | 410255 | -1394381
3 | 3 | 17 | 5 | 40.3583 | 0 | 169.782 | 0 | 26.2932 | 0 | 25.2933 | 19.0363 | 0 | 0 | 0 | 0 | 280.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131774 | 0 | 131774 | 404758 | -448669 | 21 | 26 | 404758 | -1448669
3 | 3 | 18 | 5 | 40.9521 | 0 | 152.497 | 30.6676 | 0 | 0 | 6.2775 | 19.0363 | 0 | 0 | 0 | 2 | 251.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98782.3 | 0 | 98782.3 | 397808 | -554998 | 20 | 24 | 397808 | -1554998
3 | 3 | 19 | 5 | 34.11 | 0 | 93.4203 | 35.0466 | 0 | 0 | 6.2829 | 19.0363 | 0 | 0 | 0 | 5.6 | 193.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61102.4 | 0 | 61102.4 | 313282 | -584444 | 20 | 23 | 313282 | -1584444
3 | 3 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.5661 | 0 | 5.9561 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43674.2 | 0 | 43674.2 | 181575 | -17329.3 | 19 | 23 | 181575 | -1017329.3
3 | 3 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.7978 | 0 | 5.9386 | 15.4625 | 0 | 0 | 0 | 7.2 | 115.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38746.3 | 0 | 38746.3 | 173848 | -25399.4 | 18 | 22 | 173848 | -1025399.4
3 | 3 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 13.6988 | 0 | 5.9373 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23722.6 | 0 | 23722.6 | 173831 | -44646.7 | 18 | 21 | 173831 | -1044646.7
3 | 3 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.4649 | 0 | 5.916 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12699.3 | 0 | 12699.3 | 157795 | -68313.1 | 17 | 21 | 157795 | -1068313.1
3 | 3 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.9065 | 0 | 5.9089 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.6 | 0 | 11033.6 | 150765 | -88843.1 | 16 | 20 | 150765 | -1088843.1
3 | 4 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.558 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.7 | 0 | 11037.7 | 147426 | -110102 | 17 | 20 | 147426 | -1110102
3 | 4 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3786 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.2 | 0 | 11041.2 | 145429 | -126530 | 16 | 19 | 145429 | -1126530
3 | 4 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2152 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045 | 0 | 11045 | 143588 | -137562 | 16 | 19 | 143588 | -1137562
3 | 4 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.1841 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.3774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048.1 | 0 | 11048.1 | 143313 | -151898 | 16 | 19 | 143313 | -1151898
3 | 4 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0299 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051 | 0 | 11051 | 141055 | -158857 | 16 | 19 | 141055 | -1158857
3 | 4 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.9119 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 3.6 | 86.9034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.6 | 0 | 11053.6 | 139909 | -168221 | 16 | 19 | 139909 | -1168221
3 | 4 | 7 | 6 | 6.365 | 0 | 42.7453 | 0 | 10.8206 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 1.2 | 84.3948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11056.1 | 0 | 11056.1 | 138935 | -174263 | 17 | 20 | 138935 | -1174263
3 | 4 | 8 | 6 | 5.4024 | 0 | 42.7453 | 63.6544 | 0 | 0 | 25.2276 | 19.4344 | 0 | 0 | 0 | 0 | 156.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11058.5 | 0 | 11058.5 | 124961 | -1001340 | 18 | 21 | 124961 | -2001340
3 | 4 | 9 | 6 | 5.1396 | 0 | 42.7453 | 56.2895 | 0 | 0 | 25.2364 | 19.1385 | 0 | 0 | 0 | 0 | 148.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11060.6 | 0 | 11060.6 | 127038 | -872204 | 18 | 22 | 127038 | -1872204
3 | 4 | 10 | 6 | 5.4751 | 0 | 42.7453 | 43.601 | 0 | 0 | 25.2426 | 18.8924 | 0 | 0 | 0 | 0 | 135.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051 | 0 | 11051 | 123753 | -719235 | 19 | 24 | 123753 | -1719235
3 | 4 | 11 | 6 | 5.4756 | 0 | 42.7453 | 39.2803 | 0 | 0 | 25.2434 | 18.8896 | 0 | 0 | 0 | 0 | 131.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047.1 | 0 | 11047.1 | 123187 | -669963 | 21 | 25 | 123187 | -1669963
3 | 4 | 12 | 6 | 5.5321 | 0 | 42.7453 | 35.6022 | 0 | 0 | 6.2421 | 18.8896 | 0 | 0 | 0 | 0 | 109.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045.7 | 0 | 11045.7 | 122686 | -621279 | 22 | 27 | 122686 | -1621279
3 | 4 | 13 | 6 | 5.4716 | 0 | 42.7453 | 32.143 | 0 | 0 | 6.244 | 18.8896 | 0 | 0 | 0 | 0 | 105.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.8 | 0 | 11044.8 | 122293 | -567909 | 24 | 29 | 122293 | -1567909
3 | 4 | 14 | 6 | 5.4747 | 0 | 42.7453 | 29.4678 | 0 | 0 | 6.2442 | 18.8896 | 0 | 0 | 0 | 0 | 102.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.5 | 0 | 11044.5 | 121893 | -528938 | 25 | 30 | 121893 | -1528938
3 | 4 | 15 | 6 | 5.474 | 0 | 42.7453 | 0 | 10.2024 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 0 | 77.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.2 | 0 | 11044.2 | 123002 | -15620.4 | 25 | 32 | 123002 | -1015620.4
3 | 4 | 16 | 6 | 5.4771 | 0 | 42.7453 | 0 | 10.0882 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 77.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.2 | 0 | 11044.2 | 121316 | -20618.3 | 26 | 32 | 121316 | -1020618.3
3 | 4 | 17 | 6 | 5.6678 | 0 | 42.7453 | 0 | 11.8841 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 0 | 83.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047.9 | 0 | 11047.9 | 146130 | -35985.7 | 25 | 31 | 146130 | -1035985.7
3 | 4 | 18 | 6 | 7.9492 | 0 | 42.7453 | 0 | 11.5153 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 2 | 87.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11050.7 | 0 | 11050.7 | 141224 | -39680.8 | 25 | 31 | 141224 | -1039680.8
3 | 4 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.261 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.3 | 0 | 11053.3 | 138400 | -55177.6 | 25 | 30 | 138400 | -1055177.6
3 | 4 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0633 | 0 | 5.9005 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11056.5 | 0 | 11056.5 | 136073 | -71771.7 | 24 | 29 | 136073 | -1071771.7
3 | 4 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9148 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059 | 0 | 11059 | 134563 | -88827.8 | 24 | 28 | 134563 | -1088827.8
3 | 4 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8012 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061.5 | 0 | 11061.5 | 133441 | -101902 | 23 | 27 | 133441 | -1101902
3 | 4 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7217 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11063.8 | 0 | 11063.8 | 132640 | -115926 | 23 | 26 | 132640 | -1115926
3 | 4 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.785 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.1 | 0 | 11066.1 | 132824 | -125172 | 21 | 25 | 132824 | -1125172
3 | 5 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7816 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.52 | 0 | 4113.52 | 131219 | -127765 | 21 | 25 | 131219 | -1127765
3 | 5 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8117 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.51 | 0 | 4115.51 | 130615 | -129545 | 21 | 24 | 130615 | -1129545
3 | 5 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8613 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4117.39 | 0 | 4117.39 | 130831 | -133479 | 21 | 24 | 130831 | -1133479
3 | 5 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7982 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.88 | 0 | 4118.88 | 129608 | -136306 | 21 | 24 | 129608 | -1136306
3 | 5 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.6612 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.35 | 0 | 4120.35 | 129132 | -144372 | 21 | 24 | 129132 | -1144372
3 | 5 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4786 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.1908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4121.72 | 0 | 4121.72 | 128638 | -160538 | 21 | 24 | 128638 | -1160538
3 | 5 | 7 | 7 | 5.0702 | 0 | 42.7453 | 0 | 10.3683 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.05 | 0 | 4123.05 | 128253 | -165261 | 22 | 25 | 128253 | -1165261
3 | 5 | 8 | 7 | 3.9179 | 0 | 42.7453 | 0 | 10.3195 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.71 | 0 | 4124.71 | 128127 | -163831 | 23 | 27 | 128127 | -1163831
3 | 5 | 9 | 7 | 3.7873 | 0 | 42.7453 | 0 | 10.3067 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4126.43 | 0 | 4126.43 | 127859 | -127004 | 24 | 28 | 127859 | -1127004
3 | 5 | 10 | 7 | 4.1466 | 0 | 42.7453 | 0 | 10.4941 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 80.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.21 | 0 | 4128.21 | 130069 | -96428.5 | 26 | 30 | 130069 | -1096428.5
3 | 5 | 11 | 7 | 4.1452 | 0 | 42.7453 | 0 | 10.5243 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 80.6765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.84 | 0 | 4129.84 | 129913 | -82530.5 | 27 | 31 | 129913 | -1082530.5
3 | 5 | 12 | 7 | 4.1444 | 0 | 42.7453 | 0 | 10.6265 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 80.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4131.09 | 0 | 4131.09 | 131045 | -77271.7 | 28 | 33 | 131045 | -1077271.7
3 | 5 | 13 | 7 | 4.1466 | 0 | 42.7453 | 0 | 10.7011 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 80.8553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4131.61 | 0 | 4131.61 | 131477 | -73283.9 | 28 | 33 | 131477 | -1073283.9
3 | 5 | 14 | 7 | 4.1465 | 0 | 42.7453 | 0 | 10.7191 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 80.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.62 | 0 | 4132.62 | 131274 | -69437.3 | 28 | 32 | 131274 | -1069437.3
3 | 5 | 15 | 7 | 4.1484 | 0 | 42.7453 | 0 | 10.7205 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 80.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.32 | 0 | 4133.32 | 131400 | -69819 | 27 | 32 | 131400 | -1069819
3 | 5 | 16 | 7 | 4.1515 | 0 | 42.7453 | 0 | 10.6829 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 0 | 80.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4134.28 | 0 | 4134.28 | 131019 | -74384.7 | 26 | 30 | 131019 | -1074384.7
3 | 5 | 17 | 7 | 4.17 | 0 | 42.7453 | 0 | 10.5635 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 0 | 80.7406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.1 | 0 | 4135.1 | 129944 | -84255.7 | 24 | 28 | 129944 | -1084255.7
3 | 5 | 18 | 7 | 5.5592 | 0 | 42.7453 | 0 | 10.3619 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 2 | 83.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.24 | 0 | 4136.24 | 128181 | -100005 | 21 | 26 | 128181 | -1100005
3 | 5 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1719 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.4413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.58 | 0 | 4137.58 | 126646 | -127324 | 20 | 24 | 126646 | -1127324
3 | 5 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.0326 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.33 | 0 | 4139.33 | 125710 | -162251 | 19 | 22 | 125710 | -1162251
3 | 5 | 21 | 7 | 6.6633 | 0 | 42.7453 | 10.4288 | 0 | 0 | 8.0059 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.32 | 0 | 4141.32 | 125232 | -186307 | 17 | 20 | 125232 | -1186307
3 | 5 | 22 | 7 | 6.6633 | 0 | 42.7453 | 11.6026 | 0 | 0 | 8.8616 | 17.3638 | 0 | 0 | 0 | 7.2 | 94.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4143.18 | 0 | 4143.18 | 124771 | -205202 | 16 | 18 | 124771 | -1205202
3 | 5 | 23 | 7 | 6.6633 | 0 | 42.7453 | 12.8831 | 0 | 0 | 9.9954 | 17.3638 | 0 | 0 | 0 | 6.4 | 96.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.94 | 0 | 4144.94 | 124339 | -220197 | 14 | 17 | 124339 | -1220197
3 | 5 | 24 | 7 | 6.6633 | 0 | 42.7453 | 13.517 | 0 | 0 | 10.6816 | 17.3638 | 0 | 0 | 0 | 5.6 | 96.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4146.7 | 0 | 4146.7 | 123914 | -236251 | 12 | 15 | 123914 | -1236251
3 | 6 | 1 | 1 | 10.8489 | 0 | 42.3304 | 14.3086 | 0 | 0 | 11.8024 | 17.3638 | 0 | 0 | 0 | 4.8 | 101.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11103.1 | 0 | 11103.1 | 123858 | -248007 | 11 | 14 | 123858 | -1248007
3 | 6 | 2 | 1 | 10.8489 | 0 | 42.3304 | 15.0411 | 0 | 0 | 12.6274 | 17.3638 | 0 | 0 | 0 | 4.8 | 103.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11104.8 | 0 | 11104.8 | 124615 | -263778 | 10 | 12 | 124615 | -1263778
3 | 6 | 3 | 1 | 10.8489 | 0 | 42.3304 | 15.5824 | 0 | 0 | 13.5182 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11105.8 | 0 | 11105.8 | 123308 | -269256 | 9 | 11 | 123308 | -1269256
3 | 6 | 4 | 1 | 10.8489 | 0 | 42.3304 | 16.333 | 0 | 0 | 14.2614 | 17.3638 | 0 | 0 | 0 | 4.8 | 105.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11107.3 | 0 | 11107.3 | 129958 | -275470 | 9 | 11 | 129958 | -1275470
3 | 6 | 5 | 1 | 11.8202 | 0 | 44.8242 | 15.3492 | 0 | 0 | 12.8807 | 17.5105 | 0 | 0 | 0 | 4.8 | 107.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12340.6 | 0 | 12340.6 | 125803 | -259385 | 9 | 11 | 125803 | -1259385
3 | 6 | 6 | 1 | 24.3093 | 0 | 69.9783 | 13.6246 | 0 | 0 | 10.8839 | 17.5105 | 0 | 0 | 0 | 3.6 | 139.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30026.9 | 0 | 30026.9 | 172730 | -247306 | 9 | 11 | 172730 | -1247306
3 | 6 | 7 | 1 | 48.3156 | 0 | 140.608 | 69.2037 | 0 | 0 | 25.2091 | 19.6412 | 0 | 0 | 0 | 1.2 | 304.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89068.3 | 0 | 89068.3 | 308751 | -1195150 | 11 | 14 | 308751 | -2195150
3 | 6 | 8 | 1 | 39.7424 | 0 | 168.222 | 58.0953 | 0 | 0 | 25.2093 | 19.2614 | 0 | 0 | 0 | 0 | 310.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108184 | 0 | 108184 | 371393 | -1028690 | 14 | 16 | 371393 | -2028690
3 | 6 | 9 | 1 | 39.9679 | 0 | 173.795 | 43.2667 | 0 | 0 | 25.2244 | 19.0363 | 0 | 0 | 0 | 0 | 301.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149757 | 0 | 149757 | 390939 | -790774 | 16 | 19 | 390939 | -1790774
3 | 6 | 10 | 1 | 40.7486 | 0 | 172.186 | 37.2804 | 0 | 0 | 25.2401 | 19.0363 | 0 | 0 | 0 | 0 | 294.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176228 | 0 | 176228 | 389509 | -683259 | 19 | 22 | 389509 | -1683259
3 | 6 | 11 | 1 | 41.1895 | 0 | 163.102 | 35.5667 | 0 | 0 | 25.2518 | 19.0363 | 0 | 0 | 0 | 0 | 284.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180001 | 0 | 180001 | 373430 | -630330 | 21 | 25 | 373430 | -1630330
3 | 6 | 12 | 1 | 40.7403 | 0 | 149.692 | 31.3039 | 0 | 0 | 25.2791 | 19.0363 | 0 | 0 | 0 | 0 | 266.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179999 | 0 | 179999 | 358839 | -531234 | 24 | 28 | 358839 | -1531234
3 | 6 | 13 | 1 | 39.8322 | 0 | 150.207 | 27.8218 | 0 | 0 | 25.2849 | 19.0363 | 0 | 0 | 0 | 0 | 262.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179997 | 0 | 179997 | 346213 | -483188 | 25 | 30 | 346213 | -1483188
3 | 6 | 14 | 1 | 41.3132 | 0 | 165.698 | 0 | 25.3866 | 0 | 6.2958 | 19.0363 | 0 | 0 | 0 | 0 | 257.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179993 | 0 | 179993 | 379858 | -402058 | 27 | 32 | 379858 | -1402058
3 | 6 | 15 | 1 | 40.7085 | 0 | 172.702 | 0 | 25.3035 | 0 | 6.3047 | 19.0363 | 0 | 0 | 0 | 0 | 264.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177665 | 0 | 177665 | 398403 | -358781 | 28 | 34 | 398403 | -1358781
3 | 6 | 16 | 1 | 40.615 | 0 | 173.986 | 0 | 25.5353 | 0 | 6.3032 | 19.0363 | 0 | 0 | 0 | 0 | 265.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161503 | 0 | 161503 | 401964 | -371953 | 28 | 33 | 401964 | -1371953
3 | 6 | 17 | 1 | 40.4538 | 0 | 169.782 | 0 | 26.1618 | 0 | 6.3022 | 19.0363 | 0 | 0 | 0 | 0 | 261.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131807 | 0 | 131807 | 395849 | -403693 | 28 | 33 | 395849 | -1403693
3 | 6 | 18 | 1 | 41.3939 | 0 | 152.497 | 0 | 26.9364 | 0 | 6.2926 | 19.0363 | 0 | 0 | 0 | 2 | 248.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98814.6 | 0 | 98814.6 | 383197 | -478831 | 27 | 32 | 383197 | -1478831
3 | 6 | 19 | 1 | 34.11 | 0 | 93.4203 | 32.263 | 0 | 0 | 25.2899 | 19.0363 | 0 | 0 | 0 | 5.6 | 209.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61133.3 | 0 | 61133.3 | 295551 | -520401 | 28 | 32 | 295551 | -1520401
3 | 6 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 14.3111 | 0 | 5.9478 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43704.2 | 0 | 43704.2 | 175379 | -14994.2 | 28 | 32 | 175379 | -1014994.2
3 | 6 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.7374 | 0 | 5.9179 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38776.4 | 0 | 38776.4 | 156503 | -20857.6 | 27 | 32 | 156503 | -1020857.6
3 | 6 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.3625 | 0 | 5.9287 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23753.6 | 0 | 23753.6 | 166184 | -35367.6 | 27 | 31 | 166184 | -1035367.6
3 | 6 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.1729 | 0 | 5.9108 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12729.4 | 0 | 12729.4 | 150599 | -50833.8 | 27 | 31 | 150599 | -1050833.8
3 | 6 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.6191 | 0 | 5.905 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11063.2 | 0 | 11063.2 | 143911 | -70236.2 | 27 | 30 | 143911 | -1070236.2
3 | 7 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3467 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.9 | 0 | 11066.9 | 140940 | -87312.7 | 24 | 27 | 140940 | -1087312.7
3 | 7 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.1128 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11069.6 | 0 | 11069.6 | 139121 | -107204 | 21 | 25 | 139121 | -1107204
3 | 7 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.9135 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11072.2 | 0 | 11072.2 | 137890 | -133721 | 19 | 22 | 137890 | -1133721
3 | 7 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.716 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11074.6 | 0 | 11074.6 | 136709 | -162565 | 15 | 18 | 136709 | -1162565
3 | 7 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 10.6965 | 0 | 5.8997 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12308.8 | 0 | 12308.8 | 138587 | -192312 | 11 | 14 | 138587 | -1192312
3 | 7 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.6362 | 0 | 5.9434 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29996.2 | 0 | 29996.2 | 184896 | -193958 | 7 | 10 | 184896 | -1193958
3 | 7 | 7 | 2 | 47.796 | 0 | 140.608 | 63.3226 | 0 | 0 | 25.2088 | 19.2851 | 0 | 0 | 0 | 1.2 | 297.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89039.1 | 0 | 89039.1 | 317078 | -1123590 | 6 | 9 | 317078 | -2123590
3 | 7 | 8 | 2 | 40.068 | 0 | 168.222 | 59.0102 | 0 | 0 | 25.2073 | 19.1237 | 0 | 0 | 0 | 0 | 311.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108156 | 0 | 108156 | 379012 | -1078300 | 5 | 7 | 379012 | -2078300
3 | 7 | 9 | 2 | 39.9943 | 0 | 173.795 | 48.2406 | 0 | 0 | 25.2123 | 19.0363 | 0 | 0 | 0 | 0 | 306.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149740 | 0 | 149740 | 398228 | -911371 | 4 | 6 | 398228 | -1911371
3 | 7 | 10 | 2 | 40.72 | 0 | 172.186 | 46.7544 | 0 | 0 | 25.2185 | 19.0363 | 0 | 0 | 0 | 0 | 303.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176212 | 0 | 176212 | 396008 | -876451 | 4 | 6 | 396008 | -1876451
3 | 7 | 11 | 2 | 41.1851 | 0 | 163.102 | 47.4348 | 0 | 0 | 25.2177 | 19.0363 | 0 | 0 | 0 | 0 | 295.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179988 | 0 | 179988 | 377147 | -881548 | 4 | 7 | 377147 | -1881548
3 | 7 | 12 | 2 | 40.7373 | 0 | 149.692 | 43.4291 | 0 | 0 | 25.2257 | 19.0363 | 0 | 0 | 0 | 0 | 278.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179988 | 0 | 179988 | 352696 | -798293 | 4 | 7 | 352696 | -1798293
3 | 7 | 13 | 2 | 39.8251 | 0 | 150.207 | 40.9357 | 0 | 0 | 6.2242 | 19.0363 | 0 | 0 | 0 | 0 | 256.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179986 | 0 | 179986 | 350643 | -770726 | 6 | 9 | 350643 | -1770726
3 | 7 | 14 | 2 | 41.3267 | 0 | 165.698 | 36.745 | 0 | 0 | 6.2261 | 19.0363 | 0 | 0 | 0 | 0 | 269.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179983 | 0 | 179983 | 383522 | -729894 | 8 | 10 | 383522 | -1729894
3 | 7 | 15 | 2 | 40.7104 | 0 | 172.702 | 34.4024 | 0 | 0 | 6.2399 | 19.0363 | 0 | 0 | 0 | 0 | 273.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177655 | 0 | 177655 | 402509 | -680834 | 9 | 12 | 402509 | -1680834
3 | 7 | 16 | 2 | 40.6453 | 0 | 173.986 | 35.992 | 0 | 0 | 6.2387 | 19.0363 | 0 | 0 | 0 | 0 | 275.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161495 | 0 | 161495 | 405532 | -709317 | 8 | 11 | 405532 | -1709317
3 | 7 | 17 | 2 | 40.9861 | 0 | 169.782 | 40.1661 | 0 | 0 | 6.2283 | 19.0363 | 0 | 0 | 0 | 0 | 276.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131801 | 0 | 131801 | 395567 | -788253 | 6 | 9 | 395567 | -1788253
3 | 7 | 18 | 2 | 40.2015 | 0 | 152.497 | 46.0364 | 0 | 0 | 6.216 | 19.0363 | 0 | 0 | 0 | 2 | 265.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98809.6 | 0 | 98809.6 | 370075 | -881008 | 5 | 8 | 370075 | -1881008
3 | 7 | 19 | 2 | 34.11 | 0 | 93.4203 | 56.1077 | 0 | 0 | 6.3418 | 19.0363 | 0 | 0 | 0 | 5.6 | 214.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61129.7 | 0 | 61129.7 | 320996 | -946802 | 4 | 6 | 320996 | -1946802
3 | 7 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 15.4158 | 0 | 5.9956 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43700.5 | 0 | 43700.5 | 210076 | -19523.3 | 2 | 5 | 210076 | -1019523.3
3 | 7 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.8162 | 0 | 5.9294 | 17.5105 | 0 | 0 | 0 | 7.2 | 116.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38771.7 | 0 | 38771.7 | 176683 | -107228 | 1 | 3 | 176683 | -1107228
3 | 7 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 11.6163 | 0 | 5.9106 | 17.5105 | 0 | 0 | 0 | 7.2 | 104.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23750.9 | 0 | 23750.9 | 160284 | -163928 | 0 | 2 | 160284 | -1163928
3 | 7 | 23 | 2 | 11.1963 | 0 | 44.3342 | 11.7201 | 0 | 0 | 9.046 | 17.5105 | 0 | 0 | 0 | 6.4 | 100.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12729.3 | 0 | 12729.3 | 146864 | -216384 | -1 | 0 | 146864 | -1216384
3 | 7 | 24 | 2 | 10.3176 | 0 | 42.5403 | 13.7498 | 0 | 0 | 10.9235 | 17.5105 | 0 | 0 | 0 | 5.6 | 100.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11064.2 | 0 | 11064.2 | 141189 | -239049 | -3 | -1 | 141189 | -1239049
3 | 8 | 1 | 3 | 10.8489 | 0 | 42.3304 | 14.8017 | 0 | 0 | 12.1281 | 17.3638 | 0 | 0 | 0 | 4.8 | 102.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11068.7 | 0 | 11068.7 | 148705 | -255575 | -3 | -1 | 148705 | -1255575
3 | 8 | 2 | 3 | 10.8489 | 0 | 42.3304 | 14.1455 | 0 | 0 | 11.2224 | 17.3638 | 0 | 0 | 0 | 4.8 | 100.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11072.3 | 0 | 11072.3 | 137341 | -237212 | -3 | -1 | 137341 | -1237212
3 | 8 | 3 | 3 | 10.8489 | 0 | 42.3304 | 16.3224 | 0 | 0 | 14.0041 | 17.3638 | 0 | 0 | 0 | 4.8 | 105.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11075.4 | 0 | 11075.4 | 139283 | -289203 | -3 | -1 | 139283 | -1289203
3 | 8 | 4 | 3 | 10.8489 | 0 | 42.3304 | 17.3307 | 0 | 0 | 15.6266 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11077.3 | 0 | 11077.3 | 134662 | -294470 | -4 | -2 | 134662 | -1294470
3 | 8 | 5 | 3 | 11.8202 | 0 | 44.8242 | 19.4152 | 0 | 0 | 19.3791 | 17.5105 | 0 | 0 | 0 | 4.8 | 117.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12312 | 0 | 12312 | 138993 | -328504 | -4 | -3 | 138993 | -1328504
3 | 8 | 6 | 3 | 24.3093 | 0 | 69.9783 | 18.5257 | 0 | 0 | 17.406 | 17.5105 | 0 | 0 | 0 | 3.6 | 151.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29999.9 | 0 | 29999.9 | 182121 | -302839 | -5 | -4 | 182121 | -1302839
3 | 8 | 7 | 3 | 47.9038 | 0 | 140.608 | 75.8692 | 0 | 0 | 25.2264 | 19.6665 | 0 | 0 | 0 | 1.2 | 310.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89043.3 | 0 | 89043.3 | 316221 | -1363350 | -2 | 0 | 316221 | -2363350
3 | 8 | 8 | 3 | 39.874 | 0 | 168.222 | 65.3884 | 0 | 0 | 25.2103 | 19.2937 | 0 | 0 | 0 | 0 | 317.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108161 | 0 | 108161 | 378570 | -1195560 | 2 | 4 | 378570 | -2195560
3 | 8 | 9 | 3 | 39.923 | 0 | 173.795 | 50.4871 | 0 | 0 | 25.2104 | 19.0363 | 0 | 0 | 0 | 0 | 308.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149741 | 0 | 149741 | 398015 | -946389 | 6 | 8 | 398015 | -1946389
3 | 8 | 10 | 3 | 40.705 | 0 | 172.186 | 44.6228 | 0 | 0 | 25.2188 | 19.0363 | 0 | 0 | 0 | 0 | 301.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176212 | 0 | 176212 | 396115 | -830718 | 10 | 12 | 396115 | -1830718
3 | 8 | 11 | 3 | 41.179 | 0 | 163.102 | 42.087 | 0 | 0 | 25.2307 | 19.0363 | 0 | 0 | 0 | 0 | 290.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179986 | 0 | 179986 | 377664 | -758029 | 14 | 17 | 377664 | -1758029
3 | 8 | 12 | 3 | 40.733 | 0 | 149.692 | 36.2277 | 0 | 0 | 25.2525 | 19.0363 | 0 | 0 | 0 | 0 | 270.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179985 | 0 | 179985 | 358311 | -632991 | 17 | 21 | 358311 | -1632991
3 | 8 | 13 | 3 | 39.8264 | 0 | 150.207 | 32.7309 | 0 | 0 | 6.2606 | 19.0363 | 0 | 0 | 0 | 0 | 248.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179983 | 0 | 179983 | 351547 | -585897 | 19 | 23 | 351547 | -1585897
3 | 8 | 14 | 3 | 41.3013 | 0 | 165.698 | 27.5309 | 0 | 0 | 6.2683 | 19.0363 | 0 | 0 | 0 | 0 | 259.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179980 | 0 | 179980 | 384638 | -525409 | 20 | 24 | 384638 | -1525409
3 | 8 | 15 | 3 | 40.7003 | 0 | 172.702 | 0 | 26.5654 | 0 | 6.2807 | 19.0363 | 0 | 0 | 0 | 0 | 265.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177651 | 0 | 177651 | 403363 | -478106 | 21 | 26 | 403363 | -1478106
3 | 8 | 16 | 3 | 40.6131 | 0 | 173.986 | 0 | 26.4081 | 0 | 6.2806 | 19.0363 | 0 | 0 | 0 | 0 | 266.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161490 | 0 | 161490 | 406436 | -479720 | 21 | 26 | 406436 | -1479720
3 | 8 | 17 | 3 | 40.6822 | 0 | 169.782 | 27.8339 | 0 | 0 | 6.2761 | 19.0363 | 0 | 0 | 0 | 0 | 263.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131796 | 0 | 131796 | 399250 | -525706 | 21 | 25 | 399250 | -1525706
3 | 8 | 18 | 3 | 40.2385 | 0 | 152.497 | 33.1979 | 0 | 0 | 8.0054 | 19.0363 | 0 | 0 | 0 | 2 | 254.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98803.7 | 0 | 98803.7 | 388884 | -595871 | 20 | 25 | 388884 | -1595871
3 | 8 | 19 | 3 | 34.11 | 0 | 93.4203 | 40.6222 | 0 | 0 | 25.2671 | 19.0363 | 0 | 0 | 0 | 5.6 | 218.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61123.5 | 0 | 61123.5 | 308799 | -653910 | 20 | 24 | 308799 | -1653910
3 | 8 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.0935 | 0 | 5.947 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43694.6 | 0 | 43694.6 | 178511 | -19327.7 | 19 | 24 | 178511 | -1019327.7
3 | 8 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.2976 | 0 | 5.9527 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38766.5 | 0 | 38766.5 | 184689 | -37688.1 | 18 | 23 | 184689 | -1037688.1
3 | 8 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.8227 | 0 | 5.9231 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23743.9 | 0 | 23743.9 | 165844 | -65722.5 | 19 | 23 | 165844 | -1065722.5
3 | 8 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.7555 | 0 | 5.9083 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12720.9 | 0 | 12720.9 | 151580 | -94782.3 | 19 | 23 | 151580 | -1094782.3
3 | 8 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.2879 | 0 | 5.9036 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11055.3 | 0 | 11055.3 | 145197 | -113683 | 18 | 23 | 145197 | -1113683
3 | 9 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.1319 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059.3 | 0 | 11059.3 | 143325 | -130627 | 19 | 23 | 143325 | -1130627
3 | 9 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.9979 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11062.6 | 0 | 11062.6 | 141531 | -143405 | 19 | 23 | 141531 | -1143405
3 | 9 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.9198 | 0 | 5.9008 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11065.4 | 0 | 11065.4 | 140557 | -154015 | 19 | 23 | 140557 | -1154015
3 | 9 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.8296 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11067.8 | 0 | 11067.8 | 139316 | -161581 | 20 | 23 | 139316 | -1161581
3 | 9 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 10.9708 | 0 | 5.9012 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12301.9 | 0 | 12301.9 | 141541 | -169637 | 20 | 23 | 141541 | -1169637
3 | 9 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.1821 | 0 | 5.9535 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29989.2 | 0 | 29989.2 | 188564 | -145117 | 20 | 23 | 188564 | -1145117
3 | 9 | 7 | 4 | 47.8342 | 0 | 140.608 | 50.8851 | 0 | 0 | 25.2184 | 19.2278 | 0 | 0 | 0 | 1.2 | 284.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89031.8 | 0 | 89031.8 | 320277 | -889667 | 21 | 25 | 320277 | -1889667
3 | 9 | 8 | 4 | 39.3892 | 0 | 168.222 | 44.4384 | 0 | 0 | 25.234 | 19.0726 | 0 | 0 | 0 | 0 | 296.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108149 | 0 | 108149 | 382167 | -776584 | 23 | 26 | 382167 | -1776584
3 | 9 | 9 | 4 | 39.7008 | 0 | 173.795 | 32.0229 | 0 | 0 | 25.2506 | 19.0363 | 0 | 0 | 0 | 0 | 289.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149732 | 0 | 149732 | 400991 | -594062 | 24 | 28 | 400991 | -1594062
3 | 9 | 10 | 4 | 40.673 | 0 | 172.186 | 0 | 26.6188 | 0 | 6.2777 | 19.0363 | 0 | 0 | 0 | 0 | 264.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176202 | 0 | 176202 | 399366 | -474186 | 27 | 32 | 399366 | -1474186
3 | 9 | 11 | 4 | 41.1679 | 0 | 163.102 | 0 | 27.4204 | 0 | 6.3024 | 19.0363 | 0 | 0 | 0 | 0 | 257.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179977 | 0 | 179977 | 391151 | -418400 | 30 | 35 | 391151 | -1418400
3 | 9 | 12 | 4 | 40.722 | 0 | 149.692 | 0 | 26.9973 | 0 | 6.3263 | 19.0363 | 0 | 0 | 0 | 0 | 242.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179975 | 0 | 179975 | 387263 | -333423 | 32 | 39 | 387263 | -1333423
3 | 9 | 13 | 4 | 39.8212 | 0 | 150.207 | 0 | 25.3333 | 0 | 6.331 | 19.0363 | 0 | 0 | 0 | 0 | 240.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179973 | 0 | 179973 | 374554 | -291750 | 34 | 41 | 374554 | -1291750
3 | 9 | 14 | 4 | 41.3034 | 0 | 165.698 | 0 | 29.5647 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 436926 | -252936 | 36 | 43 | 436926 | -1252936
3 | 9 | 15 | 4 | 40.6927 | 0 | 172.702 | 0 | 32.2633 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177641 | 0 | 177641 | 464379 | -224175 | 37 | 45 | 464379 | -1224175
3 | 9 | 16 | 4 | 40.602 | 0 | 173.986 | 0 | 31.4062 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161478 | 0 | 161478 | 452277 | -209984 | 38 | 45 | 452277 | -1209984
3 | 9 | 17 | 4 | 40.4556 | 0 | 169.782 | 0 | 32.0235 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 267.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131781 | 0 | 131781 | 460304 | -233374 | 38 | 45 | 460304 | -1233374
3 | 9 | 18 | 4 | 40.5575 | 0 | 152.497 | 0 | 28.9794 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 249.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98787.4 | 0 | 98787.4 | 424799 | -262693 | 38 | 45 | 424799 | -1262693
3 | 9 | 19 | 4 | 34.11 | 0 | 93.4203 | 0 | 24.2859 | 0 | 6.3172 | 19.0363 | 0 | 0 | 0 | 5.6 | 182.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61105.9 | 0 | 61105.9 | 346748 | -336745 | 37 | 44 | 346748 | -1336745
3 | 9 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.0958 | 0 | 5.4892 | 12.9754 | 0 | 0 | 0 | 7.2 | 121.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43676.8 | 0 | 43676.8 | 183462 | 0 | 37 | 44 | 183462 | -1000000
3 | 9 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 10.3642 | 0 | 5.9046 | 12.9754 | 0 | 0 | 0 | 7.2 | 109.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38748.9 | 0 | 38748.9 | 162783 | -8258.99 | 37 | 43 | 162783 | -1008258.99
3 | 9 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 10.4939 | 0 | 5.9013 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.2908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23726 | 0 | 23726 | 149485 | -12614.7 | 37 | 42 | 149485 | -1012614.7
3 | 9 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 9.9972 | 0 | 5.8979 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12700.5 | 0 | 12700.5 | 138384 | -13884.7 | 37 | 42 | 138384 | -1013884.7
3 | 9 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.9261 | 0 | 5.9126 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.6 | 0 | 11033.6 | 160497 | -18007.9 | 36 | 41 | 160497 | -1018007.9
3 | 10 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.67 | 0 | 5.9088 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.4 | 0 | 11036.4 | 154795 | -20130.2 | 36 | 39 | 154795 | -1020130.2
3 | 10 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.8489 | 0 | 5.9089 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.2 | 0 | 11039.2 | 151907 | -27012.3 | 35 | 36 | 151907 | -1027012.3
3 | 10 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.9811 | 0 | 5.9089 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.2331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.8 | 0 | 11041.8 | 149155 | -36202 | 34 | 34 | 149155 | -1036202
3 | 10 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.0755 | 0 | 5.9088 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044 | 0 | 11044 | 147175 | -41950.2 | 34 | 35 | 147175 | -1041950.2
3 | 10 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 12.182 | 0 | 5.9102 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12278.3 | 0 | 12278.3 | 149112 | -50344.1 | 34 | 35 | 149112 | -1050344.1
3 | 10 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 15.7559 | 0 | 5.9865 | 17.5105 | 0 | 0 | 0 | 3.6 | 137.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29965.6 | 0 | 29965.6 | 196937 | -40233.2 | 35 | 36 | 196937 | -1040233.2
3 | 10 | 7 | 5 | 47.0131 | 0 | 140.608 | 24.5666 | 0 | 0 | 25.2752 | 19.0363 | 0 | 0 | 0 | 1.2 | 257.699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89008.4 | 0 | 89008.4 | 323686 | -479981 | 36 | 38 | 323686 | -1479981
3 | 10 | 8 | 5 | 40.0705 | 0 | 168.222 | 0 | 28.9707 | 0 | 6.2886 | 19.0363 | 0 | 0 | 0 | 0 | 262.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108125 | 0 | 108125 | 415091 | -446142 | 38 | 40 | 415091 | -1446142
3 | 10 | 9 | 5 | 39.9952 | 0 | 173.795 | 0 | 29.2072 | 0 | 6.3209 | 19.0363 | 0 | 0 | 0 | 0 | 268.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149716 | 0 | 149716 | 438858 | -308537 | 40 | 42 | 438858 | -1308537
3 | 10 | 10 | 5 | 40.8095 | 0 | 172.186 | 0 | 31.9451 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176185 | 0 | 176185 | 463234 | -259592 | 42 | 45 | 463234 | -1259592
3 | 10 | 11 | 5 | 41.1764 | 0 | 163.102 | 0 | 31.189 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179959 | 0 | 179959 | 439737 | -222705 | 43 | 47 | 439737 | -1222705
3 | 10 | 12 | 5 | 40.7332 | 0 | 149.692 | 0 | 32.2148 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179956 | 0 | 179956 | 434975 | -184743 | 45 | 50 | 434975 | -1184743
3 | 10 | 13 | 5 | 39.8392 | 0 | 150.207 | 0 | 29.9967 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179954 | 0 | 179954 | 402006 | -153917 | 46 | 51 | 402006 | -1153917
3 | 10 | 14 | 5 | 41.3195 | 0 | 165.698 | 0 | 35.6471 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179951 | 0 | 179951 | 462729 | -122046 | 47 | 53 | 462729 | -1122046
3 | 10 | 15 | 5 | 40.7128 | 0 | 172.702 | 0 | 37.1034 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177622 | 0 | 177622 | 499975 | -92702.9 | 48 | 54 | 499975 | -1092702.9
3 | 10 | 16 | 5 | 40.6909 | 0 | 173.986 | 0 | 33.0697 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161459 | 0 | 161459 | 490083 | -79658.6 | 47 | 53 | 490083 | -1079658.6
3 | 10 | 17 | 5 | 41.023 | 0 | 169.782 | 0 | 30.8454 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 267.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131762 | 0 | 131762 | 464630 | -92054.8 | 47 | 51 | 464630 | -1092054.8
3 | 10 | 18 | 5 | 39.1578 | 0 | 152.497 | 0 | 29.09 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 248.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98769 | 0 | 98769 | 414824 | -119184 | 46 | 50 | 414824 | -1119184
3 | 10 | 19 | 5 | 34.11 | 0 | 93.4203 | 0 | 24.4863 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 182.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61088.1 | 0 | 61088.1 | 340876 | -229783 | 43 | 45 | 340876 | -1229783
3 | 10 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.1188 | 0 | 5.4895 | 8.818 | 0 | 0 | 0 | 7.2 | 117.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43659.9 | 0 | 43659.9 | 184075 | 0 | 39 | 41 | 184075 | -1000000
3 | 10 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 11.732 | 0 | 5.9134 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38732.8 | 0 | 38732.8 | 164863 | -7691.33 | 36 | 36 | 164863 | -1007691.33
3 | 10 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.5113 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23707.8 | 0 | 23707.8 | 151271 | 0 | 35 | 36 | 151271 | -1000000
3 | 10 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 9.8939 | 0 | 5.8979 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12681.6 | 0 | 12681.6 | 140208 | -11660.7 | 35 | 35 | 140208 | -1011660.7
3 | 10 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 10.357 | 0 | 5.9016 | 15.0234 | 0 | 0 | 0 | 5.6 | 89.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014.4 | 0 | 11014.4 | 153325 | -9853.66 | 35 | 35 | 153325 | -1009853.66
3 | 11 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4287 | 0 | 5.9094 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11016.7 | 0 | 11016.7 | 160587 | -16912.3 | 34 | 35 | 160587 | -1016912.3
3 | 11 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3415 | 0 | 5.9074 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11019.3 | 0 | 11019.3 | 156632 | -23957.8 | 33 | 34 | 156632 | -1023957.8
3 | 11 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.8609 | 0 | 5.9097 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.8 | 0 | 11022.8 | 153734 | -29321 | 32 | 34 | 153734 | -1029321
3 | 11 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.0409 | 0 | 5.91 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026 | 0 | 11026 | 151236 | -37153.6 | 31 | 32 | 151236 | -1037153.6
3 | 11 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.2085 | 0 | 5.9104 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.4097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.8 | 0 | 11028.8 | 149040 | -44279.1 | 29 | 31 | 149040 | -1044279.1
3 | 11 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.971 | 0 | 5.9081 | 17.3638 | 0 | 0 | 0 | 3.6 | 87.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.7 | 0 | 11031.7 | 146985 | -55140 | 27 | 29 | 146985 | -1055140
3 | 11 | 7 | 6 | 6.1722 | 0 | 42.7453 | 0 | 11.7799 | 0 | 5.9064 | 17.3638 | 0 | 0 | 0 | 1.2 | 85.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.4 | 0 | 11034.4 | 145507 | -63287 | 29 | 30 | 145507 | -1063287
3 | 11 | 8 | 6 | 4.8758 | 0 | 42.7453 | 40.9532 | 0 | 0 | 25.2556 | 18.9137 | 0 | 0 | 0 | 0 | 132.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.1 | 0 | 11037.1 | 127244 | -696299 | 30 | 31 | 127244 | -1696299
3 | 11 | 9 | 6 | 5.4965 | 0 | 42.7453 | 39.1687 | 0 | 0 | 25.253 | 18.8896 | 0 | 0 | 0 | 0 | 131.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.5 | 0 | 11039.5 | 144493 | -642821 | 30 | 32 | 144493 | -1642821
3 | 11 | 10 | 6 | 5.649 | 0 | 42.7453 | 30.0159 | 0 | 0 | 25.2574 | 18.8896 | 0 | 0 | 0 | 0 | 122.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.7 | 0 | 11037.7 | 139269 | -526294 | 32 | 34 | 139269 | -1526294
3 | 11 | 11 | 6 | 5.471 | 0 | 42.7453 | 24.6462 | 0 | 0 | 6.2604 | 18.8896 | 0 | 0 | 0 | 0 | 98.0125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.9 | 0 | 11034.9 | 133602 | -441112 | 33 | 35 | 133602 | -1441112
3 | 11 | 12 | 6 | 5.4703 | 0 | 42.7453 | 21.4447 | 0 | 0 | 6.2507 | 18.8896 | 0 | 0 | 0 | 0 | 94.8005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.7 | 0 | 11034.7 | 143843 | -393808 | 33 | 37 | 143843 | -1393808
3 | 11 | 13 | 6 | 5.4751 | 0 | 42.7453 | 20.1758 | 0 | 0 | 6.1797 | 18.8896 | 0 | 0 | 0 | 0 | 93.4654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.5 | 0 | 11034.5 | 155500 | -374261 | 34 | 38 | 155500 | -1374261
3 | 11 | 14 | 6 | 5.4764 | 0 | 42.7453 | 19.2714 | 0 | 0 | 6.1319 | 18.8896 | 0 | 0 | 0 | 0 | 92.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.5 | 0 | 11034.5 | 170744 | -360837 | 35 | 40 | 170744 | -1360837
3 | 11 | 15 | 6 | 5.4792 | 0 | 42.7453 | 0 | 9.5139 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 76.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.5 | 0 | 11034.5 | 127300 | -9771.08 | 36 | 41 | 127300 | -1009771.08
3 | 11 | 16 | 6 | 5.4795 | 0 | 42.7453 | 0 | 6.5886 | 0 | 6.7857 | 12.8287 | 0 | 0 | 0 | 0 | 74.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11034.7 | 0 | 11034.7 | 123236 | -9666.15 | 35 | 40 | 123236 | -1009666.15
3 | 11 | 17 | 6 | 5.492 | 0 | 42.7453 | 0 | 8.8799 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 0 | 75.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.4 | 0 | 11036.4 | 122945 | -13799 | 35 | 39 | 122945 | -1013799
3 | 11 | 18 | 6 | 7.3672 | 0 | 42.7453 | 0 | 9.8459 | 0 | 5.8973 | 15.3158 | 0 | 0 | 0 | 2 | 83.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.7 | 0 | 11037.7 | 135585 | -19709.2 | 34 | 38 | 135585 | -1019709.2
3 | 11 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2979 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.7089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.2 | 0 | 11039.2 | 149098 | -24993.6 | 33 | 37 | 149098 | -1024993.6
3 | 11 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3483 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.4 | 0 | 11041.4 | 144756 | -29577.4 | 31 | 35 | 144756 | -1029577.4
3 | 11 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.5412 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.1 | 0 | 11044.1 | 142090 | -36234.9 | 30 | 34 | 142090 | -1036234.9
3 | 11 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.5231 | 0 | 5.9035 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11046.4 | 0 | 11046.4 | 140193 | -46660.8 | 29 | 32 | 140193 | -1046660.8
3 | 11 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3237 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048.8 | 0 | 11048.8 | 138576 | -57976 | 27 | 31 | 138576 | -1057976
3 | 11 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.1486 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051.2 | 0 | 11051.2 | 137079 | -70006.6 | 25 | 29 | 137079 | -1070006.6
3 | 12 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9635 | 0 | 5.9 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4098.82 | 0 | 4098.82 | 135606 | -83329.1 | 25 | 28 | 135606 | -1083329.1
3 | 12 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.817 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4101.12 | 0 | 4101.12 | 134557 | -99631.7 | 25 | 28 | 134557 | -1099631.7
3 | 12 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7231 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103.58 | 0 | 4103.58 | 133672 | -108589 | 25 | 27 | 133672 | -1108589
3 | 12 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.6275 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4105.91 | 0 | 4105.91 | 132875 | -119932 | 25 | 26 | 132875 | -1119932
3 | 12 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.5377 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.2 | 0 | 4108.2 | 132169 | -128363 | 24 | 26 | 132169 | -1128363
3 | 12 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4624 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4110.4 | 0 | 4110.4 | 131459 | -137458 | 24 | 25 | 131459 | -1137458
3 | 12 | 7 | 7 | 5.0392 | 0 | 42.7453 | 0 | 10.3986 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 0 | 81.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4112.6 | 0 | 4112.6 | 130894 | -140196 | 25 | 26 | 130894 | -1140196
3 | 12 | 8 | 7 | 4.8041 | 0 | 42.7453 | 0 | 10.418 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 81.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4114.75 | 0 | 4114.75 | 131177 | -141537 | 25 | 26 | 131177 | -1141537
3 | 12 | 9 | 7 | 4.8406 | 0 | 42.7453 | 0 | 10.3716 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 0 | 81.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.85 | 0 | 4116.85 | 130176 | -128145 | 26 | 27 | 130176 | -1128145
3 | 12 | 10 | 7 | 4.7724 | 0 | 42.7453 | 0 | 10.4367 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 81.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.88 | 0 | 4118.88 | 130774 | -124418 | 27 | 28 | 130774 | -1124418
3 | 12 | 11 | 7 | 4.4617 | 0 | 42.7453 | 0 | 10.4001 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 0 | 80.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.78 | 0 | 4120.78 | 129886 | -108053 | 28 | 30 | 129886 | -1108053
3 | 12 | 12 | 7 | 4.5132 | 0 | 42.7453 | 0 | 10.5336 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 0 | 81.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.49 | 0 | 4122.49 | 131194 | -104143 | 29 | 31 | 131194 | -1104143
3 | 12 | 13 | 7 | 4.5306 | 0 | 42.7453 | 0 | 10.4649 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 0 | 81.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.17 | 0 | 4124.17 | 129605 | -96744.4 | 30 | 32 | 129605 | -1096744.4
3 | 12 | 14 | 7 | 4.5334 | 0 | 42.7453 | 0 | 10.5619 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 0 | 81.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.66 | 0 | 4125.66 | 130506 | -94517.4 | 31 | 33 | 130506 | -1094517.4
3 | 12 | 15 | 7 | 4.6162 | 0 | 42.7453 | 0 | 10.516 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 81.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4127.14 | 0 | 4127.14 | 129246 | -89939.7 | 31 | 34 | 129246 | -1089939.7
3 | 12 | 16 | 7 | 4.7369 | 0 | 42.7453 | 0 | 10.5401 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 81.2839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128.55 | 0 | 4128.55 | 129102 | -92710.1 | 32 | 34 | 129102 | -1092710.1
3 | 12 | 17 | 7 | 5.0443 | 0 | 42.7453 | 0 | 10.5289 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 2 | 83.5801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.92 | 0 | 4129.92 | 128691 | -99493.5 | 32 | 34 | 128691 | -1099493.5
3 | 12 | 18 | 7 | 6.052 | 0 | 42.7453 | 0 | 10.5411 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4131.24 | 0 | 4131.24 | 128719 | -111797 | 32 | 34 | 128719 | -1111797
3 | 12 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4858 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.55 | 0 | 4132.55 | 127844 | -120063 | 32 | 33 | 127844 | -1120063
3 | 12 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4732 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.93 | 0 | 4133.93 | 127681 | -124942 | 32 | 33 | 127681 | -1124942
3 | 12 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6177 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.29 | 0 | 4135.29 | 128992 | -129424 | 32 | 32 | 128992 | -1129424
3 | 12 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5774 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.65 | 0 | 4136.65 | 127072 | -126472 | 32 | 32 | 127072 | -1126472
3 | 12 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5164 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.7864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.92 | 0 | 4137.92 | 126883 | -125144 | 32 | 32 | 126883 | -1125144
3 | 12 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 10.4217 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11093.7 | 0 | 11093.7 | 126999 | -132936 | 32 | 32 | 126999 | -1132936
3 | 13 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3744 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11094.6 | 0 | 11094.6 | 126907 | -136091 | 32 | 32 | 126907 | -1136091
3 | 13 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.326 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11095 | 0 | 11095 | 126810 | -148803 | 32 | 32 | 126810 | -1148803
3 | 13 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.2968 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11095.9 | 0 | 11095.9 | 126596 | -152133 | 31 | 32 | 126596 | -1152133
3 | 13 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.5183 | 0 | 5.8979 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.3712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12328.8 | 0 | 12328.8 | 129855 | -156277 | 31 | 32 | 129855 | -1156277
3 | 13 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.8963 | 0 | 5.9416 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30015 | 0 | 30015 | 177494 | -127772 | 30 | 31 | 177494 | -1127772
3 | 13 | 6 | 1 | 49.0171 | 0 | 140.608 | 48.6815 | 0 | 0 | 25.2254 | 19.2619 | 0 | 0 | 0 | 1.2 | 283.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89056.7 | 0 | 89056.7 | 311721 | -848656 | 29 | 31 | 311721 | -1848656
3 | 13 | 7 | 1 | 52.0292 | 0 | 168.222 | 42.6473 | 0 | 0 | 25.2426 | 19.1098 | 0 | 0 | 0 | 0 | 307.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108173 | 0 | 108173 | 374270 | -738843 | 29 | 31 | 374270 | -1738843
3 | 13 | 8 | 1 | 44.6444 | 0 | 173.795 | 32.6125 | 0 | 0 | 25.2501 | 19.0363 | 0 | 0 | 0 | 0 | 295.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149750 | 0 | 149750 | 393141 | -614671 | 29 | 31 | 393141 | -1614671
3 | 13 | 9 | 1 | 41.5136 | 0 | 172.186 | 31.4653 | 0 | 0 | 25.2624 | 19.0363 | 0 | 0 | 0 | 0 | 289.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176219 | 0 | 176219 | 391662 | -577622 | 29 | 31 | 391662 | -1577622
3 | 13 | 10 | 1 | 42.0739 | 0 | 163.102 | 32.3484 | 0 | 0 | 25.2742 | 19.0363 | 0 | 0 | 0 | 0 | 281.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179993 | 0 | 179993 | 382404 | -562787 | 30 | 32 | 382404 | -1562787
3 | 13 | 11 | 1 | 41.1736 | 0 | 149.692 | 28.4169 | 0 | 0 | 25.2809 | 19.0363 | 0 | 0 | 0 | 0 | 263.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179991 | 0 | 179991 | 366469 | -500573 | 30 | 33 | 366469 | -1500573
3 | 13 | 12 | 1 | 39.8467 | 0 | 150.207 | 25.8584 | 0 | 0 | 25.2796 | 19.0363 | 0 | 0 | 0 | 0 | 260.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179989 | 0 | 179989 | 348209 | -470504 | 30 | 34 | 348209 | -1470504
3 | 13 | 13 | 1 | 41.6493 | 0 | 165.698 | 0 | 24.7018 | 0 | 6.282 | 19.0363 | 0 | 0 | 0 | 0 | 257.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179986 | 0 | 179986 | 381950 | -402767 | 31 | 35 | 381950 | -1402767
3 | 13 | 14 | 1 | 40.6563 | 0 | 172.702 | 0 | 25.4254 | 0 | 6.2947 | 19.0363 | 0 | 0 | 0 | 0 | 264.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177657 | 0 | 177657 | 400419 | -367231 | 32 | 35 | 400419 | -1367231
3 | 13 | 15 | 1 | 40.5685 | 0 | 173.986 | 0 | 25.6418 | 0 | 6.3056 | 19.0363 | 0 | 0 | 0 | 0 | 265.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161495 | 0 | 161495 | 403555 | -357211 | 32 | 36 | 403555 | -1357211
3 | 13 | 16 | 1 | 40.5717 | 0 | 169.782 | 0 | 25.4788 | 0 | 6.2969 | 19.0363 | 0 | 0 | 0 | 0 | 261.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131800 | 0 | 131800 | 398288 | -396179 | 32 | 35 | 398288 | -1396179
3 | 13 | 17 | 1 | 37.6849 | 0 | 152.497 | 0 | 26.201 | 0 | 6.2851 | 19.0363 | 0 | 0 | 0 | 2 | 243.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98806 | 0 | 98806 | 384654 | -464911 | 31 | 34 | 384654 | -1464911
3 | 13 | 18 | 1 | 31.302 | 0 | 93.4203 | 30.1274 | 0 | 0 | 25.2914 | 19.0363 | 0 | 0 | 0 | 5.6 | 204.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61124.9 | 0 | 61124.9 | 294234 | -504151 | 31 | 33 | 294234 | -1504151
3 | 13 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 13.4293 | 0 | 5.9372 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43695.8 | 0 | 43695.8 | 176786 | -11414.4 | 31 | 33 | 176786 | -1011414.4
3 | 13 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.2811 | 0 | 5.9145 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38768.3 | 0 | 38768.3 | 157852 | -17968.8 | 30 | 32 | 157852 | -1017968.8
3 | 13 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.6667 | 0 | 5.9337 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23745.6 | 0 | 23745.6 | 168787 | -30712.6 | 30 | 32 | 168787 | -1030712.6
3 | 13 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.4637 | 0 | 5.914 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12721.4 | 0 | 12721.4 | 152967 | -44007 | 29 | 31 | 152967 | -1044007
3 | 13 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.9064 | 0 | 5.9074 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11055.4 | 0 | 11055.4 | 146195 | -60486.7 | 29 | 31 | 146195 | -1060486.7
3 | 13 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 11.6315 | 0 | 5.9048 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059.1 | 0 | 11059.1 | 143206 | -70485.1 | 28 | 30 | 143206 | -1070485.1
3 | 14 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4582 | 0 | 5.9035 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061.9 | 0 | 11061.9 | 141544 | -88885.7 | 27 | 29 | 141544 | -1088885.7
3 | 14 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3177 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11064.6 | 0 | 11064.6 | 140187 | -105101 | 26 | 27 | 140187 | -1105101
3 | 14 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.1884 | 0 | 5.9016 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.9 | 0 | 11066.9 | 139053 | -118510 | 25 | 26 | 139053 | -1118510
3 | 14 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.3212 | 0 | 5.9028 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12300.9 | 0 | 12300.9 | 141493 | -127542 | 26 | 27 | 141493 | -1127542
3 | 14 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.695 | 0 | 5.9614 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29988.1 | 0 | 29988.1 | 188947 | -104494 | 27 | 28 | 188947 | -1104494
3 | 14 | 6 | 2 | 49.0171 | 0 | 140.608 | 43.0121 | 0 | 0 | 25.2304 | 19.0979 | 0 | 0 | 0 | 1.2 | 278.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89030.6 | 0 | 89030.6 | 319782 | -768723 | 27 | 29 | 319782 | -1768723
3 | 14 | 7 | 2 | 52.4818 | 0 | 168.222 | 39.3272 | 0 | 0 | 25.2505 | 19.0363 | 0 | 0 | 0 | 0 | 304.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108147 | 0 | 108147 | 381964 | -680926 | 28 | 30 | 381964 | -1680926
3 | 14 | 8 | 2 | 45.4253 | 0 | 173.795 | 30.3258 | 0 | 0 | 25.2591 | 19.0363 | 0 | 0 | 0 | 0 | 293.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149733 | 0 | 149733 | 400592 | -573175 | 29 | 30 | 400592 | -1573175
3 | 14 | 9 | 2 | 41.7877 | 0 | 172.186 | 29.3106 | 0 | 0 | 25.2713 | 19.0363 | 0 | 0 | 0 | 0 | 287.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176203 | 0 | 176203 | 398675 | -535378 | 29 | 31 | 398675 | -1535378
3 | 14 | 10 | 2 | 41.9344 | 0 | 163.102 | 29.9145 | 0 | 0 | 25.2837 | 19.0363 | 0 | 0 | 0 | 0 | 279.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179978 | 0 | 179978 | 389223 | -519968 | 30 | 32 | 389223 | -1519968
3 | 14 | 11 | 2 | 41.1536 | 0 | 149.692 | 0 | 26.2027 | 0 | 6.286 | 19.0363 | 0 | 0 | 0 | 0 | 242.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179976 | 0 | 179976 | 374854 | -464515 | 30 | 33 | 374854 | -1464515
3 | 14 | 12 | 2 | 39.8461 | 0 | 150.207 | 0 | 24.0298 | 0 | 6.2822 | 19.0363 | 0 | 0 | 0 | 0 | 239.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179975 | 0 | 179975 | 353949 | -439281 | 30 | 34 | 353949 | -1439281
3 | 14 | 13 | 2 | 41.258 | 0 | 165.698 | 0 | 24.648 | 0 | 6.2964 | 19.0363 | 0 | 0 | 0 | 0 | 256.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179971 | 0 | 179971 | 387407 | -359492 | 30 | 34 | 387407 | -1359492
3 | 14 | 14 | 2 | 40.6529 | 0 | 172.702 | 0 | 25.7739 | 0 | 6.3133 | 19.0363 | 0 | 0 | 0 | 0 | 264.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177643 | 0 | 177643 | 405735 | -331895 | 30 | 35 | 405735 | -1331895
3 | 14 | 15 | 2 | 40.5633 | 0 | 173.986 | 0 | 25.9682 | 0 | 6.3205 | 19.0363 | 0 | 0 | 0 | 0 | 265.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161481 | 0 | 161481 | 408500 | -320647 | 30 | 35 | 408500 | -1320647
3 | 14 | 16 | 2 | 40.3294 | 0 | 169.782 | 0 | 25.6883 | 0 | 6.3169 | 19.0363 | 0 | 0 | 0 | 0 | 261.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131785 | 0 | 131785 | 404001 | -334443 | 30 | 35 | 404001 | -1334443
3 | 14 | 17 | 2 | 35.516 | 0 | 152.497 | 0 | 25.9108 | 0 | 6.3044 | 19.0363 | 0 | 0 | 0 | 2 | 241.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98792.2 | 0 | 98792.2 | 388603 | -387410 | 30 | 35 | 388603 | -1387410
3 | 14 | 18 | 2 | 25.988 | 0 | 93.4203 | 25.0971 | 0 | 0 | 25.3078 | 19.0363 | 0 | 0 | 0 | 5.6 | 194.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61111.2 | 0 | 61111.2 | 302526 | -430896 | 30 | 35 | 302526 | -1430896
3 | 14 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 13.6754 | 0 | 5.9431 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43682.1 | 0 | 43682.1 | 180984 | -11106.4 | 29 | 32 | 180984 | -1011106.4
3 | 14 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 11.9171 | 0 | 5.9134 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38754.4 | 0 | 38754.4 | 161775 | -15371.9 | 28 | 30 | 161775 | -1015371.9
3 | 14 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 14.1046 | 0 | 5.9433 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23731.8 | 0 | 23731.8 | 175187 | -23397.3 | 26 | 27 | 175187 | -1023397.3
3 | 14 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.8541 | 0 | 5.9197 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12707.3 | 0 | 12707.3 | 158208 | -43708.4 | 25 | 26 | 158208 | -1043708.4
3 | 14 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 12.2579 | 0 | 5.9115 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.5 | 0 | 11041.5 | 150981 | -62668.6 | 25 | 26 | 150981 | -1062668.6
3 | 14 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 11.9167 | 0 | 5.9079 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045.7 | 0 | 11045.7 | 147504 | -73858.9 | 24 | 25 | 147504 | -1073858.9
3 | 15 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.7211 | 0 | 5.906 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048.8 | 0 | 11048.8 | 145565 | -90372.9 | 25 | 26 | 145565 | -1090372.9
3 | 15 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5518 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051.8 | 0 | 11051.8 | 144102 | -100517 | 26 | 27 | 144102 | -1100517
3 | 15 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.4195 | 0 | 5.9036 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11054.4 | 0 | 11054.4 | 142792 | -108453 | 26 | 28 | 142792 | -1108453
3 | 15 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.5555 | 0 | 5.9049 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12288.7 | 0 | 12288.7 | 144969 | -119181 | 26 | 27 | 144969 | -1119181
3 | 15 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.876 | 0 | 5.9671 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29976.1 | 0 | 29976.1 | 192328 | -102615 | 25 | 27 | 192328 | -1102615
3 | 15 | 6 | 3 | 49.0171 | 0 | 140.608 | 44.2675 | 0 | 0 | 25.2246 | 19.0886 | 0 | 0 | 0 | 1.2 | 279.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89018.8 | 0 | 89018.8 | 322180 | -801312 | 25 | 26 | 322180 | -1801312
3 | 15 | 7 | 3 | 51.6349 | 0 | 168.222 | 41.1554 | 0 | 0 | 25.2424 | 19.0364 | 0 | 0 | 0 | 0 | 305.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108136 | 0 | 108136 | 383666 | -719831 | 25 | 27 | 383666 | -1719831
3 | 15 | 8 | 3 | 40.3597 | 0 | 173.795 | 32.4949 | 0 | 0 | 25.2534 | 19.0363 | 0 | 0 | 0 | 0 | 290.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149723 | 0 | 149723 | 402252 | -609237 | 24 | 27 | 402252 | -1609237
3 | 15 | 9 | 3 | 40.6607 | 0 | 172.186 | 29.3518 | 0 | 0 | 25.2675 | 19.0363 | 0 | 0 | 0 | 0 | 286.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176194 | 0 | 176194 | 400144 | -537782 | 24 | 28 | 400144 | -1537782
3 | 15 | 10 | 3 | 41.2019 | 0 | 163.102 | 28.4971 | 0 | 0 | 25.2867 | 19.0363 | 0 | 0 | 0 | 0 | 277.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 389390 | -496877 | 26 | 30 | 389390 | -1496877
3 | 15 | 11 | 3 | 40.719 | 0 | 149.692 | 0 | 26.4561 | 0 | 6.3003 | 19.0363 | 0 | 0 | 0 | 0 | 242.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179969 | 0 | 179969 | 375693 | -413255 | 28 | 33 | 375693 | -1413255
3 | 15 | 12 | 3 | 39.7655 | 0 | 150.207 | 0 | 24.4767 | 0 | 6.3119 | 19.0363 | 0 | 0 | 0 | 0 | 239.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179967 | 0 | 179967 | 355643 | -357740 | 29 | 35 | 355643 | -1357740
3 | 15 | 13 | 3 | 41.3042 | 0 | 165.698 | 0 | 25.1563 | 0 | 6.3217 | 19.0363 | 0 | 0 | 0 | 0 | 257.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179964 | 0 | 179964 | 388942 | -306749 | 29 | 35 | 388942 | -1306749
3 | 15 | 14 | 3 | 40.6912 | 0 | 172.702 | 0 | 25.8798 | 0 | 6.3299 | 19.0363 | 0 | 0 | 0 | 0 | 264.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177636 | 0 | 177636 | 407099 | -288108 | 29 | 35 | 407099 | -1288108
3 | 15 | 15 | 3 | 40.593 | 0 | 173.986 | 0 | 26.1908 | 0 | 12.9012 | 19.0363 | 0 | 0 | 0 | 0 | 272.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161475 | 0 | 161475 | 411875 | -291837 | 28 | 35 | 411875 | -1291837
3 | 15 | 16 | 3 | 40.3535 | 0 | 169.782 | 0 | 25.8018 | 0 | 6.3157 | 19.0363 | 0 | 0 | 0 | 0 | 261.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131779 | 0 | 131779 | 405804 | -336056 | 28 | 33 | 405804 | -1336056
3 | 15 | 17 | 3 | 35.7111 | 0 | 152.497 | 0 | 26.3119 | 0 | 6.3023 | 19.0363 | 0 | 0 | 0 | 2 | 241.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98786.3 | 0 | 98786.3 | 387865 | -406727 | 27 | 32 | 387865 | -1406727
3 | 15 | 18 | 3 | 26.0972 | 0 | 93.4203 | 28.118 | 0 | 0 | 25.305 | 19.0363 | 0 | 0 | 0 | 5.6 | 197.577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61105.9 | 0 | 61105.9 | 303388 | -471363 | 25 | 30 | 303388 | -1471363
3 | 15 | 19 | 3 | 24.195 | 0 | 62.7906 | 0 | 14.8245 | 0 | 5.96 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43677.3 | 0 | 43677.3 | 181663 | -14037 | 24 | 28 | 181663 | -1014037
3 | 15 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.1582 | 0 | 5.9249 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38749.4 | 0 | 38749.4 | 162528 | -20303.2 | 23 | 26 | 162528 | -1020303.2
3 | 15 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 13.9161 | 0 | 5.9409 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23726.4 | 0 | 23726.4 | 175419 | -36084.4 | 21 | 24 | 175419 | -1036084.4
3 | 15 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.6686 | 0 | 5.9183 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12702.3 | 0 | 12702.3 | 158853 | -54144.4 | 21 | 23 | 158853 | -1054144.4
3 | 15 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 12.0899 | 0 | 5.9105 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.9688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.7 | 0 | 11036.7 | 151613 | -72390.9 | 20 | 23 | 151613 | -1072390.9
3 | 15 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 11.889 | 0 | 5.9079 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041 | 0 | 11041 | 148296 | -85753.5 | 20 | 22 | 148296 | -1085753.5
3 | 16 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.358 | 0 | 5.9127 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.5 | 0 | 11044.5 | 152359 | -97883.7 | 20 | 22 | 152359 | -1097883.7
3 | 16 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.7512 | 0 | 5.906 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047.5 | 0 | 11047.5 | 144617 | -96249.5 | 20 | 22 | 144617 | -1096249.5
3 | 16 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.5265 | 0 | 5.9045 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11050 | 0 | 11050 | 144240 | -120167 | 20 | 22 | 144240 | -1120167
3 | 16 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.5115 | 0 | 5.9047 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.3712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12283.9 | 0 | 12283.9 | 145261 | -132305 | 20 | 22 | 145261 | -1132305
3 | 16 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.9777 | 0 | 5.9719 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29971.4 | 0 | 29971.4 | 196176 | -122046 | 20 | 21 | 196176 | -1122046
3 | 16 | 6 | 4 | 49.0171 | 0 | 140.608 | 47.5345 | 0 | 0 | 25.2157 | 19.0865 | 0 | 0 | 0 | 1.2 | 282.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89014.2 | 0 | 89014.2 | 322136 | -862045 | 20 | 21 | 322136 | -1862045
3 | 16 | 7 | 4 | 50.0863 | 0 | 168.222 | 44.1454 | 0 | 0 | 25.2315 | 19.041 | 0 | 0 | 0 | 0 | 306.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108132 | 0 | 108132 | 383803 | -778476 | 22 | 23 | 383803 | -1778476
3 | 16 | 8 | 4 | 40.1636 | 0 | 173.795 | 35.3823 | 0 | 0 | 25.2502 | 19.0363 | 0 | 0 | 0 | 0 | 293.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149719 | 0 | 149719 | 402686 | -645230 | 23 | 25 | 402686 | -1645230
3 | 16 | 9 | 4 | 40.6568 | 0 | 172.186 | 31.8213 | 0 | 0 | 25.2663 | 19.0363 | 0 | 0 | 0 | 0 | 288.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176191 | 0 | 176191 | 400585 | -571915 | 25 | 27 | 400585 | -1571915
3 | 16 | 10 | 4 | 41.1995 | 0 | 163.102 | 30.3592 | 0 | 0 | 25.283 | 19.0363 | 0 | 0 | 0 | 0 | 278.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179966 | 0 | 179966 | 388343 | -526221 | 27 | 30 | 388343 | -1526221
3 | 16 | 11 | 4 | 40.7315 | 0 | 149.692 | 0 | 26.5954 | 0 | 6.2955 | 19.0363 | 0 | 0 | 0 | 0 | 242.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179965 | 0 | 179965 | 376278 | -431194 | 29 | 33 | 376278 | -1431194
3 | 16 | 12 | 4 | 39.8597 | 0 | 150.207 | 0 | 24.4382 | 0 | 6.2907 | 19.0363 | 0 | 0 | 0 | 0 | 239.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179964 | 0 | 179964 | 355776 | -402436 | 31 | 36 | 355776 | -1402436
3 | 16 | 13 | 4 | 41.6375 | 0 | 165.698 | 0 | 24.9594 | 0 | 6.2848 | 19.0363 | 0 | 0 | 0 | 0 | 257.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179961 | 0 | 179961 | 388826 | -392260 | 29 | 33 | 388826 | -1392260
3 | 16 | 14 | 4 | 40.9486 | 0 | 172.702 | 0 | 25.8126 | 0 | 25.2868 | 19.0363 | 0 | 0 | 0 | 0 | 283.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177633 | 0 | 177633 | 406973 | -414859 | 27 | 30 | 406973 | -1414859
3 | 16 | 15 | 4 | 40.8077 | 0 | 173.986 | 0 | 25.9734 | 0 | 25.2824 | 19.0363 | 0 | 0 | 0 | 0 | 285.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161472 | 0 | 161472 | 409621 | -458237 | 24 | 27 | 409621 | -1458237
3 | 16 | 16 | 4 | 40.3165 | 0 | 169.782 | 0 | 26.4028 | 0 | 25.2792 | 19.0363 | 0 | 0 | 0 | 0 | 280.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131777 | 0 | 131777 | 402822 | -502524 | 23 | 26 | 402822 | -1502524
3 | 16 | 17 | 4 | 35.5409 | 0 | 152.497 | 33.6442 | 0 | 0 | 6.2633 | 19.0363 | 0 | 0 | 0 | 2 | 248.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98785.5 | 0 | 98785.5 | 396714 | -602067 | 21 | 24 | 396714 | -1602067
3 | 16 | 18 | 4 | 26.4846 | 0 | 93.4203 | 38.9201 | 0 | 0 | 6.2717 | 19.0363 | 0 | 0 | 0 | 5.6 | 189.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61105.6 | 0 | 61105.6 | 311297 | -644076 | 20 | 23 | 311297 | -1644076
3 | 16 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.4425 | 0 | 5.9538 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43677.5 | 0 | 43677.5 | 181100 | -17545.4 | 19 | 22 | 181100 | -1017545.4
3 | 16 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.7011 | 0 | 5.9623 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38749.6 | 0 | 38749.6 | 189295 | -37090.5 | 17 | 20 | 189295 | -1037090.5
3 | 16 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.1555 | 0 | 5.9288 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23726.5 | 0 | 23726.5 | 169819 | -61336.6 | 16 | 19 | 169819 | -1061336.6
3 | 16 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.0189 | 0 | 5.9115 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.3713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12703.8 | 0 | 12703.8 | 155320 | -95017.5 | 15 | 18 | 155320 | -1095017.5
3 | 16 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.5023 | 0 | 5.9057 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.4 | 0 | 11038.4 | 148701 | -130054 | 14 | 17 | 148701 | -1130054
3 | 16 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 11.224 | 0 | 5.9035 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.9 | 0 | 11042.9 | 145954 | -147894 | 13 | 16 | 145954 | -1147894
3 | 17 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.0749 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11046.7 | 0 | 11046.7 | 144235 | -169769 | 12 | 15 | 144235 | -1169769
3 | 17 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9229 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.9 | 0 | 11049.9 | 142690 | -186909 | 11 | 13 | 142690 | -1186909
3 | 17 | 3 | 5 | 10.8489 | 0 | 42.3304 | 11.2349 | 0 | 0 | 8.5993 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11052.9 | 0 | 11052.9 | 141305 | -203881 | 10 | 12 | 141305 | -1203881
3 | 17 | 4 | 5 | 11.8202 | 0 | 44.8242 | 12.2194 | 0 | 0 | 9.4397 | 17.5105 | 0 | 0 | 0 | 4.8 | 100.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12287.6 | 0 | 12287.6 | 143028 | -220012 | 9 | 11 | 143028 | -1220012
3 | 17 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.9616 | 0 | 5.9511 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29975.4 | 0 | 29975.4 | 189429 | -207619 | 7 | 9 | 189429 | -1207619
3 | 17 | 6 | 5 | 49.0171 | 0 | 140.608 | 62.6173 | 0 | 0 | 25.2094 | 19.2727 | 0 | 0 | 0 | 1.2 | 297.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89018.7 | 0 | 89018.7 | 319862 | -1127670 | 6 | 8 | 319862 | -2127670
3 | 17 | 7 | 5 | 48.9279 | 0 | 168.222 | 56.946 | 0 | 0 | 25.2079 | 19.1324 | 0 | 0 | 0 | 0 | 318.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108136 | 0 | 108136 | 381988 | -1034670 | 7 | 10 | 381988 | -2034670
3 | 17 | 8 | 5 | 40.5197 | 0 | 173.795 | 47.0435 | 0 | 0 | 25.2171 | 19.0363 | 0 | 0 | 0 | 0 | 305.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149722 | 0 | 149722 | 401184 | -879838 | 9 | 11 | 401184 | -1879838
3 | 17 | 9 | 5 | 40.882 | 0 | 172.186 | 42.6151 | 0 | 0 | 25.2248 | 19.0363 | 0 | 0 | 0 | 0 | 299.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176194 | 0 | 176194 | 398874 | -799802 | 10 | 13 | 398874 | -1799802
3 | 17 | 10 | 5 | 41.2865 | 0 | 163.102 | 41.2879 | 0 | 0 | 25.2339 | 19.0363 | 0 | 0 | 0 | 0 | 289.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 380343 | -767673 | 12 | 15 | 380343 | -1767673
3 | 17 | 11 | 5 | 40.7055 | 0 | 149.692 | 36.019 | 0 | 0 | 6.2495 | 19.0363 | 0 | 0 | 0 | 0 | 251.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 364517 | -646144 | 14 | 18 | 364517 | -1646144
3 | 17 | 12 | 5 | 39.7647 | 0 | 150.207 | 33.3472 | 0 | 0 | 6.2556 | 19.0363 | 0 | 0 | 0 | 0 | 248.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179968 | 0 | 179968 | 353692 | -604124 | 16 | 20 | 353692 | -1604124
3 | 17 | 13 | 5 | 41.3117 | 0 | 165.698 | 27.6078 | 0 | 0 | 6.2657 | 19.0363 | 0 | 0 | 0 | 0 | 259.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179965 | 0 | 179965 | 386780 | -536100 | 16 | 21 | 386780 | -1536100
3 | 17 | 14 | 5 | 40.6984 | 0 | 172.702 | 0 | 26.1911 | 0 | 6.2731 | 19.0363 | 0 | 0 | 0 | 0 | 264.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177639 | 0 | 177639 | 405424 | -514640 | 17 | 21 | 405424 | -1514640
3 | 17 | 15 | 5 | 40.5995 | 0 | 173.986 | 0 | 26.0462 | 0 | 6.2733 | 19.0363 | 0 | 0 | 0 | 0 | 265.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161478 | 0 | 161478 | 408221 | -510347 | 17 | 22 | 408221 | -1510347
3 | 17 | 16 | 5 | 40.3584 | 0 | 169.782 | 28.6501 | 0 | 0 | 6.2673 | 19.0363 | 0 | 0 | 0 | 0 | 264.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131784 | 0 | 131784 | 400719 | -554084 | 17 | 21 | 400719 | -1554084
3 | 17 | 17 | 5 | 35.9018 | 0 | 152.497 | 34.2694 | 0 | 0 | 25.2603 | 19.0363 | 0 | 0 | 0 | 2 | 268.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98792.6 | 0 | 98792.6 | 391110 | -634406 | 16 | 20 | 391110 | -1634406
3 | 17 | 18 | 5 | 26.0021 | 0 | 93.4203 | 40.2519 | 0 | 0 | 25.264 | 19.0363 | 0 | 0 | 0 | 5.6 | 209.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61112.9 | 0 | 61112.9 | 311319 | -671354 | 15 | 19 | 311319 | -1671354
3 | 17 | 19 | 5 | 24.1819 | 0 | 62.7906 | 0 | 14.0049 | 0 | 5.9466 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43684.2 | 0 | 43684.2 | 179663 | -19723.4 | 14 | 17 | 179663 | -1019723.4
3 | 17 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 14.1744 | 0 | 5.9522 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38755.8 | 0 | 38755.8 | 186314 | -44107.5 | 13 | 16 | 186314 | -1044107.5
3 | 17 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.7601 | 0 | 5.9234 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23732.8 | 0 | 23732.8 | 167411 | -85138.2 | 12 | 14 | 167411 | -1085138.2
3 | 17 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.7115 | 0 | 5.9085 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12710.2 | 0 | 12710.2 | 152933 | -119429 | 11 | 13 | 152933 | -1119429
3 | 17 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.3383 | 0 | 5.9046 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.2113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.8 | 0 | 11044.8 | 147833 | -147819 | 10 | 11 | 147833 | -1147819
3 | 17 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 11.0592 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.2 | 0 | 11049.2 | 143592 | -166091 | 9 | 10 | 143592 | -1166091
3 | 18 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7714 | 0 | 5.908 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11052.8 | 0 | 11052.8 | 150807 | -187698 | 8 | 9 | 150807 | -1187698
3 | 18 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.232 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11056.4 | 0 | 11056.4 | 140354 | -175550 | 8 | 9 | 140354 | -1175550
3 | 18 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4766 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059.3 | 0 | 11059.3 | 143073 | -192889 | 7 | 8 | 143073 | -1192889
3 | 18 | 4 | 6 | 6.3817 | 0 | 42.7453 | 11.7707 | 0 | 0 | 8.8781 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061.3 | 0 | 11061.3 | 137860 | -196234 | 6 | 7 | 137860 | -1196234
3 | 18 | 5 | 6 | 6.3817 | 0 | 42.7453 | 12.6535 | 0 | 0 | 9.6138 | 17.3638 | 0 | 0 | 0 | 3.6 | 92.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11063.3 | 0 | 11063.3 | 138868 | -213376 | 5 | 6 | 138868 | -1213376
3 | 18 | 6 | 6 | 6.3817 | 0 | 42.7453 | 13.0518 | 0 | 0 | 9.8774 | 17.3638 | 0 | 0 | 0 | 1.2 | 90.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11065.2 | 0 | 11065.2 | 135576 | -216439 | 4 | 5 | 135576 | -1216439
3 | 18 | 7 | 6 | 5.8285 | 0 | 42.7453 | 72.3696 | 0 | 0 | 25.2141 | 19.6432 | 0 | 0 | 0 | 0 | 165.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.9 | 0 | 11066.9 | 123064 | -1129870 | 7 | 8 | 123064 | -2129870
3 | 18 | 8 | 6 | 4.9967 | 0 | 42.7453 | 64.7177 | 0 | 0 | 25.2259 | 19.2033 | 0 | 0 | 0 | 0 | 156.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11068.3 | 0 | 11068.3 | 122394 | -977010 | 10 | 12 | 122394 | -1977010
3 | 18 | 9 | 6 | 5.4852 | 0 | 42.7453 | 53.5528 | 0 | 0 | 25.2349 | 18.9383 | 0 | 0 | 0 | 0 | 145.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11057.4 | 0 | 11057.4 | 121785 | -833507 | 13 | 15 | 121785 | -1833507
3 | 18 | 10 | 6 | 5.4745 | 0 | 42.7453 | 46.5904 | 0 | 0 | 25.2385 | 18.8896 | 0 | 0 | 0 | 0 | 138.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.3 | 0 | 11053.3 | 121321 | -742778 | 15 | 18 | 121321 | -1742778
3 | 18 | 11 | 6 | 5.4689 | 0 | 42.7453 | 39.9838 | 0 | 0 | 25.245 | 18.8896 | 0 | 0 | 0 | 0 | 132.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051.6 | 0 | 11051.6 | 120869 | -664053 | 18 | 22 | 120869 | -1664053
3 | 18 | 12 | 6 | 5.4693 | 0 | 42.7453 | 35.6635 | 0 | 0 | 6.2447 | 18.8896 | 0 | 0 | 0 | 0 | 109.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11050.5 | 0 | 11050.5 | 120470 | -610711 | 20 | 25 | 120470 | -1610711
3 | 18 | 13 | 6 | 5.4743 | 0 | 42.7453 | 32.046 | 0 | 0 | 6.2484 | 18.8896 | 0 | 0 | 0 | 0 | 105.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.9 | 0 | 11049.9 | 120158 | -559000 | 22 | 27 | 120158 | -1559000
3 | 18 | 14 | 6 | 5.4747 | 0 | 42.7453 | 0 | 9.8291 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 76.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.5 | 0 | 11049.5 | 119899 | -18469.9 | 23 | 30 | 119899 | -1018469.9
3 | 18 | 15 | 6 | 5.4761 | 0 | 42.7453 | 0 | 11.9279 | 0 | 5.908 | 17.3638 | 0 | 0 | 0 | 0 | 83.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.4 | 0 | 11049.4 | 148297 | -35649.2 | 25 | 32 | 148297 | -1035649.2
3 | 18 | 16 | 6 | 5.4774 | 0 | 42.7453 | 0 | 11.7038 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 0 | 83.1958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053.6 | 0 | 11053.6 | 144484 | -39852.2 | 25 | 32 | 144484 | -1039852.2
3 | 18 | 17 | 6 | 5.4793 | 0 | 42.7453 | 0 | 11.3824 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 2 | 84.8734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11056.5 | 0 | 11056.5 | 140112 | -42784.2 | 25 | 31 | 140112 | -1042784.2
3 | 18 | 18 | 6 | 7.7545 | 0 | 42.7453 | 0 | 11.1188 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.4832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059.4 | 0 | 11059.4 | 137112 | -52191.6 | 24 | 31 | 137112 | -1052191.6
3 | 18 | 19 | 6 | 8.7863 | 0 | 42.7453 | 0 | 10.9384 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061.9 | 0 | 11061.9 | 135010 | -72587.9 | 25 | 31 | 135010 | -1072587.9
3 | 18 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8136 | 0 | 5.8992 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.8191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11064.4 | 0 | 11064.4 | 133380 | -85657.8 | 25 | 31 | 133380 | -1085657.8
3 | 18 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7161 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.7 | 0 | 11066.7 | 132122 | -95476.3 | 25 | 31 | 132122 | -1095476.3
3 | 18 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6759 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11068.9 | 0 | 11068.9 | 131576 | -104472 | 25 | 31 | 131576 | -1104472
3 | 18 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6096 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.0142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11071 | 0 | 11071 | 130768 | -112733 | 25 | 31 | 130768 | -1112733
3 | 18 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 10.5191 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.3 | 0 | 4118.3 | 129976 | -122897 | 25 | 31 | 129976 | -1122897
3 | 19 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4646 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.11 | 0 | 4120.11 | 129599 | -129544 | 25 | 31 | 129599 | -1129544
3 | 19 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.42 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.3321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.07 | 0 | 4122.07 | 129134 | -136504 | 26 | 30 | 129134 | -1136504
3 | 19 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3582 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.87 | 0 | 4123.87 | 128640 | -142104 | 25 | 30 | 128640 | -1142104
3 | 19 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3257 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.63 | 0 | 4125.63 | 128456 | -150475 | 25 | 30 | 128456 | -1150475
3 | 19 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.2828 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 3.6 | 84.9945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4127.33 | 0 | 4127.33 | 127912 | -155501 | 25 | 30 | 127912 | -1155501
3 | 19 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.2471 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4129.04 | 0 | 4129.04 | 127539 | -160829 | 25 | 30 | 127539 | -1160829
3 | 19 | 7 | 7 | 4.9504 | 0 | 42.7453 | 0 | 10.2328 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 81.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.69 | 0 | 4130.69 | 127394 | -160904 | 26 | 31 | 127394 | -1160904
3 | 19 | 8 | 7 | 4.7389 | 0 | 42.7453 | 0 | 10.2767 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 81.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4132.3 | 0 | 4132.3 | 127811 | -150892 | 28 | 33 | 127811 | -1150892
3 | 19 | 9 | 7 | 5.0166 | 0 | 42.7453 | 0 | 10.2855 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 81.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.87 | 0 | 4133.87 | 127240 | -138544 | 28 | 34 | 127240 | -1138544
3 | 19 | 10 | 7 | 4.641 | 0 | 42.7453 | 0 | 10.3182 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 80.9655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.38 | 0 | 4135.38 | 127022 | -121553 | 29 | 34 | 127022 | -1121553
3 | 19 | 11 | 7 | 4.368 | 0 | 42.7453 | 0 | 10.3687 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.7431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4136.79 | 0 | 4136.79 | 127382 | -104552 | 29 | 35 | 127382 | -1104552
3 | 19 | 12 | 7 | 4.4702 | 0 | 42.7453 | 0 | 10.406 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.8827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4138.08 | 0 | 4138.08 | 127537 | -102147 | 29 | 35 | 127537 | -1102147
3 | 19 | 13 | 7 | 4.4111 | 0 | 42.7453 | 0 | 10.3869 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.8045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.28 | 0 | 4139.28 | 127026 | -97143.3 | 29 | 35 | 127026 | -1097143.3
3 | 19 | 14 | 7 | 4.4354 | 0 | 42.7453 | 0 | 10.4012 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.35 | 0 | 4140.35 | 127147 | -95648.6 | 30 | 35 | 127147 | -1095648.6
3 | 19 | 15 | 7 | 4.5594 | 0 | 42.7453 | 0 | 10.3796 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.9453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.48 | 0 | 4141.48 | 126714 | -98360.5 | 29 | 35 | 126714 | -1098360.5
3 | 19 | 16 | 7 | 4.6897 | 0 | 42.7453 | 0 | 10.3754 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 81.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4142.57 | 0 | 4142.57 | 126560 | -103289 | 30 | 35 | 126560 | -1103289
3 | 19 | 17 | 7 | 5.0102 | 0 | 42.7453 | 0 | 10.3659 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 2 | 83.3824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4143.67 | 0 | 4143.67 | 126346 | -115224 | 30 | 35 | 126346 | -1115224
3 | 19 | 18 | 7 | 5.9502 | 0 | 42.7453 | 0 | 10.3477 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.9042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.79 | 0 | 4144.79 | 126074 | -127647 | 30 | 35 | 126074 | -1127647
3 | 19 | 19 | 7 | 6.6549 | 0 | 42.7453 | 0 | 10.3498 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4145.92 | 0 | 4145.92 | 126089 | -137586 | 30 | 35 | 126089 | -1137586
3 | 19 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3194 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.05 | 0 | 4147.05 | 125753 | -143066 | 30 | 35 | 125753 | -1143066
3 | 19 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2928 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4148.15 | 0 | 4148.15 | 125558 | -148130 | 30 | 35 | 125558 | -1148130
3 | 19 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2854 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.3549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149.22 | 0 | 4149.22 | 125573 | -152875 | 31 | 34 | 125573 | -1152875
3 | 19 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2469 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4150.3 | 0 | 4150.3 | 125295 | -160123 | 31 | 32 | 125295 | -1160123
3 | 19 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 10.2151 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11106 | 0 | 11106 | 125416 | -165289 | 31 | 31 | 125416 | -1165289
3 | 20 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1878 | 0 | 5.8963 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.4272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11107.1 | 0 | 11107.1 | 125408 | -170979 | 31 | 31 | 125408 | -1170979
3 | 20 | 2 | 1 | 10.8489 | 0 | 42.3304 | 10.36 | 0 | 0 | 7.9297 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11107.4 | 0 | 11107.4 | 125249 | -174032 | 31 | 31 | 125249 | -1174032
3 | 20 | 3 | 1 | 10.8489 | 0 | 42.3304 | 10.5864 | 0 | 0 | 8.0966 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11108.2 | 0 | 11108.2 | 125442 | -177203 | 31 | 31 | 125442 | -1177203
3 | 20 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.4168 | 0 | 5.8951 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12340.9 | 0 | 12340.9 | 128388 | -177502 | 31 | 31 | 128388 | -1177502
3 | 20 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.7864 | 0 | 5.9393 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30026.9 | 0 | 30026.9 | 176062 | -140099 | 31 | 32 | 176062 | -1140099
3 | 20 | 6 | 1 | 49.0171 | 0 | 140.608 | 51.1544 | 0 | 0 | 25.2233 | 19.3248 | 0 | 0 | 0 | 1.2 | 286.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89068.3 | 0 | 89068.3 | 311192 | -874855 | 31 | 32 | 311192 | -1874855
3 | 20 | 7 | 1 | 50.8756 | 0 | 168.222 | 44.2983 | 0 | 0 | 25.2414 | 19.1515 | 0 | 0 | 0 | 0 | 307.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108184 | 0 | 108184 | 373828 | -756634 | 32 | 32 | 373828 | -1756634
3 | 20 | 8 | 1 | 40.7211 | 0 | 173.795 | 32.7947 | 0 | 0 | 25.2506 | 19.0363 | 0 | 0 | 0 | 0 | 291.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149758 | 0 | 149758 | 392737 | -612663 | 32 | 33 | 392737 | -1612663
3 | 20 | 9 | 1 | 41.3958 | 0 | 172.186 | 30.7986 | 0 | 0 | 25.2633 | 19.0363 | 0 | 0 | 0 | 0 | 288.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176227 | 0 | 176227 | 391399 | -564195 | 33 | 33 | 391399 | -1564195
3 | 20 | 10 | 1 | 41.8753 | 0 | 163.102 | 32.1628 | 0 | 0 | 25.2734 | 19.0363 | 0 | 0 | 0 | 0 | 281.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180000 | 0 | 180000 | 382508 | -557580 | 33 | 33 | 382508 | -1557580
3 | 20 | 11 | 1 | 40.9983 | 0 | 149.692 | 27.8194 | 0 | 0 | 25.2787 | 19.0363 | 0 | 0 | 0 | 0 | 262.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179998 | 0 | 179998 | 365459 | -489785 | 33 | 34 | 365459 | -1489785
3 | 20 | 12 | 1 | 39.8009 | 0 | 150.207 | 25.5985 | 0 | 0 | 25.2771 | 19.0363 | 0 | 0 | 0 | 0 | 259.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179996 | 0 | 179996 | 348072 | -467611 | 34 | 34 | 348072 | -1467611
3 | 20 | 13 | 1 | 41.48 | 0 | 165.698 | 0 | 24.3816 | 0 | 6.2784 | 19.0363 | 0 | 0 | 0 | 0 | 256.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179993 | 0 | 179993 | 381396 | -409966 | 34 | 34 | 381396 | -1409966
3 | 20 | 14 | 1 | 40.843 | 0 | 172.702 | 0 | 25.3868 | 0 | 6.2879 | 19.0363 | 0 | 0 | 0 | 0 | 264.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177665 | 0 | 177665 | 399978 | -391074 | 34 | 34 | 399978 | -1391074
3 | 20 | 15 | 1 | 40.8367 | 0 | 173.986 | 0 | 25.597 | 0 | 6.2931 | 19.0363 | 0 | 0 | 0 | 0 | 265.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161502 | 0 | 161502 | 403114 | -394467 | 34 | 34 | 403114 | -1394467
3 | 20 | 16 | 1 | 41.1938 | 0 | 169.782 | 0 | 25.2566 | 0 | 6.289 | 19.0363 | 0 | 0 | 0 | 0 | 261.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131807 | 0 | 131807 | 396958 | -419657 | 33 | 34 | 396958 | -1419657
3 | 20 | 17 | 1 | 36.6752 | 0 | 152.497 | 27.4949 | 0 | 0 | 25.2819 | 19.0363 | 0 | 0 | 0 | 2 | 262.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98813.8 | 0 | 98813.8 | 383970 | -486192 | 33 | 33 | 383970 | -1486192
3 | 20 | 18 | 1 | 29.8553 | 0 | 93.4203 | 30.8131 | 0 | 0 | 25.2887 | 19.0363 | 0 | 0 | 0 | 5.6 | 204.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61132.5 | 0 | 61132.5 | 293718 | -516515 | 33 | 33 | 293718 | -1516515
3 | 20 | 19 | 1 | 24.1529 | 0 | 62.7906 | 0 | 13.2564 | 0 | 5.935 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43703.4 | 0 | 43703.4 | 176465 | -10991.7 | 33 | 33 | 176465 | -1010991.7
3 | 20 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.0655 | 0 | 5.9127 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38775.6 | 0 | 38775.6 | 157539 | -17192 | 33 | 33 | 157539 | -1017192
3 | 20 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.595 | 0 | 5.9324 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23752.8 | 0 | 23752.8 | 168030 | -29747.2 | 33 | 33 | 168030 | -1029747.2
3 | 20 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.4128 | 0 | 5.9132 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12728.5 | 0 | 12728.5 | 152026 | -44575.6 | 32 | 33 | 152026 | -1044575.6
3 | 20 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.8817 | 0 | 5.907 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11062.3 | 0 | 11062.3 | 145383 | -60083.8 | 32 | 33 | 145383 | -1060083.8
3 | 20 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 11.5905 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11065.9 | 0 | 11065.9 | 142447 | -68399.3 | 32 | 33 | 142447 | -1068399.3
3 | 21 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4407 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11068.6 | 0 | 11068.6 | 140915 | -81332.8 | 32 | 33 | 140915 | -1081332.8
3 | 21 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3295 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11071.1 | 0 | 11071.1 | 139730 | -92343.5 | 32 | 33 | 139730 | -1092343.5
3 | 21 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.2459 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11073.2 | 0 | 11073.2 | 138788 | -101962 | 32 | 33 | 138788 | -1101962
3 | 21 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.4228 | 0 | 5.9032 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12307.1 | 0 | 12307.1 | 141358 | -108759 | 32 | 33 | 141358 | -1108759
3 | 21 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.8147 | 0 | 5.9633 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29994 | 0 | 29994 | 189000 | -89114.9 | 32 | 33 | 189000 | -1089114.9
3 | 21 | 6 | 2 | 49.0171 | 0 | 140.608 | 39.6636 | 0 | 0 | 25.2401 | 19.072 | 0 | 0 | 0 | 1.2 | 274.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89036.3 | 0 | 89036.3 | 320012 | -704615 | 31 | 33 | 320012 | -1704615
3 | 21 | 7 | 2 | 50.1599 | 0 | 168.222 | 35.9791 | 0 | 0 | 25.2577 | 19.0363 | 0 | 0 | 0 | 0 | 298.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108153 | 0 | 108153 | 382212 | -630125 | 32 | 34 | 382212 | -1630125
3 | 21 | 8 | 2 | 44.0091 | 0 | 173.795 | 27.2442 | 0 | 0 | 25.2672 | 19.0363 | 0 | 0 | 0 | 0 | 289.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149738 | 0 | 149738 | 400825 | -521558 | 32 | 34 | 400825 | -1521558
3 | 21 | 9 | 2 | 40.6757 | 0 | 172.186 | 0 | 25.9578 | 0 | 6.2774 | 19.0363 | 0 | 0 | 0 | 0 | 264.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176207 | 0 | 176207 | 398839 | -459543 | 32 | 35 | 398839 | -1459543
3 | 21 | 10 | 2 | 41.182 | 0 | 163.102 | 0 | 26.5228 | 0 | 6.2915 | 19.0363 | 0 | 0 | 0 | 0 | 256.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179982 | 0 | 179982 | 388732 | -432292 | 33 | 36 | 388732 | -1432292
3 | 21 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 25.3557 | 0 | 6.3013 | 19.0363 | 0 | 0 | 0 | 0 | 241.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179980 | 0 | 179980 | 372843 | -375505 | 33 | 36 | 372843 | -1375505
3 | 21 | 12 | 2 | 39.8461 | 0 | 150.207 | 0 | 23.7468 | 0 | 6.2928 | 19.0363 | 0 | 0 | 0 | 0 | 239.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179978 | 0 | 179978 | 354375 | -376571 | 33 | 37 | 354375 | -1376571
3 | 21 | 13 | 2 | 41.4461 | 0 | 165.698 | 0 | 24.6466 | 0 | 6.2988 | 19.0363 | 0 | 0 | 0 | 0 | 257.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179974 | 0 | 179974 | 387938 | -332670 | 33 | 37 | 387938 | -1332670
3 | 21 | 14 | 2 | 40.9638 | 0 | 172.702 | 0 | 26.5455 | 0 | 6.305 | 19.0363 | 0 | 0 | 0 | 0 | 265.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177645 | 0 | 177645 | 413799 | -338551 | 33 | 37 | 413799 | -1338551
3 | 21 | 15 | 2 | 40.9783 | 0 | 173.986 | 0 | 26.3868 | 0 | 6.3105 | 19.0363 | 0 | 0 | 0 | 0 | 266.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161483 | 0 | 161483 | 412976 | -338406 | 33 | 37 | 412976 | -1338406
3 | 21 | 16 | 2 | 41.4846 | 0 | 169.782 | 0 | 25.6677 | 0 | 6.302 | 19.0363 | 0 | 0 | 0 | 0 | 262.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131788 | 0 | 131788 | 403874 | -371834 | 33 | 36 | 403874 | -1371834
3 | 21 | 17 | 2 | 37.1466 | 0 | 152.497 | 0 | 25.9071 | 0 | 6.2912 | 19.0363 | 0 | 0 | 0 | 2 | 242.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98794.4 | 0 | 98794.4 | 386671 | -418302 | 33 | 36 | 386671 | -1418302
3 | 21 | 18 | 2 | 29.6117 | 0 | 93.4203 | 27.5719 | 0 | 0 | 25.2953 | 19.0363 | 0 | 0 | 0 | 5.6 | 200.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61113.5 | 0 | 61113.5 | 307992 | -470885 | 32 | 35 | 307992 | -1470885
3 | 21 | 19 | 2 | 24.1865 | 0 | 62.7906 | 0 | 13.2424 | 0 | 5.938 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43684.4 | 0 | 43684.4 | 181051 | -10013.7 | 31 | 33 | 181051 | -1010013.7
3 | 21 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 11.891 | 0 | 5.9132 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38757.2 | 0 | 38757.2 | 161818 | -15113.6 | 29 | 31 | 161818 | -1015113.6
3 | 21 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.9641 | 0 | 5.9413 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23734.5 | 0 | 23734.5 | 175034 | -22690.8 | 27 | 29 | 175034 | -1022690.8
3 | 21 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.8341 | 0 | 5.9195 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12710.1 | 0 | 12710.1 | 158168 | -39648.3 | 27 | 28 | 158168 | -1039648.3
3 | 21 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 12.2171 | 0 | 5.9112 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.0967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044.3 | 0 | 11044.3 | 150821 | -64179.1 | 25 | 26 | 150821 | -1064179.1
3 | 21 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 11.9667 | 0 | 5.9082 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11048.4 | 0 | 11048.4 | 147380 | -74490.5 | 24 | 25 | 147380 | -1074490.5
3 | 22 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 12.3713 | 0 | 5.9123 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11051.6 | 0 | 11051.6 | 150988 | -90756.9 | 24 | 25 | 150988 | -1090756.9
3 | 22 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5073 | 0 | 5.9043 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11054.6 | 0 | 11054.6 | 143812 | -90594.7 | 24 | 24 | 143812 | -1090594.7
3 | 22 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5288 | 0 | 5.9042 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11057 | 0 | 11057 | 142918 | -117297 | 24 | 24 | 142918 | -1117297
3 | 22 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.5614 | 0 | 5.9048 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12290.8 | 0 | 12290.8 | 144623 | -128660 | 24 | 24 | 144623 | -1128660
3 | 22 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.7652 | 0 | 5.9648 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29978.2 | 0 | 29978.2 | 191802 | -115709 | 24 | 24 | 191802 | -1115709
3 | 22 | 6 | 3 | 49.0171 | 0 | 140.608 | 46.3183 | 0 | 0 | 25.2207 | 19.1034 | 0 | 0 | 0 | 1.2 | 281.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89020.9 | 0 | 89020.9 | 321931 | -832811 | 23 | 24 | 321931 | -1832811
3 | 22 | 7 | 3 | 48.0797 | 0 | 168.222 | 42.5933 | 0 | 0 | 25.2393 | 19.0473 | 0 | 0 | 0 | 0 | 303.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108138 | 0 | 108138 | 383780 | -741774 | 25 | 26 | 383780 | -1741774
3 | 22 | 8 | 3 | 40.1847 | 0 | 173.795 | 32.531 | 0 | 0 | 25.2555 | 19.0363 | 0 | 0 | 0 | 0 | 290.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149726 | 0 | 149726 | 402581 | -605416 | 27 | 28 | 402581 | -1605416
3 | 22 | 9 | 3 | 42.1889 | 0 | 172.186 | 30.5903 | 0 | 0 | 25.2687 | 19.0363 | 0 | 0 | 0 | 0 | 289.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176197 | 0 | 176197 | 400509 | -556942 | 28 | 30 | 400509 | -1556942
3 | 22 | 10 | 3 | 41.213 | 0 | 163.102 | 28.2349 | 0 | 0 | 25.287 | 19.0363 | 0 | 0 | 0 | 0 | 276.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179972 | 0 | 179972 | 387217 | -498264 | 31 | 33 | 387217 | -1498264
3 | 22 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 25.6711 | 0 | 6.3049 | 19.0363 | 0 | 0 | 0 | 0 | 241.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179970 | 0 | 179970 | 371056 | -372207 | 34 | 37 | 371056 | -1372207
3 | 22 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 24.6866 | 0 | 6.3242 | 19.0363 | 0 | 0 | 0 | 0 | 240.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179968 | 0 | 179968 | 366146 | -300003 | 36 | 40 | 366146 | -1300003
3 | 22 | 13 | 3 | 41.2562 | 0 | 165.698 | 0 | 28.3686 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179965 | 0 | 179965 | 425682 | -264080 | 38 | 42 | 425682 | -1264080
3 | 22 | 14 | 3 | 40.6383 | 0 | 172.702 | 0 | 32.5266 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177637 | 0 | 177637 | 470163 | -238055 | 40 | 45 | 470163 | -1238055
3 | 22 | 15 | 3 | 40.5521 | 0 | 173.986 | 0 | 32.323 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161474 | 0 | 161474 | 455366 | -202047 | 41 | 47 | 455366 | -1202047
3 | 22 | 16 | 3 | 40.3084 | 0 | 169.782 | 0 | 32.7282 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131777 | 0 | 131777 | 463642 | -215085 | 41 | 46 | 463642 | -1215085
3 | 22 | 17 | 3 | 35.5082 | 0 | 152.497 | 0 | 29.6694 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 245.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98783.2 | 0 | 98783.2 | 433498 | -252948 | 41 | 45 | 433498 | -1252948
3 | 22 | 18 | 3 | 25.4397 | 0 | 93.4203 | 0 | 24.5075 | 0 | 6.32 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61101.8 | 0 | 61101.8 | 349171 | -326976 | 40 | 44 | 349171 | -1326976
3 | 22 | 19 | 3 | 23.9806 | 0 | 62.7906 | 0 | 9.0707 | 0 | 5.4888 | 8.818 | 0 | 0 | 0 | 7.2 | 117.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43672.6 | 0 | 43672.6 | 182863 | 0 | 38 | 41 | 182863 | -1000000
3 | 22 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.0279 | 0 | 5.924 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38744.9 | 0 | 38744.9 | 163465 | -12964.9 | 36 | 38 | 163465 | -1012964.9
3 | 22 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.4536 | 0 | 5.8968 | 12.9754 | 0 | 0 | 0 | 7.2 | 96.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23721.8 | 0 | 23721.8 | 150009 | -9244.72 | 33 | 35 | 150009 | -1009244.72
3 | 22 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.3512 | 0 | 5.9194 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.7116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12696.3 | 0 | 12696.3 | 167644 | -17863.4 | 33 | 34 | 167644 | -1017863.4
3 | 22 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.6611 | 0 | 5.9099 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11029.8 | 0 | 11029.8 | 157743 | -22817.4 | 32 | 34 | 157743 | -1022817.4
3 | 22 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 11.9593 | 0 | 5.9109 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.3 | 0 | 11033.3 | 155332 | -29953.6 | 31 | 33 | 155332 | -1029953.6
3 | 23 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.4563 | 0 | 5.9062 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.6 | 0 | 11036.6 | 151168 | -35042.7 | 30 | 31 | 151168 | -1035042.7
3 | 23 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.7662 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11039.2 | 0 | 11039.2 | 148949 | -40039.2 | 29 | 30 | 148949 | -1040039.2
3 | 23 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.7563 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.6 | 0 | 11041.6 | 147421 | -47154.7 | 28 | 28 | 147421 | -1047154.7
3 | 23 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 10.8008 | 0 | 5.9022 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12275.4 | 0 | 12275.4 | 148579 | -57186.8 | 27 | 27 | 148579 | -1057186.8
3 | 23 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 13.7459 | 0 | 5.9533 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29962.4 | 0 | 29962.4 | 195767 | -52980.6 | 25 | 25 | 195767 | -1052980.6
3 | 23 | 6 | 4 | 49.0171 | 0 | 140.608 | 37.5279 | 0 | 0 | 25.2394 | 19.0363 | 0 | 0 | 0 | 1.2 | 272.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89004.8 | 0 | 89004.8 | 322908 | -690666 | 24 | 24 | 322908 | -1690666
3 | 23 | 7 | 4 | 46.6306 | 0 | 168.222 | 34.6264 | 0 | 0 | 25.264 | 19.0363 | 0 | 0 | 0 | 0 | 293.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108121 | 0 | 108121 | 385270 | -612604 | 27 | 27 | 385270 | -1612604
3 | 23 | 8 | 4 | 39.9559 | 0 | 173.795 | 0 | 26.2986 | 0 | 6.2781 | 19.0363 | 0 | 0 | 0 | 0 | 265.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149714 | 0 | 149714 | 404056 | -454311 | 30 | 31 | 404056 | -1454311
3 | 23 | 9 | 4 | 40.6668 | 0 | 172.186 | 0 | 26.3267 | 0 | 6.2943 | 19.0363 | 0 | 0 | 0 | 0 | 264.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176184 | 0 | 176184 | 401929 | -386521 | 32 | 34 | 401929 | -1386521
3 | 23 | 10 | 4 | 41.18 | 0 | 163.102 | 0 | 28.4614 | 0 | 6.3159 | 19.0363 | 0 | 0 | 0 | 0 | 258.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179958 | 0 | 179958 | 417214 | -345687 | 34 | 38 | 417214 | -1345687
3 | 23 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 28.6442 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179956 | 0 | 179956 | 423627 | -288550 | 36 | 41 | 423627 | -1288550
3 | 23 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 28.0526 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179953 | 0 | 179953 | 406988 | -235921 | 38 | 45 | 406988 | -1235921
3 | 23 | 13 | 4 | 41.2526 | 0 | 165.698 | 0 | 32.1074 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179950 | 0 | 179950 | 460264 | -220555 | 38 | 45 | 460264 | -1220555
3 | 23 | 14 | 4 | 40.6509 | 0 | 172.702 | 0 | 34.0206 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177622 | 0 | 177622 | 482846 | -216019 | 38 | 45 | 482846 | -1216019
3 | 23 | 15 | 4 | 41.0608 | 0 | 173.986 | 0 | 33.1664 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161460 | 0 | 161460 | 470354 | -209056 | 38 | 45 | 470354 | -1209056
3 | 23 | 16 | 4 | 41.332 | 0 | 169.782 | 0 | 33.1013 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131763 | 0 | 131763 | 474604 | -244907 | 38 | 44 | 474604 | -1244907
3 | 23 | 17 | 4 | 36.5292 | 0 | 152.497 | 0 | 28.7489 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 245.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98770.6 | 0 | 98770.6 | 426923 | -275091 | 37 | 43 | 426923 | -1275091
3 | 23 | 18 | 4 | 29.3329 | 0 | 93.4203 | 0 | 23.8723 | 0 | 6.3116 | 19.0363 | 0 | 0 | 0 | 5.6 | 177.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61090.3 | 0 | 61090.3 | 344366 | -343538 | 37 | 42 | 344366 | -1343538
3 | 23 | 19 | 4 | 24.1785 | 0 | 62.7906 | 0 | 9.1119 | 0 | 5.4894 | 8.818 | 0 | 0 | 0 | 7.2 | 117.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43661.9 | 0 | 43661.9 | 183862 | 0 | 36 | 41 | 183862 | -1000000
3 | 23 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 12.6632 | 0 | 5.9209 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38734.1 | 0 | 38734.1 | 164455 | -11673.4 | 36 | 40 | 164455 | -1011673.4
3 | 23 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.4978 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23710 | 0 | 23710 | 150977 | 0 | 35 | 39 | 150977 | -1000000
3 | 23 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.6851 | 0 | 5.9043 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12684.3 | 0 | 12684.3 | 139890 | -20284.9 | 36 | 39 | 139890 | -1020284.9
3 | 23 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 8.0675 | 0 | 5.8978 | 17.5105 | 0 | 0 | 0 | 5.6 | 89.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017.5 | 0 | 11017.5 | 164075 | -12222 | 36 | 40 | 164075 | -1012222
3 | 23 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 11.8107 | 0 | 5.9121 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.4 | 0 | 11020.4 | 160743 | -20403.5 | 36 | 40 | 160743 | -1020403.5
3 | 24 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.8121 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.4 | 0 | 11023.4 | 155996 | -19416.7 | 36 | 40 | 155996 | -1019416.7
3 | 24 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3366 | 0 | 5.9065 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.2 | 0 | 11026.2 | 153921 | -23391.3 | 36 | 39 | 153921 | -1023391.3
3 | 24 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.0907 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.5 | 0 | 11028.5 | 151684 | -26673.6 | 36 | 39 | 151684 | -1026673.6
3 | 24 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.5965 | 0 | 5.9079 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12262.7 | 0 | 12262.7 | 153620 | -29599.2 | 37 | 40 | 153620 | -1029599.2
3 | 24 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.6631 | 0 | 5.9718 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29949.9 | 0 | 29949.9 | 201640 | -26195.5 | 37 | 40 | 201640 | -1026195.5
3 | 24 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 24.0415 | 0 | 6.2878 | 19.0363 | 0 | 0 | 0 | 1.2 | 240.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88992.7 | 0 | 88992.7 | 325087 | -419107 | 37 | 41 | 325087 | -1419107
3 | 24 | 7 | 5 | 47.7529 | 0 | 168.222 | 0 | 29.63 | 0 | 6.292 | 19.0363 | 0 | 0 | 0 | 0 | 270.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108110 | 0 | 108110 | 430089 | -429077 | 38 | 42 | 430089 | -1429077
3 | 24 | 8 | 5 | 40.0007 | 0 | 173.795 | 0 | 30.5665 | 0 | 6.3065 | 19.0363 | 0 | 0 | 0 | 0 | 269.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149702 | 0 | 149702 | 452491 | -329093 | 39 | 43 | 452491 | -1329093
3 | 24 | 9 | 5 | 40.6651 | 0 | 172.186 | 0 | 31.6137 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176173 | 0 | 176173 | 460547 | -274589 | 40 | 44 | 460547 | -1274589
3 | 24 | 10 | 5 | 41.1733 | 0 | 163.102 | 0 | 30.9659 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179948 | 0 | 179948 | 441976 | -231628 | 41 | 46 | 441976 | -1231628
3 | 24 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 31.2947 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179946 | 0 | 179946 | 430640 | -191817 | 43 | 49 | 430640 | -1191817
3 | 24 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 29.6543 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179944 | 0 | 179944 | 400220 | -147824 | 45 | 51 | 400220 | -1147824
3 | 24 | 13 | 5 | 41.292 | 0 | 165.698 | 0 | 34.0609 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179941 | 0 | 179941 | 449869 | -125793 | 45 | 52 | 449869 | -1125793
3 | 24 | 14 | 5 | 40.6769 | 0 | 172.702 | 0 | 36.2021 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177613 | 0 | 177613 | 480176 | -107371 | 46 | 52 | 480176 | -1107371
3 | 24 | 15 | 5 | 40.5661 | 0 | 173.986 | 0 | 32.3745 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161451 | 0 | 161451 | 467724 | -77544.8 | 46 | 53 | 467724 | -1077544.8
3 | 24 | 16 | 5 | 40.3293 | 0 | 169.782 | 0 | 31.4611 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131755 | 0 | 131755 | 467641 | -82986.1 | 46 | 52 | 467641 | -1082986.1
3 | 24 | 17 | 5 | 35.5193 | 0 | 152.497 | 0 | 27.6952 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 243.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98762 | 0 | 98762 | 418863 | -103161 | 47 | 51 | 418863 | -1103161
3 | 24 | 18 | 5 | 25.6051 | 0 | 93.4203 | 0 | 24.7141 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61081.5 | 0 | 61081.5 | 327719 | -175452 | 46 | 50 | 327719 | -1175452
3 | 24 | 19 | 5 | 24.0431 | 0 | 62.7906 | 0 | 9.1828 | 0 | 5.4904 | 8.818 | 0 | 0 | 0 | 7.2 | 117.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43653.4 | 0 | 43653.4 | 185722 | 0 | 46 | 49 | 185722 | -1000000
3 | 24 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.1921 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 103.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38726.4 | 0 | 38726.4 | 166072 | 0 | 46 | 49 | 166072 | -1000000
3 | 24 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 10.5677 | 0 | 5.9024 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.3657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23700.3 | 0 | 23700.3 | 152678 | -8036.54 | 46 | 48 | 152678 | -1008036.54
3 | 24 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.0619 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12673.6 | 0 | 12673.6 | 141474 | 0 | 46 | 48 | 141474 | -1000000
3 | 24 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 10.3706 | 0 | 5.8984 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.7024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11005.9 | 0 | 11005.9 | 136622 | -11879 | 46 | 49 | 136622 | -1011879
3 | 24 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.7572 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11008.2 | 0 | 11008.2 | 134964 | 0 | 47 | 49 | 134964 | -1000000
3 | 25 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.2465 | 0 | 5.8978 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11010 | 0 | 11010 | 133879 | -12819.7 | 47 | 49 | 133879 | -1012819.7
3 | 25 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6596 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 74.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11012.4 | 0 | 11012.4 | 132840 | 0 | 46 | 50 | 132840 | -1000000
3 | 25 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4474 | 0 | 5.9059 | 14.8767 | 0 | 0 | 0 | 4.8 | 86.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11014 | 0 | 11014 | 150477 | -14382.6 | 46 | 50 | 150477 | -1014382.6
3 | 25 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6056 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.7 | 0 | 11015.7 | 131357 | 0 | 44 | 48 | 131357 | -1000000
3 | 25 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.3078 | 0 | 5.9159 | 17.3638 | 0 | 0 | 0 | 3.6 | 88.3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11017.2 | 0 | 11017.2 | 161250 | -16584.4 | 43 | 45 | 161250 | -1016584.4
3 | 25 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.746 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 1.2 | 81.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.7 | 0 | 11018.7 | 156557 | -9510.42 | 41 | 43 | 156557 | -1009510.42
3 | 25 | 7 | 6 | 5.8311 | 0 | 42.7453 | 24.9818 | 0 | 0 | 25.2878 | 18.8896 | 0 | 0 | 0 | 0 | 117.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.6 | 0 | 11020.6 | 136130 | -443124 | 41 | 43 | 136130 | -1443124
3 | 25 | 8 | 6 | 5.3192 | 0 | 42.7453 | 26.2594 | 0 | 0 | 25.2812 | 18.8896 | 0 | 0 | 0 | 0 | 118.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.8 | 0 | 11022.8 | 198538 | -453633 | 41 | 42 | 198538 | -1453633
3 | 25 | 9 | 6 | 6.4875 | 0 | 42.7453 | 22.2297 | 0 | 0 | 25.2775 | 18.8896 | 0 | 0 | 0 | 0 | 115.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.7 | 0 | 11024.7 | 185681 | -401522 | 41 | 42 | 185681 | -1401522
3 | 25 | 10 | 6 | 5.9152 | 0 | 42.7453 | 20.9014 | 0 | 0 | 6.2236 | 18.8896 | 0 | 0 | 0 | 0 | 94.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11022.9 | 0 | 11022.9 | 194077 | -386651 | 41 | 42 | 194077 | -1386651
3 | 25 | 11 | 6 | 5.9132 | 0 | 42.7453 | 20.3028 | 0 | 0 | 6.1918 | 18.8896 | 0 | 0 | 0 | 0 | 94.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11023.8 | 0 | 11023.8 | 187048 | -379594 | 41 | 41 | 187048 | -1379594
3 | 25 | 12 | 6 | 5.6625 | 0 | 42.7453 | 19.4719 | 0 | 0 | 6.1423 | 18.8896 | 0 | 0 | 0 | 0 | 92.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.2 | 0 | 11024.2 | 183207 | -362340 | 40 | 41 | 183207 | -1362340
3 | 25 | 13 | 6 | 5.8923 | 0 | 42.7453 | 19.6193 | 0 | 0 | 6.1507 | 18.8896 | 0 | 0 | 0 | 0 | 93.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.9 | 0 | 11024.9 | 184011 | -366120 | 41 | 41 | 184011 | -1366120
3 | 25 | 14 | 6 | 5.9173 | 0 | 42.7453 | 0 | 6.3509 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 0 | 69.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11025.6 | 0 | 11025.6 | 125120 | 0 | 41 | 42 | 125120 | -1000000
3 | 25 | 15 | 6 | 6.3081 | 0 | 42.7453 | 0 | 10.2546 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 0 | 78.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.5 | 0 | 11026.5 | 124949 | -13233.3 | 42 | 42 | 124949 | -1013233.3
3 | 25 | 16 | 6 | 6.1115 | 0 | 42.7453 | 0 | 6.2744 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 0 | 69.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11027 | 0 | 11027 | 124418 | 0 | 41 | 41 | 124418 | -1000000
3 | 25 | 17 | 6 | 6.5656 | 0 | 42.7453 | 0 | 10.488 | 0 | 5.8974 | 12.8287 | 0 | 0 | 0 | 2 | 80.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11028.8 | 0 | 11028.8 | 124111 | -19505.6 | 41 | 41 | 124111 | -1019505.6
3 | 25 | 18 | 6 | 8.1286 | 0 | 42.7453 | 0 | 7.5645 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.2989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11030.2 | 0 | 11030.2 | 153145 | -13846.9 | 40 | 40 | 153145 | -1013846.9
3 | 25 | 19 | 6 | 8.7591 | 0 | 42.7453 | 0 | 11.0543 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.7 | 0 | 11031.7 | 150618 | -21154.4 | 39 | 39 | 150618 | -1021154.4
3 | 25 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.278 | 0 | 5.8999 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.8 | 0 | 11033.8 | 146631 | -21911.8 | 39 | 39 | 146631 | -1021911.8
3 | 25 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8048 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11036.2 | 0 | 11036.2 | 144762 | -26273.5 | 38 | 38 | 144762 | -1026273.5
3 | 25 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6254 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11038.3 | 0 | 11038.3 | 142946 | -28386.3 | 38 | 38 | 142946 | -1028386.3
3 | 25 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8765 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040.4 | 0 | 11040.4 | 141548 | -31106.6 | 38 | 38 | 141548 | -1031106.6
3 | 25 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 10.7555 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4087.82 | 0 | 4087.82 | 140008 | -33221.7 | 38 | 38 | 140008 | -1033221.7
3 | 26 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9235 | 0 | 5.9005 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4089.88 | 0 | 4089.88 | 138850 | -43066.1 | 37 | 38 | 138850 | -1043066.1
3 | 26 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9141 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4092.06 | 0 | 4092.06 | 138091 | -49683.8 | 37 | 37 | 138091 | -1049683.8
3 | 26 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7883 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4094.1 | 0 | 4094.1 | 137283 | -54019.5 | 37 | 37 | 137283 | -1054019.5
3 | 26 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0678 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4096.08 | 0 | 4096.08 | 139917 | -57982.4 | 37 | 37 | 139917 | -1057982.4
3 | 26 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.9977 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 3.6 | 84.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4097.94 | 0 | 4097.94 | 136050 | -54426.2 | 37 | 37 | 136050 | -1054426.2
3 | 26 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.0753 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.3875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4099.7 | 0 | 4099.7 | 136485 | -58479.3 | 37 | 37 | 136485 | -1058479.3
3 | 26 | 7 | 7 | 4.7456 | 0 | 42.7453 | 0 | 9.6748 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 80.4265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4101.15 | 0 | 4101.15 | 135066 | -55128.3 | 38 | 38 | 135066 | -1055128.3
3 | 26 | 8 | 7 | 4.3613 | 0 | 42.7453 | 0 | 9.4777 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 79.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4102.57 | 0 | 4102.57 | 134692 | -51937.3 | 38 | 38 | 134692 | -1051937.3
3 | 26 | 9 | 7 | 5.0102 | 0 | 42.7453 | 0 | 9.8002 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 80.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103.93 | 0 | 4103.93 | 134485 | -50635 | 39 | 39 | 134485 | -1050635
3 | 26 | 10 | 7 | 4.5854 | 0 | 42.7453 | 0 | 9.9655 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.5573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4105.2 | 0 | 4105.2 | 134292 | -42575.2 | 38 | 39 | 134292 | -1042575.2
3 | 26 | 11 | 7 | 4.4159 | 0 | 42.7453 | 0 | 9.8675 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 80.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4106.64 | 0 | 4106.64 | 134571 | -37559.6 | 38 | 38 | 134571 | -1037559.6
3 | 26 | 12 | 7 | 4.6549 | 0 | 42.7453 | 0 | 9.9664 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.18 | 0 | 4108.18 | 134284 | -41853.1 | 38 | 38 | 134284 | -1041853.1
3 | 26 | 13 | 7 | 4.3628 | 0 | 42.7453 | 0 | 9.9864 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.3557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4109.4 | 0 | 4109.4 | 134084 | -37482.5 | 38 | 38 | 134084 | -1037482.5
3 | 26 | 14 | 7 | 4.4241 | 0 | 42.7453 | 0 | 9.9886 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4110.66 | 0 | 4110.66 | 134080 | -37633.1 | 38 | 38 | 134080 | -1037633.1
3 | 26 | 15 | 7 | 4.856 | 0 | 42.7453 | 0 | 10.1776 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 81.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4112.19 | 0 | 4112.19 | 133404 | -46356.2 | 38 | 38 | 133404 | -1046356.2
3 | 26 | 16 | 7 | 4.6549 | 0 | 42.7453 | 0 | 10.1388 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.36 | 0 | 4113.36 | 132598 | -46405.9 | 37 | 38 | 132598 | -1046405.9
3 | 26 | 17 | 7 | 4.966 | 0 | 42.7453 | 0 | 10.2845 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 2 | 83.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4114.76 | 0 | 4114.76 | 132263 | -54546 | 37 | 38 | 132263 | -1054546
3 | 26 | 18 | 7 | 5.8488 | 0 | 42.7453 | 0 | 10.4372 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.37 | 0 | 4116.37 | 131980 | -67622.4 | 38 | 38 | 131980 | -1067622.4
3 | 26 | 19 | 7 | 6.6167 | 0 | 42.7453 | 0 | 10.4464 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4117.73 | 0 | 4117.73 | 131137 | -78324.7 | 37 | 38 | 131137 | -1078324.7
3 | 26 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5475 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4119.3 | 0 | 4119.3 | 130820 | -87604.5 | 37 | 37 | 130820 | -1087604.5
3 | 26 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.7043 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4120.74 | 0 | 4120.74 | 130373 | -94280.7 | 37 | 37 | 130373 | -1094280.7
3 | 26 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.7899 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.19 | 0 | 4122.19 | 130027 | -99096.9 | 37 | 37 | 130027 | -1099096.9
3 | 26 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.747 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4123.66 | 0 | 4123.66 | 129644 | -104654 | 36 | 36 | 129644 | -1104654
3 | 26 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 10.723 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11079.8 | 0 | 11079.8 | 129732 | -104784 | 36 | 36 | 129732 | -1104784
3 | 27 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.7274 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11081.2 | 0 | 11081.2 | 130057 | -108310 | 36 | 36 | 130057 | -1108310
3 | 27 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.6907 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11081.8 | 0 | 11081.8 | 129461 | -112445 | 35 | 35 | 129461 | -1112445
3 | 27 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.6584 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11082.9 | 0 | 11082.9 | 129273 | -115256 | 35 | 35 | 129273 | -1115256
3 | 27 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.8774 | 0 | 5.8992 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12315.9 | 0 | 12315.9 | 132521 | -117797 | 35 | 35 | 132521 | -1117797
3 | 27 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 14.4026 | 0 | 5.9507 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30002.1 | 0 | 30002.1 | 180541 | -92894.5 | 35 | 35 | 180541 | -1092894.5
3 | 27 | 6 | 1 | 49.0171 | 0 | 140.608 | 39.9195 | 0 | 0 | 25.2416 | 19.0895 | 0 | 0 | 0 | 1.2 | 275.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89043.9 | 0 | 89043.9 | 313195 | -710803 | 35 | 35 | 313195 | -1710803
3 | 27 | 7 | 1 | 49.3416 | 0 | 168.222 | 35.6388 | 0 | 0 | 25.2578 | 19.0363 | 0 | 0 | 0 | 0 | 297.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108160 | 0 | 108160 | 382304 | -628808 | 36 | 36 | 382304 | -1628808
3 | 27 | 8 | 1 | 40.4906 | 0 | 173.795 | 0 | 27.3128 | 0 | 6.2672 | 19.0363 | 0 | 0 | 0 | 0 | 266.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149741 | 0 | 149741 | 414180 | -497567 | 37 | 38 | 414180 | -1497567
3 | 27 | 9 | 1 | 41.4795 | 0 | 172.186 | 0 | 27.7815 | 0 | 6.2798 | 19.0363 | 0 | 0 | 0 | 0 | 266.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176210 | 0 | 176210 | 422232 | -447423 | 38 | 39 | 422232 | -1447423
3 | 27 | 10 | 1 | 41.7968 | 0 | 163.102 | 0 | 28.444 | 0 | 6.2943 | 19.0363 | 0 | 0 | 0 | 0 | 258.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179983 | 0 | 179983 | 417905 | -411086 | 39 | 41 | 417905 | -1411086
3 | 27 | 11 | 1 | 41.0045 | 0 | 149.692 | 0 | 27.9528 | 0 | 6.2958 | 19.0363 | 0 | 0 | 0 | 0 | 243.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179981 | 0 | 179981 | 412880 | -369573 | 40 | 42 | 412880 | -1369573
3 | 27 | 12 | 1 | 39.829 | 0 | 150.207 | 0 | 26.697 | 0 | 6.3031 | 19.0363 | 0 | 0 | 0 | 0 | 242.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179978 | 0 | 179978 | 392719 | -328811 | 41 | 44 | 392719 | -1328811
3 | 27 | 13 | 1 | 41.2555 | 0 | 165.698 | 0 | 30.9488 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179974 | 0 | 179974 | 447308 | -265233 | 42 | 45 | 447308 | -1265233
3 | 27 | 14 | 1 | 40.7761 | 0 | 172.702 | 0 | 32.9068 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177645 | 0 | 177645 | 462495 | -244385 | 43 | 47 | 462495 | -1244385
3 | 27 | 15 | 1 | 40.5512 | 0 | 173.986 | 0 | 32.5644 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161482 | 0 | 161482 | 452144 | -209257 | 43 | 48 | 452144 | -1209257
3 | 27 | 16 | 1 | 41.3088 | 0 | 169.782 | 0 | 32.8985 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131785 | 0 | 131785 | 460342 | -251072 | 43 | 47 | 460342 | -1251072
3 | 27 | 17 | 1 | 36.8791 | 0 | 152.497 | 0 | 29.9324 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 246.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98791.1 | 0 | 98791.1 | 426934 | -274566 | 43 | 47 | 426934 | -1274566
3 | 27 | 18 | 1 | 28.7753 | 0 | 93.4203 | 0 | 25.33 | 0 | 6.3153 | 19.0363 | 0 | 0 | 0 | 5.6 | 178.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61109.3 | 0 | 61109.3 | 351789 | -344634 | 42 | 46 | 351789 | -1344634
3 | 27 | 19 | 1 | 24.097 | 0 | 62.7906 | 0 | 8.8994 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 7.2 | 117.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43679.8 | 0 | 43679.8 | 179005 | 0 | 41 | 44 | 179005 | -1000000
3 | 27 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 11.552 | 0 | 5.9101 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38751.9 | 0 | 38751.9 | 159883 | -9439.55 | 40 | 41 | 159883 | -1009439.55
3 | 27 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.2888 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23729.7 | 0 | 23729.7 | 146402 | 0 | 38 | 39 | 146402 | -1000000
3 | 27 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.5962 | 0 | 5.9144 | 15.0234 | 0 | 0 | 0 | 6.4 | 95.4645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12704.1 | 0 | 12704.1 | 151564 | -20239.9 | 38 | 39 | 151564 | -1020239.9
3 | 27 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.6703 | 0 | 5.8967 | 17.5105 | 0 | 0 | 0 | 5.6 | 89.5354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11037.4 | 0 | 11037.4 | 155035 | -13892.9 | 38 | 38 | 155035 | -1013892.9
3 | 27 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 11.4131 | 0 | 5.9072 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040.3 | 0 | 11040.3 | 154937 | -23197.2 | 38 | 38 | 154937 | -1023197.2
3 | 28 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.1815 | 0 | 5.9 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11043.2 | 0 | 11043.2 | 148862 | -23383.4 | 37 | 38 | 148862 | -1023383.4
3 | 28 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.7936 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11045.8 | 0 | 11045.8 | 147876 | -26128 | 37 | 38 | 147876 | -1026128
3 | 28 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.6402 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047.7 | 0 | 11047.7 | 145776 | -28283.7 | 38 | 38 | 145776 | -1028283.7
3 | 28 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 9.7454 | 0 | 5.8986 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12281.3 | 0 | 12281.3 | 147735 | -30822.1 | 37 | 38 | 147735 | -1030822.1
3 | 28 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.6576 | 0 | 5.9402 | 17.5105 | 0 | 0 | 0 | 3.6 | 133.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29967.9 | 0 | 29967.9 | 195947 | -23468.4 | 37 | 38 | 195947 | -1023468.4
3 | 28 | 6 | 2 | 49.0171 | 0 | 140.608 | 25.6536 | 0 | 0 | 25.2827 | 19.0363 | 0 | 0 | 0 | 1.2 | 260.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89009.9 | 0 | 89009.9 | 322464 | -453286 | 38 | 38 | 322464 | -1453286
3 | 28 | 7 | 2 | 49.2477 | 0 | 168.222 | 0 | 29.2337 | 0 | 6.2879 | 19.0363 | 0 | 0 | 0 | 0 | 272.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108126 | 0 | 108126 | 417396 | -464018 | 38 | 39 | 417396 | -1464018
3 | 28 | 8 | 2 | 42.8012 | 0 | 173.795 | 0 | 30.1757 | 0 | 6.297 | 19.0363 | 0 | 0 | 0 | 0 | 272.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149718 | 0 | 149718 | 448561 | -376232 | 39 | 41 | 448561 | -1376232
3 | 28 | 9 | 2 | 41.5396 | 0 | 172.186 | 0 | 30.7993 | 0 | 6.3068 | 19.0363 | 0 | 0 | 0 | 0 | 269.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176186 | 0 | 176186 | 452951 | -351686 | 40 | 42 | 452951 | -1351686
3 | 28 | 10 | 2 | 41.2113 | 0 | 163.102 | 0 | 30.6 | 0 | 6.3242 | 19.0363 | 0 | 0 | 0 | 0 | 260.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179959 | 0 | 179959 | 441152 | -300938 | 42 | 45 | 441152 | -1300938
3 | 28 | 11 | 2 | 40.7155 | 0 | 149.692 | 0 | 30.9774 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179957 | 0 | 179957 | 426199 | -225203 | 44 | 49 | 426199 | -1225203
3 | 28 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 29.4088 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179955 | 0 | 179955 | 394730 | -157119 | 46 | 52 | 394730 | -1157119
3 | 28 | 13 | 2 | 41.2614 | 0 | 165.698 | 0 | 33.2328 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179952 | 0 | 179952 | 436486 | -125610 | 46 | 53 | 436486 | -1125610
3 | 28 | 14 | 2 | 40.6614 | 0 | 172.702 | 0 | 32.6732 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177623 | 0 | 177623 | 462146 | -100837 | 47 | 54 | 462146 | -1100837
3 | 28 | 15 | 2 | 40.5651 | 0 | 173.986 | 0 | 31.6966 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161461 | 0 | 161461 | 465139 | -76368.4 | 47 | 55 | 465139 | -1076368.4
3 | 28 | 16 | 2 | 40.3258 | 0 | 169.782 | 0 | 29.7557 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131764 | 0 | 131764 | 461171 | -85872.9 | 46 | 53 | 461171 | -1085872.9
3 | 28 | 17 | 2 | 35.5142 | 0 | 152.497 | 0 | 27.4079 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 242.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98770.7 | 0 | 98770.7 | 422771 | -110109 | 45 | 52 | 422771 | -1110109
3 | 28 | 18 | 2 | 25.4155 | 0 | 93.4203 | 0 | 24.4706 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61089.7 | 0 | 61089.7 | 324086 | -183557 | 44 | 50 | 324086 | -1183557
3 | 28 | 19 | 2 | 23.8473 | 0 | 62.7906 | 0 | 9.11 | 0 | 5.4894 | 8.818 | 0 | 0 | 0 | 7.2 | 117.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43661.2 | 0 | 43661.2 | 184164 | 0 | 42 | 46 | 184164 | -1000000
3 | 28 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.1255 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 7.2 | 102.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38733.9 | 0 | 38733.9 | 164615 | 0 | 40 | 43 | 164615 | -1000000
3 | 28 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 10.6357 | 0 | 5.9022 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23709.1 | 0 | 23709.1 | 151075 | -8457.44 | 37 | 39 | 151075 | -1008457.44
3 | 28 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 6.9971 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12682.8 | 0 | 12682.8 | 140059 | 0 | 37 | 38 | 140059 | -1000000
3 | 28 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.4112 | 0 | 5.9018 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.6 | 0 | 11015.6 | 135184 | -18383.7 | 36 | 37 | 135184 | -1018383.7
3 | 28 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 8.0123 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11018.6 | 0 | 11018.6 | 162926 | -11305.8 | 35 | 36 | 162926 | -1011305.8
3 | 29 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.8183 | 0 | 5.9114 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11021.2 | 0 | 11021.2 | 159052 | -22328.9 | 35 | 36 | 159052 | -1022328.9
3 | 29 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9863 | 0 | 5.905 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11024.1 | 0 | 11024.1 | 155113 | -22934 | 35 | 37 | 155113 | -1022934
3 | 29 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5609 | 0 | 5.9075 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11026.8 | 0 | 11026.8 | 153226 | -28700 | 36 | 37 | 153226 | -1028700
3 | 29 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.5712 | 0 | 5.9079 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.4341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12261.2 | 0 | 12261.2 | 154219 | -31235.4 | 35 | 36 | 154219 | -1031235.4
3 | 29 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 15.3387 | 0 | 5.9865 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29948.8 | 0 | 29948.8 | 205150 | -30936.8 | 34 | 35 | 205150 | -1030936.8
3 | 29 | 6 | 3 | 48.9927 | 0 | 140.608 | 24.5818 | 0 | 0 | 25.278 | 19.0363 | 0 | 0 | 0 | 1.2 | 259.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88991.7 | 0 | 88991.7 | 324926 | -488488 | 34 | 34 | 324926 | -1488488
3 | 29 | 7 | 3 | 43.9901 | 0 | 168.222 | 0 | 27.8758 | 0 | 6.2927 | 19.0363 | 0 | 0 | 0 | 0 | 265.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108109 | 0 | 108109 | 399272 | -439552 | 37 | 38 | 399272 | -1439552
3 | 29 | 8 | 3 | 39.9557 | 0 | 173.795 | 0 | 30.3643 | 0 | 6.3124 | 19.0363 | 0 | 0 | 0 | 0 | 269.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149702 | 0 | 149702 | 450411 | -308407 | 39 | 43 | 450411 | -1308407
3 | 29 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 32.8037 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176173 | 0 | 176173 | 463717 | -237985 | 42 | 47 | 463717 | -1237985
3 | 29 | 10 | 3 | 41.1527 | 0 | 163.102 | 0 | 31.8604 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179947 | 0 | 179947 | 434705 | -181618 | 44 | 50 | 434705 | -1181618
3 | 29 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 31.8661 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179944 | 0 | 179944 | 418986 | -143905 | 46 | 53 | 418986 | -1143905
3 | 29 | 12 | 3 | 39.7715 | 0 | 150.207 | 0 | 31.5625 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179942 | 0 | 179942 | 404452 | -97728.3 | 49 | 56 | 404452 | -1097728.3
3 | 29 | 13 | 3 | 41.2662 | 0 | 165.698 | 0 | 31.7078 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179939 | 0 | 179939 | 448650 | -75805.7 | 50 | 57 | 448650 | -1075805.7
3 | 29 | 14 | 3 | 40.6643 | 0 | 172.702 | 0 | 31.3677 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177612 | 0 | 177612 | 481383 | -57891.1 | 51 | 58 | 481383 | -1057891.1
3 | 29 | 15 | 3 | 40.5565 | 0 | 173.986 | 0 | 31.2116 | 0 | 6.332 | 19.0712 | 0 | 0 | 0 | 0 | 271.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161450 | 0 | 161450 | 496865 | -33488.8 | 52 | 59 | 496865 | -1033488.8
3 | 29 | 16 | 3 | 40.3194 | 0 | 169.782 | 0 | 30.946 | 0 | 6.332 | 19.1829 | 0 | 0 | 0 | 0 | 266.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131755 | 0 | 131755 | 490257 | -26394.5 | 52 | 59 | 490257 | -1026394.5
3 | 29 | 17 | 3 | 35.525 | 0 | 152.497 | 0 | 28.4564 | 0 | 6.332 | 19.0527 | 0 | 0 | 0 | 2 | 243.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98761.4 | 0 | 98761.4 | 448013 | -30914.7 | 53 | 59 | 448013 | -1030914.7
3 | 29 | 18 | 3 | 25.3514 | 0 | 93.4203 | 0 | 21.8398 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 171.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61080.8 | 0 | 61080.8 | 338228 | -65188.5 | 53 | 59 | 338228 | -1065188.5
3 | 29 | 19 | 3 | 23.8116 | 0 | 62.7906 | 0 | 9.2348 | 0 | 5.4912 | 8.818 | 0 | 0 | 0 | 7.2 | 117.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43652.6 | 0 | 43652.6 | 186701 | 0 | 53 | 59 | 186701 | -1000000
3 | 29 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.2386 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 7.2 | 103.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38725.5 | 0 | 38725.5 | 167091 | 0 | 54 | 59 | 167091 | -1000000
3 | 29 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.6239 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23698.6 | 0 | 23698.6 | 153739 | 0 | 55 | 59 | 153739 | -1000000
3 | 29 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.1135 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12670.8 | 0 | 12670.8 | 142604 | 0 | 55 | 59 | 142604 | -1000000
3 | 29 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8784 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11002.3 | 0 | 11002.3 | 137562 | 0 | 54 | 60 | 137562 | -1000000
3 | 29 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8143 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11003.6 | 0 | 11003.6 | 136219 | 0 | 54 | 60 | 136219 | -1000000
3 | 30 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7739 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11004.7 | 0 | 11004.7 | 135344 | 0 | 54 | 60 | 135344 | -1000000
3 | 30 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7389 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11005.5 | 0 | 11005.5 | 134578 | 0 | 54 | 60 | 134578 | -1000000
3 | 30 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7067 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11006.1 | 0 | 11006.1 | 133876 | 0 | 54 | 60 | 133876 | -1000000
3 | 30 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.8541 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12238.6 | 0 | 12238.6 | 137167 | 0 | 55 | 60 | 137167 | -1000000
3 | 30 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 9.2651 | 0 | 5.4925 | 8.818 | 0 | 0 | 0 | 3.6 | 121.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29924.3 | 0 | 29924.3 | 183990 | 0 | 55 | 61 | 183990 | -1000000
3 | 30 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 30.1825 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 246.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88965.4 | 0 | 88965.4 | 368798 | -54546 | 55 | 61 | 368798 | -1054546
3 | 30 | 7 | 4 | 48.4867 | 0 | 168.222 | 0 | 36.9491 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 279.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108081 | 0 | 108081 | 507815 | -33460.4 | 56 | 62 | 507815 | -1033460.4
3 | 30 | 8 | 4 | 39.7966 | 0 | 173.795 | 0 | 37.6885 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 276.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149678 | 0 | 149678 | 552960 | -22582.7 | 56 | 64 | 552960 | -1022582.7
3 | 30 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 40.5141 | 0 | 6.332 | 19.0683 | 0 | 0 | 0 | 0 | 278.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176152 | 0 | 176152 | 601598 | -18677.2 | 57 | 65 | 601598 | -1018677.2
3 | 30 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 50.0675 | 0 | 6.332 | 19.6249 | 0 | 0 | 0 | 0 | 280.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179927 | 0 | 179927 | 698245 | -13095.8 | 59 | 69 | 698245 | -1013095.8
3 | 30 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 52.1611 | 0 | 6.332 | 19.71 | 0 | 0 | 0 | 0 | 268.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179926 | 0 | 179926 | 707185 | -9970.12 | 61 | 72 | 707185 | -1009970.12
3 | 30 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 67.4464 | 0 | 6.332 | 19.8295 | 0 | 0 | 0 | 0 | 283.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179925 | 0 | 179925 | 914444 | -11400.4 | 63 | 76 | 914444 | -1011400.4
3 | 30 | 13 | 4 | 41.2815 | 0 | 165.698 | 0 | 50.3052 | 0 | 9.9056 | 20.929 | 0 | 0 | 0 | 0 | 288.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179924 | 0 | 179924 | 975912 | -8573.67 | 63 | 77 | 975912 | -1008573.67
3 | 30 | 14 | 4 | 40.6583 | 0 | 172.702 | 0 | 55.128 | 0 | 21.9426 | 21.1953 | 0 | 0 | 0 | 0 | 311.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177599 | 0 | 177599 | 1067780 | -9890.14 | 64 | 78 | 1067780 | -1009890.14
3 | 30 | 15 | 4 | 40.5664 | 0 | 173.986 | 0 | 58.5138 | 0 | 6.332 | 21.167 | 0 | 0 | 0 | 0 | 300.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161439 | 0 | 161439 | 1131120 | -10639.4 | 64 | 79 | 1131120 | -1010639.4
3 | 30 | 16 | 4 | 40.3171 | 0 | 169.782 | 0 | 54.0542 | 0 | 6.332 | 21.4204 | 0 | 0 | 0 | 0 | 291.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131744 | 0 | 131744 | 1044500 | -7435.84 | 63 | 77 | 1044500 | -1007435.84
3 | 30 | 17 | 4 | 35.5122 | 0 | 152.497 | 0 | 47.0608 | 0 | 6.332 | 21.323 | 0 | 0 | 0 | 2 | 264.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98751.6 | 0 | 98751.6 | 910884 | -4987.52 | 62 | 76 | 910884 | -1004987.52
3 | 30 | 18 | 4 | 25.6114 | 0 | 93.4203 | 0 | 29.8593 | 0 | 6.332 | 19.3889 | 0 | 0 | 0 | 5.6 | 180.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61070.9 | 0 | 61070.9 | 585311 | -4431.09 | 61 | 74 | 585311 | -1004431.09
3 | 30 | 19 | 4 | 23.9277 | 0 | 62.7906 | 0 | 10.0463 | 0 | 5.5258 | 8.818 | 0 | 0 | 0 | 7.2 | 118.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43642.1 | 0 | 43642.1 | 190433 | 0 | 61 | 73 | 190433 | -1000000
3 | 30 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.6886 | 0 | 5.4919 | 8.818 | 0 | 0 | 0 | 7.2 | 103.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38714.7 | 0 | 38714.7 | 170124 | 0 | 60 | 72 | 170124 | -1000000
3 | 30 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.9874 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 7.2 | 92.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23682.6 | 0 | 23682.6 | 156872 | 0 | 60 | 71 | 156872 | -1000000
3 | 30 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 6.1669 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 6.4 | 82.4005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12652.9 | 0 | 12652.9 | 145622 | 0 | 58 | 66 | 145622 | -1000000
3 | 30 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 5.4684 | 0 | 5.4987 | 8.818 | 0 | 0 | 0 | 5.6 | 78.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10982.6 | 0 | 10982.6 | 140383 | 0 | 55 | 60 | 140383 | -1000000
3 | 30 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9245 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10982.7 | 0 | 10982.7 | 138624 | 0 | 52 | 55 | 138624 | -1000000
3 | 31 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8798 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10982.8 | 0 | 10982.8 | 137659 | 0 | 51 | 54 | 137659 | -1000000
3 | 31 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8418 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10983.4 | 0 | 10983.4 | 136830 | 0 | 51 | 54 | 136830 | -1000000
3 | 31 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8033 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10984.2 | 0 | 10984.2 | 135987 | 0 | 51 | 53 | 135987 | -1000000
3 | 31 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9249 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12217.2 | 0 | 12217.2 | 138708 | 0 | 50 | 51 | 138708 | -1000000
3 | 31 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 9.0097 | 0 | 5.488 | 8.818 | 0 | 0 | 0 | 3.6 | 121.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29903.3 | 0 | 29903.3 | 185071 | 0 | 49 | 50 | 185071 | -1000000
3 | 31 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 24.7526 | 0 | 6.332 | 19.0977 | 0 | 0 | 0 | 1.2 | 241.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88944.8 | 0 | 88944.8 | 337246 | -42099.4 | 47 | 48 | 337246 | -1042099.4
3 | 31 | 7 | 5 | 46.0338 | 0 | 168.222 | 0 | 30.1256 | 0 | 6.332 | 19.0369 | 0 | 0 | 0 | 0 | 269.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108061 | 0 | 108061 | 468118 | -66989.2 | 49 | 50 | 468118 | -1066989.2
3 | 31 | 8 | 5 | 40.1303 | 0 | 173.795 | 0 | 31.4015 | 0 | 6.332 | 19.0562 | 0 | 0 | 0 | 0 | 270.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149665 | 0 | 149665 | 515263 | -75005.8 | 50 | 51 | 515263 | -1075005.8
3 | 31 | 9 | 5 | 40.8989 | 0 | 172.186 | 0 | 33.017 | 0 | 6.332 | 19.0798 | 0 | 0 | 0 | 0 | 271.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176140 | 0 | 176140 | 532596 | -58239.9 | 51 | 53 | 532596 | -1058239.9
3 | 31 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 33.9181 | 0 | 6.332 | 19.3175 | 0 | 0 | 0 | 0 | 263.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179916 | 0 | 179916 | 533107 | -31770.6 | 52 | 56 | 533107 | -1031770.6
3 | 31 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 33.3087 | 0 | 6.332 | 19.778 | 0 | 0 | 0 | 0 | 249.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179916 | 0 | 179916 | 513789 | -11629.5 | 52 | 59 | 513789 | -1011629.5
3 | 31 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 39.4756 | 0 | 6.332 | 20.0471 | 0 | 0 | 0 | 0 | 255.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179916 | 0 | 179916 | 581805 | -11305.2 | 52 | 62 | 581805 | -1011305.2
3 | 31 | 13 | 5 | 41.272 | 0 | 165.698 | 0 | 42.6024 | 0 | 6.332 | 20.8926 | 0 | 0 | 0 | 0 | 276.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179916 | 0 | 179916 | 644305 | -10226.6 | 52 | 62 | 644305 | -1010226.6
3 | 31 | 14 | 5 | 40.6438 | 0 | 172.702 | 0 | 37.7751 | 0 | 25.335 | 20.9202 | 0 | 0 | 0 | 0 | 297.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177590 | 0 | 177590 | 700340 | -9747.49 | 52 | 63 | 700340 | -1009747.49
3 | 31 | 15 | 5 | 40.5942 | 0 | 173.986 | 0 | 35.6857 | 0 | 25.335 | 20.7567 | 0 | 0 | 0 | 0 | 296.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161430 | 0 | 161430 | 666743 | -9256.44 | 51 | 63 | 666743 | -1009256.44
3 | 31 | 16 | 5 | 41.924 | 0 | 169.782 | 0 | 36.815 | 0 | 6.332 | 20.2787 | 0 | 0 | 0 | 0 | 275.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131736 | 0 | 131736 | 626875 | -9333.61 | 51 | 62 | 626875 | -1009333.61
3 | 31 | 17 | 5 | 35.5181 | 0 | 152.497 | 0 | 35.0567 | 0 | 6.332 | 20.1623 | 0 | 0 | 0 | 2 | 251.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98742.9 | 0 | 98742.9 | 554864 | -8578.21 | 50 | 62 | 554864 | -1008578.21
3 | 31 | 18 | 5 | 26.8496 | 0 | 93.4203 | 0 | 24.6718 | 0 | 6.332 | 19.1162 | 0 | 0 | 0 | 5.6 | 175.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61062.9 | 0 | 61062.9 | 375282 | -8336.44 | 49 | 61 | 375282 | -1008336.44
3 | 31 | 19 | 5 | 23.7409 | 0 | 62.7906 | 0 | 9.1346 | 0 | 5.4897 | 8.818 | 0 | 0 | 0 | 7.2 | 117.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43635.5 | 0 | 43635.5 | 189552 | 0 | 46 | 54 | 189552 | -1000000
3 | 31 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.3483 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 7.2 | 103.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38709 | 0 | 38709 | 169484 | 0 | 43 | 48 | 169484 | -1000000
3 | 31 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.7218 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23677.5 | 0 | 23677.5 | 155879 | 0 | 41 | 44 | 155879 | -1000000
3 | 31 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.203 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12649.3 | 0 | 12649.3 | 144562 | 0 | 40 | 43 | 144562 | -1000000
3 | 31 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 6.971 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10980.4 | 0 | 10980.4 | 139589 | 0 | 39 | 42 | 139589 | -1000000
3 | 31 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 9.3525 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10982.2 | 0 | 10982.2 | 137727 | -6996.67 | 39 | 41 | 137727 | -1006996.67
4 | 1 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8258 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10777.6 | 0 | 10777.6 | 136472 | 0 | 38 | 40 | 136472 | -1000000
4 | 1 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.3239 | 0 | 5.8982 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10780 | 0 | 10780 | 135446 | -12375.3 | 37 | 39 | 135446 | -1012375.3
4 | 1 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.737 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10782.2 | 0 | 10782.2 | 134536 | 0 | 37 | 38 | 134536 | -1000000
4 | 1 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.9119 | 0 | 5.9193 | 14.8767 | 0 | 0 | 0 | 4.8 | 87.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10784.2 | 0 | 10784.2 | 156850 | -18263.3 | 36 | 37 | 156850 | -1018263.3
4 | 1 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.58 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 3.6 | 81.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10786.4 | 0 | 10786.4 | 152936 | -6616.22 | 35 | 37 | 152936 | -1006616.22
4 | 1 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 8.2395 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 1.2 | 81.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10788.4 | 0 | 10788.4 | 167682 | -14685.9 | 34 | 35 | 167682 | -1014685.9
4 | 1 | 7 | 6 | 5.7481 | 0 | 42.7453 | 19.3752 | 0 | 0 | 6.117 | 18.8896 | 0 | 0 | 0 | 0 | 92.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10790.7 | 0 | 10790.7 | 133119 | -379560 | 32 | 34 | 133119 | -1379560
4 | 1 | 8 | 6 | 5.4994 | 0 | 42.7453 | 21.6567 | 0 | 0 | 6.2674 | 18.8896 | 0 | 0 | 0 | 0 | 95.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10793.2 | 0 | 10793.2 | 146068 | -386211 | 33 | 35 | 146068 | -1386211
4 | 1 | 9 | 6 | 6.1306 | 0 | 42.7453 | 18.7053 | 0 | 0 | 6.1167 | 18.8896 | 0 | 0 | 0 | 0 | 92.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.3 | 0 | 10796.3 | 131353 | -345346 | 32 | 34 | 131353 | -1345346
4 | 1 | 10 | 6 | 6.3422 | 0 | 42.7453 | 18.4613 | 0 | 0 | 6.1084 | 18.8896 | 0 | 0 | 0 | 0 | 92.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.6 | 0 | 10796.6 | 137892 | -344936 | 33 | 35 | 137892 | -1344936
4 | 1 | 11 | 6 | 6.118 | 0 | 42.7453 | 17.9801 | 0 | 0 | 6.0869 | 18.8896 | 0 | 0 | 0 | 0 | 91.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10798.2 | 0 | 10798.2 | 129609 | -339116 | 34 | 34 | 129609 | -1339116
4 | 1 | 12 | 6 | 6.118 | 0 | 42.7453 | 17.8863 | 0 | 0 | 6.0829 | 18.8896 | 0 | 0 | 0 | 0 | 91.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10799.4 | 0 | 10799.4 | 128670 | -339058 | 34 | 34 | 128670 | -1339058
4 | 1 | 13 | 6 | 6.0427 | 0 | 42.7453 | 17.6508 | 0 | 0 | 6.0718 | 18.8896 | 0 | 0 | 0 | 0 | 91.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10800.6 | 0 | 10800.6 | 133794 | -335770 | 35 | 35 | 133794 | -1335770
4 | 1 | 14 | 6 | 6.1557 | 0 | 42.7453 | 0 | 9.0641 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 76.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.8 | 0 | 10801.8 | 128799 | -8503.29 | 35 | 35 | 128799 | -1008503.29
4 | 1 | 15 | 6 | 6.2916 | 0 | 42.7453 | 0 | 6.8342 | 0 | 6.8646 | 12.8287 | 0 | 0 | 0 | 0 | 75.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.1 | 0 | 10803.1 | 125754 | -9105.97 | 36 | 36 | 125754 | -1009105.97
4 | 1 | 16 | 6 | 5.9424 | 0 | 42.7453 | 0 | 8.8198 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 0 | 76.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.9 | 0 | 10803.9 | 126221 | -13459.8 | 36 | 36 | 126221 | -1013459.8
4 | 1 | 17 | 6 | 6.4512 | 0 | 42.7453 | 0 | 9.8768 | 0 | 5.8985 | 14.8767 | 0 | 0 | 0 | 2 | 81.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10806.3 | 0 | 10806.3 | 145119 | -14474.7 | 36 | 36 | 145119 | -1014474.7
4 | 1 | 18 | 6 | 7.4052 | 0 | 42.7453 | 0 | 11.429 | 0 | 5.9092 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.4525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10808 | 0 | 10808 | 160320 | -18871 | 36 | 36 | 160320 | -1018871
4 | 1 | 19 | 6 | 8.6843 | 0 | 42.7453 | 0 | 10.326 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10809.8 | 0 | 10809.8 | 152451 | -16431.5 | 36 | 36 | 152451 | -1016431.5
4 | 1 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2932 | 0 | 5.9055 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10812 | 0 | 10812 | 151773 | -24531.6 | 36 | 36 | 151773 | -1024531.6
4 | 1 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0606 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10814.4 | 0 | 10814.4 | 149581 | -24887.3 | 34 | 34 | 149581 | -1024887.3
4 | 1 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.0437 | 0 | 5.8992 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10816.8 | 0 | 10816.8 | 146685 | -22827.9 | 33 | 33 | 146685 | -1022827.9
4 | 1 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.9345 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10819.2 | 0 | 10819.2 | 146311 | -24145 | 34 | 34 | 146311 | -1024145
4 | 1 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 9.542 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.4541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4010.88 | 0 | 4010.88 | 143793 | -25347.6 | 34 | 34 | 143793 | -1025347.6
4 | 2 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.7357 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4012.79 | 0 | 4012.79 | 142673 | -35495.9 | 31 | 31 | 142673 | -1035495.9
4 | 2 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.589 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.79 | 0 | 4014.79 | 141029 | -41505.5 | 31 | 31 | 141029 | -1041505.5
4 | 2 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.2929 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.69 | 0 | 4016.69 | 140114 | -48179 | 32 | 32 | 140114 | -1048179
4 | 2 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.4117 | 0 | 5.9029 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.62 | 0 | 4018.62 | 140272 | -60919.4 | 32 | 32 | 140272 | -1060919.4
4 | 2 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.5317 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 3.6 | 86.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.47 | 0 | 4020.47 | 142315 | -66611.9 | 32 | 32 | 142315 | -1066611.9
4 | 2 | 6 | 7 | 5.0837 | 0 | 42.7453 | 0 | 9.8562 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.96 | 0 | 4022.96 | 137899 | -59872.8 | 32 | 32 | 137899 | -1059872.8
4 | 2 | 7 | 7 | 3.9761 | 0 | 42.7453 | 0 | 9.6803 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 79.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4025.17 | 0 | 4025.17 | 138156 | -49666 | 35 | 35 | 138156 | -1049666
4 | 2 | 8 | 7 | 3.8179 | 0 | 42.7453 | 0 | 11.7138 | 0 | 5.9055 | 17.3638 | 0 | 0 | 0 | 0 | 81.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.73 | 0 | 4026.73 | 144015 | -47200.7 | 39 | 40 | 144015 | -1047200.7
4 | 2 | 9 | 7 | 4.1462 | 0 | 42.7453 | 0 | 10.392 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 0 | 80.5466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.29 | 0 | 4028.29 | 142095 | -30247.3 | 41 | 44 | 142095 | -1030247.3
4 | 2 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.0634 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 76.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.83 | 0 | 4029.83 | 131556 | -15303.9 | 42 | 46 | 131556 | -1015303.9
4 | 2 | 11 | 7 | 4.4111 | 0 | 42.7453 | 0 | 8.8234 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 0 | 76.7532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.07 | 0 | 4030.07 | 133206 | -12655.9 | 43 | 48 | 133206 | -1012655.9
4 | 2 | 12 | 7 | 4.3103 | 0 | 42.7453 | 0 | 8.7752 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 0 | 76.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.85 | 0 | 4029.85 | 132186 | -10062.6 | 46 | 52 | 132186 | -1010062.6
4 | 2 | 13 | 7 | 4.38 | 0 | 42.7453 | 0 | 8.7813 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 0 | 76.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.16 | 0 | 4029.16 | 132204 | -8846.85 | 46 | 52 | 132204 | -1008846.85
4 | 2 | 14 | 7 | 4.3821 | 0 | 42.7453 | 0 | 9.5651 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 0 | 79.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.9 | 0 | 4029.9 | 145318 | -12695.3 | 46 | 52 | 145318 | -1012695.3
4 | 2 | 15 | 7 | 4.151 | 0 | 42.7453 | 0 | 6.0762 | 0 | 5.9069 | 12.8287 | 0 | 0 | 0 | 0 | 71.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.95 | 0 | 4029.95 | 119661 | -5415.08 | 46 | 54 | 119661 | -1005415.08
4 | 2 | 16 | 7 | 4.7196 | 0 | 42.7453 | 0 | 8.8937 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 77.1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.78 | 0 | 4030.78 | 134076 | -5581.74 | 47 | 55 | 134076 | -1005581.74
4 | 2 | 17 | 7 | 5.0581 | 0 | 42.7453 | 0 | 9.5534 | 0 | 5.8979 | 13.3531 | 0 | 0 | 0 | 2 | 78.6077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.31 | 0 | 4031.31 | 145291 | -3770.68 | 46 | 53 | 145291 | -1003770.68
4 | 2 | 18 | 7 | 5.4562 | 0 | 42.7453 | 0 | 8.0843 | 0 | 5.8993 | 12.8287 | 0 | 0 | 0 | 5.6 | 80.6138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.25 | 0 | 4031.25 | 119780 | -10532.2 | 45 | 51 | 119780 | -1010532.2
4 | 2 | 19 | 7 | 6.5967 | 0 | 42.7453 | 0 | 9.6816 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.09 | 0 | 4032.09 | 147205 | -10237.6 | 45 | 51 | 147205 | -1010237.6
4 | 2 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5245 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.96 | 0 | 4032.96 | 144957 | -13299.6 | 43 | 47 | 144957 | -1013299.6
4 | 2 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.236 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.81 | 0 | 4033.81 | 140380 | -14080.3 | 42 | 47 | 140380 | -1014080.3
4 | 2 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.1509 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.12 | 0 | 4035.12 | 139617 | -20397.9 | 41 | 44 | 139617 | -1020397.9
4 | 2 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.2439 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.5133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.16 | 0 | 4036.16 | 141343 | -18802.6 | 43 | 48 | 141343 | -1018802.6
4 | 2 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.0922 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.3322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10847.9 | 0 | 10847.9 | 138828 | -16589.6 | 43 | 46 | 138828 | -1016589.6
4 | 3 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.0137 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10849.3 | 0 | 10849.3 | 137611 | -19880.1 | 41 | 43 | 137611 | -1019880.1
4 | 3 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3636 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10849.4 | 0 | 10849.4 | 141592 | -25454.8 | 40 | 42 | 141592 | -1025454.8
4 | 3 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 8.9381 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10850.1 | 0 | 10850.1 | 136522 | -24094.8 | 41 | 42 | 136522 | -1024094.8
4 | 3 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.1778 | 0 | 5.897 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12057.5 | 0 | 12057.5 | 140718 | -25843.4 | 41 | 43 | 140718 | -1025843.4
4 | 3 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.0098 | 0 | 5.9281 | 17.5105 | 0 | 0 | 0 | 3.6 | 133.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29376.2 | 0 | 29376.2 | 188278 | -21992.8 | 40 | 40 | 188278 | -1021992.8
4 | 3 | 6 | 1 | 49.0171 | 0 | 140.608 | 24.478 | 0 | 0 | 25.2806 | 19.0363 | 0 | 0 | 0 | 1.2 | 259.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87191.6 | 0 | 87191.6 | 315601 | -435000 | 41 | 41 | 315601 | -1435000
4 | 3 | 7 | 1 | 50.1971 | 0 | 168.222 | 0 | 28.2961 | 0 | 6.2869 | 19.0363 | 0 | 0 | 0 | 0 | 272.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105910 | 0 | 105910 | 407757 | -441473 | 40 | 40 | 407757 | -1441473
4 | 3 | 8 | 1 | 45.999 | 0 | 173.795 | 0 | 26.5835 | 0 | 6.293 | 19.0363 | 0 | 0 | 0 | 0 | 271.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146635 | 0 | 146635 | 410466 | -377259 | 38 | 38 | 410466 | -1377259
4 | 3 | 9 | 1 | 42.7645 | 0 | 172.186 | 0 | 27.1608 | 0 | 6.2996 | 19.0363 | 0 | 0 | 0 | 0 | 267.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172554 | 0 | 172554 | 415869 | -377367 | 38 | 38 | 415869 | -1377367
4 | 3 | 10 | 1 | 42.6816 | 0 | 163.102 | 0 | 26.2591 | 0 | 6.3031 | 19.0363 | 0 | 0 | 0 | 0 | 257.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176250 | 0 | 176250 | 394138 | -391038 | 37 | 37 | 394138 | -1391038
4 | 3 | 11 | 1 | 41.5844 | 0 | 149.692 | 0 | 25.749 | 0 | 6.3026 | 19.0363 | 0 | 0 | 0 | 0 | 242.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176248 | 0 | 176248 | 385960 | -371559 | 37 | 37 | 385960 | -1371559
4 | 3 | 12 | 1 | 39.9363 | 0 | 150.207 | 0 | 23.013 | 0 | 6.298 | 19.0363 | 0 | 0 | 0 | 0 | 238.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176246 | 0 | 176246 | 351028 | -352285 | 37 | 37 | 351028 | -1352285
4 | 3 | 13 | 1 | 42.24 | 0 | 165.698 | 0 | 25.2465 | 0 | 6.3059 | 19.0363 | 0 | 0 | 0 | 0 | 258.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176244 | 0 | 176244 | 392975 | -322632 | 37 | 37 | 392975 | -1322632
4 | 3 | 14 | 1 | 41.2563 | 0 | 172.702 | 0 | 27.0927 | 0 | 6.3166 | 19.0363 | 0 | 0 | 0 | 0 | 266.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173965 | 0 | 173965 | 417893 | -312917 | 37 | 37 | 417893 | -1312917
4 | 3 | 15 | 1 | 41.2996 | 0 | 173.986 | 0 | 27.5103 | 0 | 6.3231 | 19.0363 | 0 | 0 | 0 | 0 | 268.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158139 | 0 | 158139 | 422955 | -307815 | 37 | 38 | 422955 | -1307815
4 | 3 | 16 | 1 | 41.0393 | 0 | 169.782 | 0 | 27.1395 | 0 | 6.3211 | 19.0363 | 0 | 0 | 0 | 0 | 263.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129060 | 0 | 129060 | 417400 | -314992 | 37 | 38 | 417400 | -1314992
4 | 3 | 17 | 1 | 36.3559 | 0 | 152.497 | 0 | 25.0357 | 0 | 6.3073 | 19.0363 | 0 | 0 | 0 | 2 | 241.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96752.1 | 0 | 96752.1 | 383609 | -352883 | 37 | 37 | 383609 | -1352883
4 | 3 | 18 | 1 | 29.8553 | 0 | 93.4203 | 23.2478 | 0 | 0 | 25.3036 | 19.0363 | 0 | 0 | 0 | 5.6 | 196.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59853.8 | 0 | 59853.8 | 312548 | -408946 | 36 | 37 | 312548 | -1408946
4 | 3 | 19 | 1 | 23.9486 | 0 | 62.7906 | 0 | 8.8718 | 0 | 5.4863 | 12.9754 | 0 | 0 | 0 | 7.2 | 121.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42787 | 0 | 42787 | 179056 | 0 | 36 | 36 | 179056 | -1000000
4 | 3 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 10.4482 | 0 | 5.904 | 12.9754 | 0 | 0 | 0 | 7.2 | 109.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37961.5 | 0 | 37961.5 | 159834 | -10907.2 | 35 | 35 | 159834 | -1010907.2
4 | 3 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 10.6714 | 0 | 5.9013 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23250.1 | 0 | 23250.1 | 146646 | -15793.8 | 35 | 35 | 146646 | -1015793.8
4 | 3 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.8429 | 0 | 5.9127 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12454.1 | 0 | 12454.1 | 162046 | -25320.1 | 35 | 35 | 162046 | -1025320.1
4 | 3 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.6088 | 0 | 5.908 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10822.1 | 0 | 10822.1 | 153548 | -31131.9 | 35 | 35 | 153548 | -1031131.9
4 | 3 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 11.8265 | 0 | 5.9082 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10825.7 | 0 | 10825.7 | 150348 | -37803.8 | 35 | 35 | 150348 | -1037803.8
4 | 4 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.832 | 0 | 5.9074 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10828.9 | 0 | 10828.9 | 147873 | -47798.8 | 33 | 33 | 147873 | -1047798.8
4 | 4 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.7809 | 0 | 5.9065 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10831.7 | 0 | 10831.7 | 146003 | -57883.9 | 32 | 32 | 146003 | -1057883.9
4 | 4 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.769 | 0 | 5.906 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10834.2 | 0 | 10834.2 | 144509 | -72329.3 | 31 | 31 | 144509 | -1072329.3
4 | 4 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.875 | 0 | 5.9073 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12043 | 0 | 12043 | 146755 | -78321.9 | 32 | 32 | 146755 | -1078321.9
4 | 4 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 15.6732 | 0 | 5.9871 | 17.5105 | 0 | 0 | 0 | 3.6 | 137.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29363.3 | 0 | 29363.3 | 199397 | -68809.4 | 32 | 32 | 199397 | -1068809.4
4 | 4 | 6 | 2 | 48.843 | 0 | 140.608 | 32.6715 | 0 | 0 | 25.2507 | 19.0363 | 0 | 0 | 0 | 1.2 | 267.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87180.1 | 0 | 87180.1 | 321770 | -613072 | 32 | 32 | 321770 | -1613072
4 | 4 | 7 | 2 | 46.1317 | 0 | 168.222 | 32.2057 | 0 | 0 | 25.2668 | 19.0363 | 0 | 0 | 0 | 0 | 290.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105900 | 0 | 105900 | 383642 | -582865 | 32 | 32 | 383642 | -1582865
4 | 4 | 8 | 2 | 40.3376 | 0 | 173.795 | 0 | 25.5717 | 0 | 6.2687 | 19.0363 | 0 | 0 | 0 | 0 | 265.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146627 | 0 | 146627 | 402299 | -486819 | 31 | 32 | 402299 | -1486819
4 | 4 | 9 | 2 | 41.4376 | 0 | 172.186 | 0 | 25.6863 | 0 | 6.2792 | 19.0363 | 0 | 0 | 0 | 0 | 264.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172548 | 0 | 172548 | 400359 | -463147 | 31 | 32 | 400359 | -1463147
4 | 4 | 10 | 2 | 41.6989 | 0 | 163.102 | 0 | 26.8098 | 0 | 6.2865 | 19.0363 | 0 | 0 | 0 | 0 | 256.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176245 | 0 | 176245 | 394399 | -470030 | 32 | 32 | 394399 | -1470030
4 | 4 | 11 | 2 | 40.9614 | 0 | 149.692 | 0 | 25.6419 | 0 | 6.2939 | 19.0363 | 0 | 0 | 0 | 0 | 241.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176244 | 0 | 176244 | 378471 | -401734 | 34 | 34 | 378471 | -1401734
4 | 4 | 12 | 2 | 39.8034 | 0 | 150.207 | 0 | 23.5305 | 0 | 6.287 | 19.0363 | 0 | 0 | 0 | 0 | 238.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176243 | 0 | 176243 | 355134 | -393120 | 32 | 34 | 355134 | -1393120
4 | 4 | 13 | 2 | 41.5139 | 0 | 165.698 | 0 | 24.7154 | 0 | 6.3027 | 19.0363 | 0 | 0 | 0 | 0 | 257.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176241 | 0 | 176241 | 388982 | -323883 | 33 | 36 | 388982 | -1323883
4 | 4 | 14 | 2 | 40.8776 | 0 | 172.702 | 0 | 27.3868 | 0 | 25.3211 | 19.0363 | 0 | 0 | 0 | 0 | 285.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173961 | 0 | 173961 | 422456 | -300668 | 34 | 38 | 422456 | -1300668
4 | 4 | 15 | 2 | 40.9155 | 0 | 173.986 | 0 | 27.5065 | 0 | 25.3274 | 19.0363 | 0 | 0 | 0 | 0 | 286.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158135 | 0 | 158135 | 424450 | -301428 | 33 | 38 | 424450 | -1301428
4 | 4 | 16 | 2 | 40.3156 | 0 | 169.782 | 0 | 28.7398 | 0 | 25.3304 | 19.0363 | 0 | 0 | 0 | 0 | 283.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129057 | 0 | 129057 | 435189 | -300043 | 34 | 40 | 435189 | -1300043
4 | 4 | 17 | 2 | 35.5951 | 0 | 152.497 | 0 | 25.8736 | 0 | 25.3186 | 19.0363 | 0 | 0 | 0 | 2 | 260.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96748.9 | 0 | 96748.9 | 397356 | -322316 | 34 | 40 | 397356 | -1322316
4 | 4 | 18 | 2 | 25.3704 | 0 | 93.4203 | 0 | 23.0709 | 0 | 6.2993 | 19.0363 | 0 | 0 | 0 | 5.6 | 172.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59850.4 | 0 | 59850.4 | 330659 | -390052 | 34 | 40 | 330659 | -1390052
4 | 4 | 19 | 2 | 23.8482 | 0 | 62.7906 | 0 | 12.6158 | 0 | 5.9333 | 12.9754 | 0 | 0 | 0 | 7.2 | 125.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42783.5 | 0 | 42783.5 | 183902 | -8215.4 | 30 | 34 | 183902 | -1008215.4
4 | 4 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 10.8007 | 0 | 5.9068 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37958.2 | 0 | 37958.2 | 163011 | -10983.3 | 29 | 31 | 163011 | -1010983.3
4 | 4 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 11.9832 | 0 | 5.9112 | 12.9754 | 0 | 0 | 0 | 7.2 | 100.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23246.2 | 0 | 23246.2 | 155573 | -17628.3 | 28 | 30 | 155573 | -1017628.3
4 | 4 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 8.1234 | 0 | 5.8981 | 17.5105 | 0 | 0 | 0 | 6.4 | 93.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12450.2 | 0 | 12450.2 | 165054 | -22496.3 | 28 | 30 | 165054 | -1022496.3
4 | 4 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.2082 | 0 | 5.907 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818.4 | 0 | 10818.4 | 157574 | -30716.2 | 28 | 30 | 157574 | -1030716.2
4 | 4 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 10.547 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10821.7 | 0 | 10821.7 | 152695 | -36981.7 | 27 | 29 | 152695 | -1036981.7
4 | 5 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.6856 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10824.6 | 0 | 10824.6 | 150751 | -44365.2 | 27 | 28 | 150751 | -1044365.2
4 | 5 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.4049 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10827 | 0 | 10827 | 148313 | -50641.5 | 27 | 28 | 148313 | -1050641.5
4 | 5 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.3982 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10829.2 | 0 | 10829.2 | 147011 | -59185.2 | 27 | 28 | 147011 | -1059185.2
4 | 5 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 10.5134 | 0 | 5.9011 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12037.5 | 0 | 12037.5 | 148665 | -68221.9 | 26 | 27 | 148665 | -1068221.9
4 | 5 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 13.2891 | 0 | 5.9477 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29357.3 | 0 | 29357.3 | 196176 | -53352 | 26 | 28 | 196176 | -1053352
4 | 5 | 6 | 3 | 48.857 | 0 | 140.608 | 34.3876 | 0 | 0 | 25.2518 | 19.0363 | 0 | 0 | 0 | 1.2 | 269.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87173.6 | 0 | 87173.6 | 323185 | -624856 | 26 | 28 | 323185 | -1624856
4 | 5 | 7 | 3 | 40.6337 | 0 | 168.222 | 31.7475 | 0 | 0 | 25.2782 | 19.0363 | 0 | 0 | 0 | 0 | 284.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105893 | 0 | 105893 | 385387 | -560911 | 29 | 31 | 385387 | -1560911
4 | 5 | 8 | 3 | 39.7098 | 0 | 173.795 | 0 | 26.2708 | 0 | 6.2875 | 19.0363 | 0 | 0 | 0 | 0 | 265.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146622 | 0 | 146622 | 403659 | -411219 | 30 | 34 | 403659 | -1411219
4 | 5 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 28.1061 | 0 | 6.3057 | 19.0363 | 0 | 0 | 0 | 0 | 266.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172542 | 0 | 172542 | 427682 | -332865 | 32 | 39 | 427682 | -1332865
4 | 5 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 28.5234 | 0 | 6.3225 | 19.0363 | 0 | 0 | 0 | 0 | 258.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176238 | 0 | 176238 | 423904 | -316191 | 34 | 40 | 423904 | -1316191
4 | 5 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 30.1606 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176236 | 0 | 176236 | 437504 | -263802 | 38 | 44 | 437504 | -1263802
4 | 5 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 27.751 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176234 | 0 | 176234 | 403356 | -227338 | 35 | 45 | 403356 | -1227338
4 | 5 | 13 | 3 | 41.2773 | 0 | 165.698 | 0 | 32.307 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176232 | 0 | 176232 | 449577 | -183810 | 37 | 48 | 449577 | -1183810
4 | 5 | 14 | 3 | 40.6658 | 0 | 172.702 | 0 | 34.7883 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173952 | 0 | 173952 | 472324 | -158121 | 38 | 49 | 472324 | -1158121
4 | 5 | 15 | 3 | 40.5843 | 0 | 173.986 | 0 | 34.6222 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158125 | 0 | 158125 | 463802 | -122852 | 38 | 50 | 463802 | -1122852
4 | 5 | 16 | 3 | 40.3336 | 0 | 169.782 | 0 | 34.6098 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129046 | 0 | 129046 | 463258 | -127948 | 37 | 50 | 463258 | -1127948
4 | 5 | 17 | 3 | 35.509 | 0 | 152.497 | 0 | 30.8947 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 246.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96737.6 | 0 | 96737.6 | 425580 | -149338 | 37 | 49 | 425580 | -1149338
4 | 5 | 18 | 3 | 25.156 | 0 | 93.4203 | 0 | 24.6115 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59839.3 | 0 | 59839.3 | 340626 | -237503 | 36 | 46 | 340626 | -1237503
4 | 5 | 19 | 3 | 23.1999 | 0 | 62.7906 | 0 | 9.1211 | 0 | 5.4895 | 8.818 | 0 | 0 | 0 | 7.2 | 116.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42773 | 0 | 42773 | 184131 | 0 | 32 | 39 | 184131 | -1000000
4 | 5 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 11.245 | 0 | 5.9101 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37948.1 | 0 | 37948.1 | 164885 | -8033.88 | 32 | 37 | 164885 | -1008033.88
4 | 5 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.5158 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23234.8 | 0 | 23234.8 | 151370 | 0 | 31 | 36 | 151370 | -1000000
4 | 5 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 10.4956 | 0 | 5.8993 | 12.9754 | 0 | 0 | 0 | 6.4 | 91.3009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12437.8 | 0 | 12437.8 | 140145 | -13665 | 30 | 32 | 140145 | -1013665
4 | 5 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 8.2808 | 0 | 5.899 | 17.5105 | 0 | 0 | 0 | 5.6 | 90.1482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10805.7 | 0 | 10805.7 | 168819 | -8732.44 | 29 | 30 | 168819 | -1008732.44
4 | 5 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 10.9772 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10808 | 0 | 10808 | 161414 | -15607.6 | 28 | 30 | 161414 | -1015607.6
4 | 6 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.491 | 0 | 5.9035 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10810.8 | 0 | 10810.8 | 157741 | -20961.9 | 27 | 28 | 157741 | -1020961.9
4 | 6 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.2401 | 0 | 5.9015 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10813.4 | 0 | 10813.4 | 154197 | -25762.6 | 28 | 29 | 154197 | -1025762.6
4 | 6 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.0759 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10815.4 | 0 | 10815.4 | 152164 | -29802.5 | 29 | 29 | 152164 | -1029802.5
4 | 6 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 10.1046 | 0 | 5.9007 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.9602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12023.8 | 0 | 12023.8 | 152990 | -36606.9 | 28 | 29 | 152990 | -1036606.9
4 | 6 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.9958 | 0 | 5.9479 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29343.5 | 0 | 29343.5 | 200703 | -31631.2 | 29 | 30 | 200703 | -1031631.2
4 | 6 | 6 | 4 | 48.7162 | 0 | 140.608 | 31.3175 | 0 | 0 | 25.2665 | 19.0363 | 0 | 0 | 0 | 1.2 | 266.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87159.8 | 0 | 87159.8 | 324325 | -572585 | 29 | 30 | 324325 | -1572585
4 | 6 | 7 | 4 | 43.7722 | 0 | 168.222 | 28.2673 | 0 | 0 | 25.2831 | 19.0363 | 0 | 0 | 0 | 0 | 284.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105880 | 0 | 105880 | 386506 | -512617 | 32 | 33 | 386506 | -1512617
4 | 6 | 8 | 4 | 39.8881 | 0 | 173.795 | 0 | 25.7834 | 0 | 6.2877 | 19.0363 | 0 | 0 | 0 | 0 | 264.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146610 | 0 | 146610 | 404837 | -381194 | 33 | 36 | 404837 | -1381194
4 | 6 | 9 | 4 | 40.7463 | 0 | 172.186 | 0 | 30.0155 | 0 | 6.3115 | 19.0363 | 0 | 0 | 0 | 0 | 268.296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172533 | 0 | 172533 | 446741 | -323378 | 37 | 42 | 446741 | -1323378
4 | 6 | 10 | 4 | 41.1639 | 0 | 163.102 | 0 | 30.5147 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176230 | 0 | 176230 | 440928 | -269901 | 39 | 45 | 440928 | -1269901
4 | 6 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 31.2515 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176227 | 0 | 176227 | 417530 | -167999 | 41 | 52 | 417530 | -1167999
4 | 6 | 12 | 4 | 39.8882 | 0 | 150.207 | 0 | 30.8711 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176226 | 0 | 176226 | 401043 | -125476 | 42 | 55 | 401043 | -1125476
4 | 6 | 13 | 4 | 41.2802 | 0 | 165.698 | 0 | 32.9446 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176223 | 0 | 176223 | 446969 | -74725 | 45 | 58 | 446969 | -1074725
4 | 6 | 14 | 4 | 40.6367 | 0 | 172.702 | 0 | 32.0916 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173943 | 0 | 173943 | 477600 | -54001.6 | 47 | 59 | 477600 | -1054001.6
4 | 6 | 15 | 4 | 41.0243 | 0 | 173.986 | 0 | 30.1418 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158118 | 0 | 158118 | 478457 | -32680.8 | 47 | 60 | 478457 | -1032680.8
4 | 6 | 16 | 4 | 40.3222 | 0 | 169.782 | 0 | 32.5907 | 0 | 6.332 | 19.1102 | 0 | 0 | 0 | 0 | 268.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129039 | 0 | 129039 | 493567 | -25056.4 | 48 | 62 | 493567 | -1025056.4
4 | 6 | 17 | 4 | 35.6096 | 0 | 152.497 | 0 | 28.0314 | 0 | 6.332 | 19.0559 | 0 | 0 | 0 | 2 | 243.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96730.8 | 0 | 96730.8 | 440632 | -23895.1 | 48 | 61 | 440632 | -1023895.1
4 | 6 | 18 | 4 | 25.6637 | 0 | 93.4203 | 0 | 21.2084 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 171.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59832.8 | 0 | 59832.8 | 337036 | -79089.7 | 45 | 57 | 337036 | -1079089.7
4 | 6 | 19 | 4 | 23.9132 | 0 | 62.7906 | 0 | 9.2206 | 0 | 5.491 | 8.818 | 0 | 0 | 0 | 7.2 | 117.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42766.6 | 0 | 42766.6 | 186407 | 0 | 45 | 55 | 186407 | -1000000
4 | 6 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.215 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 7.2 | 103.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37941.8 | 0 | 37941.8 | 166571 | 0 | 44 | 53 | 166571 | -1000000
4 | 6 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.6007 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23226.5 | 0 | 23226.5 | 153232 | 0 | 44 | 52 | 153232 | -1000000
4 | 6 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.0981 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12428.1 | 0 | 12428.1 | 142271 | 0 | 44 | 45 | 142271 | -1000000
4 | 6 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.8518 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10794.7 | 0 | 10794.7 | 136975 | 0 | 43 | 43 | 136975 | -1000000
4 | 6 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 10.6821 | 0 | 5.8991 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.5 | 0 | 10796.5 | 135318 | -12610.6 | 42 | 42 | 135318 | -1012610.6
4 | 7 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7194 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10798.2 | 0 | 10798.2 | 134145 | 0 | 40 | 41 | 134145 | -1000000
4 | 7 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.3903 | 0 | 5.913 | 14.8767 | 0 | 0 | 0 | 4.8 | 91.1593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10800.3 | 0 | 10800.3 | 152588 | -17319.7 | 39 | 40 | 152588 | -1017319.7
4 | 7 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.4179 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 4.8 | 86.1707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.7 | 0 | 10801.7 | 149400 | -7296.48 | 39 | 39 | 149400 | -1007296.48
4 | 7 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.1142 | 0 | 5.898 | 17.5105 | 0 | 0 | 0 | 4.8 | 92.9672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12010.2 | 0 | 12010.2 | 164953 | -17223 | 37 | 38 | 164953 | -1017223
4 | 7 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.2118 | 0 | 5.9728 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29330.1 | 0 | 29330.1 | 209933 | -16778.1 | 37 | 37 | 209933 | -1016778.1
4 | 7 | 6 | 5 | 48.8945 | 0 | 140.608 | 0 | 23.1568 | 0 | 6.3002 | 19.0363 | 0 | 0 | 0 | 1.2 | 239.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87147.2 | 0 | 87147.2 | 326126 | -360881 | 36 | 37 | 326126 | -1360881
4 | 7 | 7 | 5 | 47.977 | 0 | 168.222 | 0 | 26.25 | 0 | 6.2983 | 19.0363 | 0 | 0 | 0 | 0 | 267.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105868 | 0 | 105868 | 388138 | -372804 | 36 | 37 | 388138 | -1372804
4 | 7 | 8 | 5 | 40.9831 | 0 | 173.795 | 0 | 26.1046 | 0 | 6.3064 | 19.0363 | 0 | 0 | 0 | 0 | 266.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146600 | 0 | 146600 | 409337 | -317266 | 36 | 37 | 409337 | -1317266
4 | 7 | 9 | 5 | 41.3161 | 0 | 172.186 | 0 | 26.8211 | 0 | 6.3147 | 19.0363 | 0 | 0 | 0 | 0 | 265.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172523 | 0 | 172523 | 415671 | -311608 | 36 | 37 | 415671 | -1311608
4 | 7 | 10 | 5 | 41.5694 | 0 | 163.102 | 0 | 26.3077 | 0 | 6.3178 | 19.0363 | 0 | 0 | 0 | 0 | 256.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176220 | 0 | 176220 | 404604 | -317629 | 35 | 37 | 404604 | -1317629
4 | 7 | 11 | 5 | 40.9596 | 0 | 149.692 | 0 | 26.7159 | 0 | 6.3265 | 19.0363 | 0 | 0 | 0 | 0 | 242.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176220 | 0 | 176220 | 406500 | -281549 | 36 | 39 | 406500 | -1281549
4 | 7 | 12 | 5 | 39.8438 | 0 | 150.207 | 0 | 24.6735 | 0 | 25.3277 | 19.0363 | 0 | 0 | 0 | 0 | 259.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176219 | 0 | 176219 | 378149 | -261187 | 36 | 40 | 378149 | -1261187
4 | 7 | 13 | 5 | 41.2602 | 0 | 165.698 | 0 | 31.0652 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 282.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176218 | 0 | 176218 | 451873 | -203051 | 37 | 44 | 451873 | -1203051
4 | 7 | 14 | 5 | 40.6618 | 0 | 172.702 | 0 | 34.1052 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 291.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173939 | 0 | 173939 | 485134 | -185998 | 37 | 45 | 485134 | -1185998
4 | 7 | 15 | 5 | 40.581 | 0 | 173.986 | 0 | 34.3076 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158114 | 0 | 158114 | 469942 | -134299 | 38 | 48 | 469942 | -1134299
4 | 7 | 16 | 5 | 40.3269 | 0 | 169.782 | 0 | 34.2966 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129036 | 0 | 129036 | 471743 | -142622 | 36 | 47 | 471743 | -1142622
4 | 7 | 17 | 5 | 35.5057 | 0 | 152.497 | 0 | 30.0866 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 245.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96728.1 | 0 | 96728.1 | 432073 | -173462 | 35 | 45 | 432073 | -1173462
4 | 7 | 18 | 5 | 25.0275 | 0 | 93.4203 | 0 | 22.8499 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 172.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59830.5 | 0 | 59830.5 | 328486 | -248475 | 33 | 42 | 328486 | -1248475
4 | 7 | 19 | 5 | 23.1158 | 0 | 62.7906 | 0 | 9.1569 | 0 | 5.4901 | 8.818 | 0 | 0 | 0 | 7.2 | 116.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42764.7 | 0 | 42764.7 | 185133 | 0 | 31 | 38 | 185133 | -1000000
4 | 7 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.6813 | 0 | 5.9218 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37940.1 | 0 | 37940.1 | 165752 | -11517.6 | 29 | 35 | 165752 | -1011517.6
4 | 7 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.5549 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23225.6 | 0 | 23225.6 | 152227 | 0 | 28 | 34 | 152227 | -1000000
4 | 7 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.653 | 0 | 5.9044 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.4634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12428.9 | 0 | 12428.9 | 141033 | -22744.1 | 28 | 34 | 141033 | -1022744.1
4 | 7 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.6943 | 0 | 5.8968 | 15.0234 | 0 | 0 | 0 | 5.6 | 87.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.6 | 0 | 10796.6 | 155748 | -12619.7 | 27 | 33 | 155748 | -1012619.7
4 | 7 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 12.745 | 0 | 5.9204 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10799.8 | 0 | 10799.8 | 162266 | -29800.3 | 25 | 29 | 162266 | -1029800.3
4 | 8 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.0058 | 0 | 5.912 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10802.8 | 0 | 10802.8 | 157239 | -31572.8 | 25 | 28 | 157239 | -1031572.8
4 | 8 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.5869 | 0 | 5.9154 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10806.7 | 0 | 10806.7 | 154081 | -43050.3 | 24 | 27 | 154081 | -1043050.3
4 | 8 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.3476 | 0 | 5.9125 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10810.4 | 0 | 10810.4 | 151722 | -48798.9 | 25 | 27 | 151722 | -1048798.9
4 | 8 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.8915 | 0 | 5.9193 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10813.6 | 0 | 10813.6 | 156804 | -61534.4 | 24 | 26 | 156804 | -1061534.4
4 | 8 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2307 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 3.6 | 87.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10816.8 | 0 | 10816.8 | 147970 | -62596.7 | 23 | 25 | 147970 | -1062596.7
4 | 8 | 6 | 6 | 6.2996 | 0 | 42.7453 | 0 | 11.3319 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 1.2 | 84.8446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10819.8 | 0 | 10819.8 | 146436 | -79927.3 | 21 | 23 | 146436 | -1079927.3
4 | 8 | 7 | 6 | 4.7477 | 0 | 42.7453 | 44.6923 | 0 | 0 | 13.6636 | 18.956 | 0 | 0 | 0 | 0 | 124.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10822.1 | 0 | 10822.1 | 128171 | -743017 | 23 | 26 | 128171 | -1743017
4 | 8 | 8 | 6 | 4.9602 | 0 | 42.7453 | 39.1898 | 0 | 0 | 6.2503 | 18.8896 | 0 | 0 | 0 | 0 | 112.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10824 | 0 | 10824 | 130019 | -647174 | 23 | 27 | 130019 | -1647174
4 | 8 | 9 | 6 | 5.483 | 0 | 42.7453 | 29.8517 | 0 | 0 | 6.257 | 18.8896 | 0 | 0 | 0 | 0 | 103.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10823 | 0 | 10823 | 128247 | -518867 | 24 | 30 | 128247 | -1518867
4 | 8 | 10 | 6 | 5.4689 | 0 | 42.7453 | 25.2598 | 0 | 0 | 6.2612 | 18.8896 | 0 | 0 | 0 | 0 | 98.6247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.3 | 0 | 10820.3 | 127977 | -446376 | 26 | 33 | 127977 | -1446376
4 | 8 | 11 | 6 | 5.4689 | 0 | 42.7453 | 21.9953 | 0 | 0 | 6.2664 | 18.8896 | 0 | 0 | 0 | 0 | 95.3654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.2 | 0 | 10820.2 | 135276 | -396736 | 28 | 36 | 135276 | -1396736
4 | 8 | 12 | 6 | 5.4689 | 0 | 42.7453 | 20.395 | 0 | 0 | 6.1838 | 18.8896 | 0 | 0 | 0 | 0 | 93.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.1 | 0 | 10820.1 | 150629 | -375324 | 29 | 38 | 150629 | -1375324
4 | 8 | 13 | 6 | 5.4722 | 0 | 42.7453 | 19.9683 | 0 | 0 | 6.1647 | 18.8896 | 0 | 0 | 0 | 0 | 93.2402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.4 | 0 | 10820.4 | 150373 | -371163 | 29 | 38 | 150373 | -1371163
4 | 8 | 14 | 6 | 5.4735 | 0 | 42.7453 | 0 | 8.9471 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 0 | 75.8916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.7 | 0 | 10820.7 | 123931 | -8935.51 | 30 | 39 | 123931 | -1008935.51
4 | 8 | 15 | 6 | 5.4728 | 0 | 42.7453 | 0 | 8.621 | 0 | 5.8976 | 12.8287 | 0 | 0 | 0 | 0 | 75.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10821.3 | 0 | 10821.3 | 123757 | -10677.6 | 31 | 41 | 123757 | -1010677.6
4 | 8 | 16 | 6 | 5.4769 | 0 | 42.7453 | 0 | 8.8683 | 0 | 5.8972 | 12.8287 | 0 | 0 | 0 | 0 | 75.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10822.9 | 0 | 10822.9 | 124742 | -13754.9 | 31 | 40 | 124742 | -1013754.9
4 | 8 | 17 | 6 | 5.5172 | 0 | 42.7453 | 0 | 8.5426 | 0 | 5.8978 | 12.8287 | 0 | 0 | 0 | 2 | 77.5316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10824.7 | 0 | 10824.7 | 123089 | -13206.8 | 30 | 40 | 123089 | -1013206.8
4 | 8 | 18 | 6 | 7.3693 | 0 | 42.7453 | 0 | 10.8249 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.8064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10825.8 | 0 | 10825.8 | 152536 | -22112.9 | 30 | 40 | 152536 | -1022112.9
4 | 8 | 19 | 6 | 8.6851 | 0 | 42.7453 | 0 | 11.1226 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10827.6 | 0 | 10827.6 | 151991 | -22888.1 | 30 | 39 | 151991 | -1022888.1
4 | 8 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.0011 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.0065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10829.5 | 0 | 10829.5 | 146068 | -20182.4 | 30 | 38 | 146068 | -1020182.4
4 | 8 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.8857 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 7.2 | 91.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10831.9 | 0 | 10831.9 | 144949 | -22647.8 | 30 | 38 | 144949 | -1022647.8
4 | 8 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.5047 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 6.4 | 90.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10833.6 | 0 | 10833.6 | 142511 | -24706.3 | 30 | 37 | 142511 | -1024706.3
4 | 8 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.4815 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10835.4 | 0 | 10835.4 | 141588 | -26184.3 | 30 | 37 | 141588 | -1026184.3
4 | 8 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 9.2618 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.7 | 0 | 4026.7 | 139520 | -28096.2 | 30 | 36 | 139520 | -1028096.2
4 | 9 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.3853 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.2968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.28 | 0 | 4028.28 | 138648 | -34572.4 | 29 | 36 | 138648 | -1034572.4
4 | 9 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.1092 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.96 | 0 | 4029.96 | 137465 | -39210.7 | 30 | 37 | 137465 | -1039210.7
4 | 9 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9583 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.54 | 0 | 4031.54 | 137793 | -54956.9 | 30 | 37 | 137793 | -1054956.9
4 | 9 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.5353 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.05 | 0 | 4033.05 | 135916 | -59698.8 | 30 | 37 | 135916 | -1059698.8
4 | 9 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0197 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 3.6 | 85.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.16 | 0 | 4035.16 | 135823 | -67473.2 | 30 | 37 | 135823 | -1067473.2
4 | 9 | 6 | 7 | 5.0305 | 0 | 42.7453 | 0 | 10.8669 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 1.2 | 83.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.09 | 0 | 4037.09 | 134691 | -73596.1 | 29 | 36 | 134691 | -1073596.1
4 | 9 | 7 | 7 | 3.843 | 0 | 42.7453 | 0 | 10.7847 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 0 | 80.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.02 | 0 | 4039.02 | 134577 | -65490.4 | 32 | 38 | 134577 | -1065490.4
4 | 9 | 8 | 7 | 3.8001 | 0 | 42.7453 | 0 | 11.1927 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 0 | 81.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.83 | 0 | 4040.83 | 136216 | -56851.4 | 33 | 38 | 136216 | -1056851.4
4 | 9 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.6858 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 0 | 80.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4042.59 | 0 | 4042.59 | 136676 | -40454.7 | 35 | 43 | 136676 | -1040454.7
4 | 9 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.9089 | 0 | 5.9011 | 17.3638 | 0 | 0 | 0 | 0 | 81.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.08 | 0 | 4044.08 | 142101 | -31042.8 | 37 | 47 | 142101 | -1031042.8
4 | 9 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.9688 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 0 | 80.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4045.01 | 0 | 4045.01 | 140761 | -24042.6 | 39 | 48 | 140761 | -1024042.6
4 | 9 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.7235 | 0 | 5.897 | 14.8767 | 0 | 0 | 0 | 0 | 76.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4045.17 | 0 | 4045.17 | 129248 | -13586.2 | 41 | 51 | 129248 | -1013586.2
4 | 9 | 13 | 7 | 4.148 | 0 | 42.7453 | 0 | 8.6879 | 0 | 5.8969 | 14.8767 | 0 | 0 | 0 | 0 | 76.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4045.18 | 0 | 4045.18 | 130824 | -11612.7 | 43 | 53 | 130824 | -1011612.7
4 | 9 | 14 | 7 | 4.1487 | 0 | 42.7453 | 0 | 9.568 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 0 | 79.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.99 | 0 | 4044.99 | 144416 | -12971.1 | 45 | 55 | 144416 | -1012971.1
4 | 9 | 15 | 7 | 4.149 | 0 | 42.7453 | 0 | 6.051 | 0 | 5.4891 | 8.818 | 0 | 0 | 0 | 0 | 67.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.46 | 0 | 4044.46 | 119116 | 0 | 46 | 56 | 119116 | -1000000
4 | 9 | 16 | 7 | 4.1498 | 0 | 42.7453 | 0 | 8.2526 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 0 | 73.8754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.41 | 0 | 4044.41 | 119173 | -10656.3 | 47 | 58 | 119173 | -1010656.3
4 | 9 | 17 | 7 | 4.1508 | 0 | 42.7453 | 0 | 9.1695 | 0 | 5.8968 | 15.3158 | 0 | 0 | 0 | 2 | 79.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.53 | 0 | 4044.53 | 137351 | -4989.31 | 46 | 55 | 137351 | -1004989.31
4 | 9 | 18 | 7 | 4.2109 | 0 | 42.7453 | 0 | 6.0467 | 0 | 5.4892 | 8.818 | 0 | 0 | 0 | 5.6 | 72.9101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4043.85 | 0 | 4043.85 | 119140 | 0 | 45 | 54 | 119140 | -1000000
4 | 9 | 19 | 7 | 6.2596 | 0 | 42.7453 | 0 | 9.9527 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.2 | 0 | 4044.2 | 144785 | -16681.5 | 41 | 47 | 144785 | -1016681.5
4 | 9 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.3447 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.2141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4044.95 | 0 | 4044.95 | 140881 | -14586.5 | 41 | 45 | 140881 | -1014586.5
4 | 9 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.4707 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.3401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4045.46 | 0 | 4045.46 | 139017 | -22780.9 | 38 | 40 | 139017 | -1022780.9
4 | 9 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.0479 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4047.26 | 0 | 4047.26 | 136249 | -29086.3 | 38 | 40 | 136249 | -1029086.3
4 | 9 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1234 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.3935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4048.63 | 0 | 4048.63 | 134916 | -41311.3 | 36 | 37 | 134916 | -1041311.3
4 | 9 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.9927 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10860.7 | 0 | 10860.7 | 134190 | -45488.7 | 36 | 36 | 134190 | -1045488.7
4 | 10 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.5288 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10862.3 | 0 | 10862.3 | 133517 | -51869.1 | 36 | 36 | 133517 | -1051869.1
4 | 10 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.5662 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10863.2 | 0 | 10863.2 | 132773 | -60674.7 | 36 | 36 | 132773 | -1060674.7
4 | 10 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.7995 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10864.5 | 0 | 10864.5 | 131870 | -73659 | 33 | 33 | 131870 | -1073659
4 | 10 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 11.1427 | 0 | 5.9005 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12072.2 | 0 | 12072.2 | 134814 | -83719.9 | 33 | 33 | 134814 | -1083719.9
4 | 10 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 14.9605 | 0 | 5.9643 | 17.5105 | 0 | 0 | 0 | 3.6 | 136.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29391.5 | 0 | 29391.5 | 187282 | -72026.9 | 34 | 34 | 187282 | -1072026.9
4 | 10 | 6 | 1 | 48.2743 | 0 | 140.608 | 34.4228 | 0 | 0 | 25.2496 | 19.0363 | 0 | 0 | 0 | 1.2 | 268.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87207.5 | 0 | 87207.5 | 313824 | -630503 | 34 | 35 | 313824 | -1630503
4 | 10 | 7 | 1 | 39.4755 | 0 | 168.222 | 31.5107 | 0 | 0 | 25.2685 | 19.0363 | 0 | 0 | 0 | 0 | 283.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105927 | 0 | 105927 | 380228 | -562877 | 36 | 37 | 380228 | -1562877
4 | 10 | 8 | 1 | 39.7552 | 0 | 173.795 | 0 | 26.7587 | 0 | 6.2805 | 19.0363 | 0 | 0 | 0 | 0 | 265.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146647 | 0 | 146647 | 409581 | -409686 | 37 | 39 | 409581 | -1409686
4 | 10 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 30.7825 | 0 | 6.3248 | 19.0363 | 0 | 0 | 0 | 0 | 268.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172567 | 0 | 172567 | 439129 | -296793 | 41 | 47 | 439129 | -1296793
4 | 10 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 31.1903 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176262 | 0 | 176262 | 400104 | -152712 | 46 | 57 | 400104 | -1152712
4 | 10 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 30.7599 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176257 | 0 | 176257 | 393491 | -142046 | 45 | 56 | 393491 | -1142046
4 | 10 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 29.9119 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176253 | 0 | 176253 | 397275 | -106306 | 46 | 58 | 397275 | -1106306
4 | 10 | 13 | 1 | 41.2702 | 0 | 165.698 | 0 | 31.5453 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176250 | 0 | 176250 | 439079 | -65768.3 | 48 | 61 | 439079 | -1065768.3
4 | 10 | 14 | 1 | 40.9288 | 0 | 172.702 | 0 | 27.7787 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173969 | 0 | 173969 | 454094 | -54208.9 | 48 | 60 | 454094 | -1054208.9
4 | 10 | 15 | 1 | 40.6862 | 0 | 173.986 | 0 | 28.6047 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158141 | 0 | 158141 | 460998 | -48549.9 | 48 | 60 | 460998 | -1048549.9
4 | 10 | 16 | 1 | 41.7844 | 0 | 169.782 | 0 | 28.5545 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129060 | 0 | 129060 | 459200 | -59555.2 | 48 | 59 | 459200 | -1059555.2
4 | 10 | 17 | 1 | 36.2787 | 0 | 152.497 | 0 | 26.1931 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 242.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96750.6 | 0 | 96750.6 | 417013 | -60609.9 | 48 | 59 | 417013 | -1060609.9
4 | 10 | 18 | 1 | 27.6704 | 0 | 93.4203 | 0 | 20.2689 | 0 | 6.288 | 19.0363 | 0 | 0 | 0 | 5.6 | 172.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59851.6 | 0 | 59851.6 | 310232 | -114952 | 48 | 58 | 310232 | -1114952
4 | 10 | 19 | 1 | 23.3279 | 0 | 62.7906 | 0 | 8.969 | 0 | 5.4875 | 8.818 | 0 | 0 | 0 | 7.2 | 116.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42784.6 | 0 | 42784.6 | 181258 | 0 | 47 | 55 | 181258 | -1000000
4 | 10 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 7.9958 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 102.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37958.9 | 0 | 37958.9 | 161778 | 0 | 47 | 54 | 161778 | -1000000
4 | 10 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.3876 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23247.1 | 0 | 23247.1 | 148570 | 0 | 47 | 54 | 148570 | -1000000
4 | 10 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.8908 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 6.4 | 83.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12448.9 | 0 | 12448.9 | 137735 | 0 | 47 | 54 | 137735 | -1000000
4 | 10 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 8.4747 | 0 | 5.897 | 12.9754 | 0 | 0 | 0 | 5.6 | 85.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10815.9 | 0 | 10815.9 | 133143 | -5399.36 | 47 | 53 | 133143 | -1005399.36
4 | 10 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6089 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.6 | 0 | 10817.6 | 131722 | 0 | 47 | 53 | 131722 | -1000000
4 | 11 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.8484 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10819 | 0 | 10819 | 133330 | -7018.63 | 47 | 53 | 133330 | -1007018.63
4 | 11 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5499 | 0 | 5.4833 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.2 | 0 | 10820.2 | 130407 | 0 | 48 | 55 | 130407 | -1000000
4 | 11 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5363 | 0 | 5.9016 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10821.1 | 0 | 10821.1 | 130153 | -1027.47 | 48 | 55 | 130153 | -1001027.47
4 | 11 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.6659 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12028.1 | 0 | 12028.1 | 133043 | 0 | 48 | 55 | 133043 | -1000000
4 | 11 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 8.7771 | 0 | 5.9033 | 12.9754 | 0 | 0 | 0 | 3.6 | 125.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29346.8 | 0 | 29346.8 | 179988 | -1608.45 | 48 | 54 | 179988 | -1001608.45
4 | 11 | 6 | 2 | 48.4107 | 0 | 140.608 | 0 | 24.3975 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 239.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87162.1 | 0 | 87162.1 | 325436 | -154668 | 48 | 53 | 325436 | -1154668
4 | 11 | 7 | 2 | 40.5129 | 0 | 168.222 | 0 | 31.7478 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105880 | 0 | 105880 | 423385 | -167711 | 48 | 53 | 423385 | -1167711
4 | 11 | 8 | 2 | 39.9237 | 0 | 173.795 | 0 | 31.1535 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146609 | 0 | 146609 | 446087 | -119849 | 49 | 53 | 446087 | -1119849
4 | 11 | 9 | 2 | 41.2048 | 0 | 172.186 | 0 | 33.3015 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172530 | 0 | 172530 | 455692 | -114791 | 49 | 53 | 455692 | -1114791
4 | 11 | 10 | 2 | 42.4885 | 0 | 163.102 | 0 | 31.4664 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176226 | 0 | 176226 | 446909 | -147675 | 48 | 50 | 446909 | -1147675
4 | 11 | 11 | 2 | 41.7276 | 0 | 149.692 | 0 | 31.1224 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176225 | 0 | 176225 | 440447 | -155652 | 49 | 50 | 440447 | -1155652
4 | 11 | 12 | 2 | 39.9661 | 0 | 150.207 | 0 | 30.3104 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176224 | 0 | 176224 | 412399 | -145295 | 48 | 50 | 412399 | -1145295
4 | 11 | 13 | 2 | 42.0456 | 0 | 165.698 | 0 | 33.2046 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176223 | 0 | 176223 | 455652 | -136528 | 48 | 50 | 455652 | -1136528
4 | 11 | 14 | 2 | 41.3663 | 0 | 172.702 | 0 | 34.1708 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173945 | 0 | 173945 | 478126 | -121113 | 49 | 51 | 478126 | -1121113
4 | 11 | 15 | 2 | 41.4515 | 0 | 173.986 | 0 | 32.4122 | 0 | 6.4575 | 19.0363 | 0 | 0 | 0 | 0 | 273.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158120 | 0 | 158120 | 467116 | -114006 | 48 | 50 | 467116 | -1114006
4 | 11 | 16 | 2 | 42.1472 | 0 | 169.782 | 0 | 32.3073 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 288.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129041 | 0 | 129041 | 478393 | -129224 | 48 | 49 | 478393 | -1129224
4 | 11 | 17 | 2 | 37.0839 | 0 | 152.497 | 0 | 30.1748 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 247.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96733.5 | 0 | 96733.5 | 434311 | -150312 | 48 | 49 | 434311 | -1150312
4 | 11 | 18 | 2 | 25.9014 | 0 | 93.4203 | 0 | 24.9459 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 175.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59835.8 | 0 | 59835.8 | 331375 | -192687 | 49 | 50 | 331375 | -1192687
4 | 11 | 19 | 2 | 23.7295 | 0 | 62.7906 | 0 | 9.1691 | 0 | 5.4902 | 8.818 | 0 | 0 | 0 | 7.2 | 117.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42769.8 | 0 | 42769.8 | 185356 | 0 | 49 | 50 | 185356 | -1000000
4 | 11 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.1837 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 103.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37944.7 | 0 | 37944.7 | 165892 | 0 | 50 | 51 | 165892 | -1000000
4 | 11 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 9.5093 | 0 | 5.8989 | 12.9754 | 0 | 0 | 0 | 7.2 | 98.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23230.7 | 0 | 23230.7 | 152618 | -5582.82 | 51 | 52 | 152618 | -1005582.82
4 | 11 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.0812 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12432.9 | 0 | 12432.9 | 141904 | 0 | 55 | 56 | 141904 | -1000000
4 | 11 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.84 | 0 | 5.481 | 12.9754 | 0 | 0 | 0 | 5.6 | 83.7543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10799.5 | 0 | 10799.5 | 136718 | 0 | 54 | 56 | 136718 | -1000000
4 | 11 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.7665 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.5 | 0 | 10801.5 | 135170 | 0 | 53 | 55 | 135170 | -1000000
4 | 12 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7254 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10802.7 | 0 | 10802.7 | 134282 | 0 | 52 | 54 | 134282 | -1000000
4 | 12 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6928 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.9 | 0 | 10803.9 | 133572 | 0 | 52 | 55 | 133572 | -1000000
4 | 12 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 9.009 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.7137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10804.8 | 0 | 10804.8 | 132957 | -8072.08 | 52 | 55 | 132957 | -1008072.08
4 | 12 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.8037 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12012.2 | 0 | 12012.2 | 136061 | 0 | 52 | 55 | 136061 | -1000000
4 | 12 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.901 | 0 | 5.9048 | 12.9754 | 0 | 0 | 0 | 3.6 | 125.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29330.9 | 0 | 29330.9 | 182696 | -1542.57 | 51 | 53 | 182696 | -1001542.57
4 | 12 | 6 | 3 | 48.4756 | 0 | 140.608 | 0 | 24.4692 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 240.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87146.4 | 0 | 87146.4 | 329788 | -103550 | 52 | 54 | 329788 | -1103550
4 | 12 | 7 | 3 | 44.3844 | 0 | 168.222 | 0 | 34.4477 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105865 | 0 | 105865 | 448313 | -117047 | 53 | 55 | 448313 | -1117047
4 | 12 | 8 | 3 | 39.8354 | 0 | 173.795 | 0 | 31.635 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146596 | 0 | 146596 | 480644 | -70570.1 | 54 | 56 | 480644 | -1070570.1
4 | 12 | 9 | 3 | 40.6492 | 0 | 172.186 | 0 | 34.357 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172519 | 0 | 172519 | 507949 | -45889 | 55 | 59 | 507949 | -1045889
4 | 12 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 31.2702 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176216 | 0 | 176216 | 495267 | -28579.5 | 56 | 60 | 495267 | -1028579.5
4 | 12 | 11 | 3 | 41.9486 | 0 | 149.692 | 0 | 32.2653 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176214 | 0 | 176214 | 485084 | -19693.3 | 57 | 62 | 485084 | -1019693.3
4 | 12 | 12 | 3 | 40.1288 | 0 | 150.207 | 0 | 24.1001 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 239.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176214 | 0 | 176214 | 405121 | -73402.6 | 47 | 50 | 405121 | -1073402.6
4 | 12 | 13 | 3 | 41.7253 | 0 | 165.698 | 0 | 30.1677 | 0 | 9.7951 | 19.0363 | 0 | 0 | 0 | 0 | 266.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176213 | 0 | 176213 | 497739 | -77837.8 | 51 | 53 | 497739 | -1077837.8
4 | 12 | 14 | 3 | 41.106 | 0 | 172.702 | 0 | 32.297 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173935 | 0 | 173935 | 491922 | -63833.3 | 49 | 55 | 491922 | -1063833.3
4 | 12 | 15 | 3 | 41.0311 | 0 | 173.986 | 0 | 28.9673 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158111 | 0 | 158111 | 476324 | -55163.4 | 49 | 53 | 476324 | -1055163.4
4 | 12 | 16 | 3 | 41.1587 | 0 | 169.782 | 0 | 29.3158 | 0 | 6.332 | 19.057 | 0 | 0 | 0 | 0 | 265.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129032 | 0 | 129032 | 480306 | -60209.6 | 49 | 53 | 480306 | -1060209.6
4 | 12 | 17 | 3 | 36.6523 | 0 | 152.497 | 0 | 26.147 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 242.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96724.7 | 0 | 96724.7 | 426071 | -72727 | 49 | 52 | 426071 | -1072727
4 | 12 | 18 | 3 | 27.054 | 0 | 93.4203 | 0 | 22.6785 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59827.2 | 0 | 59827.2 | 344024 | -142549 | 47 | 50 | 344024 | -1142549
4 | 12 | 19 | 3 | 23.5851 | 0 | 62.7906 | 0 | 9.2611 | 0 | 5.4916 | 8.818 | 0 | 0 | 0 | 7.2 | 117.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42761.4 | 0 | 42761.4 | 187189 | 0 | 47 | 50 | 187189 | -1000000
4 | 12 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.2578 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 7.2 | 103.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37937.1 | 0 | 37937.1 | 167510 | 0 | 46 | 48 | 167510 | -1000000
4 | 12 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 9.5157 | 0 | 5.8992 | 12.9754 | 0 | 0 | 0 | 7.2 | 98.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23221.4 | 0 | 23221.4 | 153971 | -5312.1 | 45 | 46 | 153971 | -1005312.1
4 | 12 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.1216 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12423.3 | 0 | 12423.3 | 142782 | 0 | 45 | 46 | 142782 | -1000000
4 | 12 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 10.336 | 0 | 5.8985 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.6679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10789.9 | 0 | 10789.9 | 137837 | -11441.2 | 44 | 45 | 137837 | -1011441.2
4 | 12 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8154 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 78.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10792.2 | 0 | 10792.2 | 136240 | 0 | 44 | 45 | 136240 | -1000000
4 | 13 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.6085 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.1964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10794.2 | 0 | 10794.2 | 135347 | -14029.7 | 45 | 46 | 135347 | -1014029.7
4 | 13 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7293 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.1 | 0 | 10796.1 | 134366 | 0 | 45 | 46 | 134366 | -1000000
4 | 13 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.5648 | 0 | 5.8985 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.1523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10797.7 | 0 | 10797.7 | 133560 | -14919.5 | 45 | 46 | 133560 | -1014919.5
4 | 13 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.7514 | 0 | 5.8968 | 15.0234 | 0 | 0 | 0 | 4.8 | 90.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12005.8 | 0 | 12005.8 | 157146 | -5967.99 | 45 | 45 | 157146 | -1005967.99
4 | 13 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 10.1765 | 0 | 5.9277 | 15.0234 | 0 | 0 | 0 | 3.6 | 129.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29325.1 | 0 | 29325.1 | 210739 | -10387.5 | 44 | 45 | 210739 | -1010387.5
4 | 13 | 6 | 4 | 48.2496 | 0 | 140.608 | 0 | 23.696 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 239.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87141.3 | 0 | 87141.3 | 327953 | -229698 | 44 | 45 | 327953 | -1229698
4 | 13 | 7 | 4 | 43.2399 | 0 | 168.222 | 0 | 31.3416 | 0 | 6.328 | 19.0363 | 0 | 0 | 0 | 0 | 268.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105861 | 0 | 105861 | 456986 | -269429 | 44 | 45 | 456986 | -1269429
4 | 13 | 8 | 4 | 40.106 | 0 | 173.795 | 0 | 32.748 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146593 | 0 | 146593 | 472490 | -221317 | 44 | 45 | 472490 | -1221317
4 | 13 | 9 | 4 | 41.2842 | 0 | 172.186 | 0 | 34.3817 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172516 | 0 | 172516 | 485432 | -204120 | 45 | 46 | 485432 | -1204120
4 | 13 | 10 | 4 | 41.6067 | 0 | 163.102 | 0 | 33.0249 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176214 | 0 | 176214 | 465934 | -193074 | 45 | 46 | 465934 | -1193074
4 | 13 | 11 | 4 | 40.9922 | 0 | 149.692 | 0 | 32.4253 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176213 | 0 | 176213 | 450114 | -179971 | 45 | 47 | 450114 | -1179971
4 | 13 | 12 | 4 | 39.7857 | 0 | 150.207 | 0 | 29.7898 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176213 | 0 | 176213 | 414751 | -142658 | 46 | 48 | 414751 | -1142658
4 | 13 | 13 | 4 | 41.4292 | 0 | 165.698 | 0 | 34.5329 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 267.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176212 | 0 | 176212 | 463443 | -121476 | 47 | 50 | 463443 | -1121476
4 | 13 | 14 | 4 | 40.7798 | 0 | 172.702 | 0 | 31.0846 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173934 | 0 | 173934 | 484345 | -108594 | 47 | 50 | 484345 | -1108594
4 | 13 | 15 | 4 | 40.8251 | 0 | 173.986 | 0 | 32.3524 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158109 | 0 | 158109 | 490442 | -96033.5 | 49 | 50 | 490442 | -1096033.5
4 | 13 | 16 | 4 | 41.1938 | 0 | 169.782 | 0 | 29.2536 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129030 | 0 | 129030 | 468141 | -96748.2 | 46 | 50 | 468141 | -1096748.2
4 | 13 | 17 | 4 | 36.3736 | 0 | 152.497 | 0 | 27.5586 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 243.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96722.8 | 0 | 96722.8 | 430673 | -105974 | 46 | 50 | 430673 | -1105974
4 | 13 | 18 | 4 | 27.4892 | 0 | 93.4203 | 0 | 22.9356 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 174.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59825.3 | 0 | 59825.3 | 348626 | -161170 | 46 | 49 | 348626 | -1161170
4 | 13 | 19 | 4 | 23.4329 | 0 | 62.7906 | 0 | 9.2608 | 0 | 5.4916 | 8.818 | 0 | 0 | 0 | 7.2 | 116.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42759.6 | 0 | 42759.6 | 187105 | 0 | 46 | 48 | 187105 | -1000000
4 | 13 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.2567 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 7.2 | 103.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37935.2 | 0 | 37935.2 | 167488 | 0 | 46 | 48 | 167488 | -1000000
4 | 13 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.639 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23219.2 | 0 | 23219.2 | 154068 | 0 | 46 | 48 | 154068 | -1000000
4 | 13 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 9.5174 | 0 | 5.8976 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12420.7 | 0 | 12420.7 | 142942 | -6887.92 | 46 | 47 | 142942 | -1006887.92
4 | 13 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.8942 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10787.4 | 0 | 10787.4 | 137906 | 0 | 45 | 46 | 137906 | -1000000
4 | 13 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 10.2452 | 0 | 5.8981 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10789.4 | 0 | 10789.4 | 136330 | -12348 | 44 | 44 | 136330 | -1012348
4 | 14 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7655 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10791.4 | 0 | 10791.4 | 135154 | 0 | 42 | 42 | 135154 | -1000000
4 | 14 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 12.4644 | 0 | 5.9147 | 14.8767 | 0 | 0 | 0 | 4.8 | 91.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10793.2 | 0 | 10793.2 | 155423 | -17596.9 | 40 | 40 | 155423 | -1017596.9
4 | 14 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.5391 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 4.8 | 86.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10795.1 | 0 | 10795.1 | 152049 | -8797.93 | 39 | 40 | 152049 | -1008797.93
4 | 14 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.3058 | 0 | 5.8992 | 17.5105 | 0 | 0 | 0 | 4.8 | 93.1599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12003.4 | 0 | 12003.4 | 169173 | -17111.2 | 38 | 38 | 169173 | -1017111.2
4 | 14 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.2045 | 0 | 5.976 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29323.4 | 0 | 29323.4 | 213205 | -16248.4 | 36 | 36 | 213205 | -1016248.4
4 | 14 | 6 | 5 | 48.0012 | 0 | 140.608 | 0 | 22.865 | 0 | 6.2937 | 19.0363 | 0 | 0 | 0 | 1.2 | 238.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87140.5 | 0 | 87140.5 | 326885 | -389032 | 34 | 34 | 326885 | -1389032
4 | 14 | 7 | 5 | 43.2399 | 0 | 168.222 | 0 | 26.2304 | 0 | 6.2939 | 19.0363 | 0 | 0 | 0 | 0 | 263.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105861 | 0 | 105861 | 388743 | -406267 | 33 | 33 | 388743 | -1406267
4 | 14 | 8 | 5 | 39.9527 | 0 | 173.795 | 0 | 25.8574 | 0 | 6.2973 | 19.0363 | 0 | 0 | 0 | 0 | 264.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146594 | 0 | 146594 | 407179 | -345854 | 33 | 33 | 407179 | -1345854
4 | 14 | 9 | 5 | 41.2149 | 0 | 172.186 | 0 | 25.7442 | 0 | 6.3057 | 19.0363 | 0 | 0 | 0 | 0 | 264.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172518 | 0 | 172518 | 404947 | -335973 | 33 | 33 | 404947 | -1335973
4 | 14 | 10 | 5 | 41.5715 | 0 | 163.102 | 0 | 26.2867 | 0 | 25.3105 | 19.0363 | 0 | 0 | 0 | 0 | 275.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176217 | 0 | 176217 | 400647 | -357155 | 33 | 33 | 400647 | -1357155
4 | 14 | 11 | 5 | 40.9184 | 0 | 149.692 | 0 | 25.37 | 0 | 25.3183 | 19.0363 | 0 | 0 | 0 | 0 | 260.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176217 | 0 | 176217 | 385492 | -313509 | 33 | 34 | 385492 | -1313509
4 | 14 | 12 | 5 | 39.8054 | 0 | 150.207 | 0 | 23.3643 | 0 | 6.4849 | 19.0363 | 0 | 0 | 0 | 0 | 238.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176216 | 0 | 176216 | 361293 | -288383 | 35 | 36 | 361293 | -1288383
4 | 14 | 13 | 5 | 41.4341 | 0 | 165.698 | 0 | 24.9693 | 0 | 25.3349 | 19.0363 | 0 | 0 | 0 | 0 | 276.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176215 | 0 | 176215 | 392463 | -249170 | 34 | 36 | 392463 | -1249170
4 | 14 | 14 | 5 | 40.797 | 0 | 172.702 | 0 | 27.5583 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 285.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173936 | 0 | 173936 | 425169 | -236468 | 34 | 37 | 425169 | -1236468
4 | 14 | 15 | 5 | 40.7963 | 0 | 173.986 | 0 | 28.4013 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 287.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158112 | 0 | 158112 | 434436 | -238174 | 35 | 38 | 434436 | -1238174
4 | 14 | 16 | 5 | 40.908 | 0 | 169.782 | 0 | 29.1147 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 284.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129034 | 0 | 129034 | 440379 | -254652 | 35 | 39 | 440379 | -1254652
4 | 14 | 17 | 5 | 36.2316 | 0 | 152.497 | 0 | 25.6338 | 0 | 25.3319 | 19.0363 | 0 | 0 | 0 | 2 | 260.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96727.3 | 0 | 96727.3 | 397890 | -276120 | 35 | 39 | 397890 | -1276120
4 | 14 | 18 | 5 | 26.2964 | 0 | 93.4203 | 0 | 22.4249 | 0 | 6.311 | 19.0363 | 0 | 0 | 0 | 5.6 | 173.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59830.1 | 0 | 59830.1 | 322202 | -346186 | 34 | 38 | 322202 | -1346186
4 | 14 | 19 | 5 | 23.2727 | 0 | 62.7906 | 0 | 9.2319 | 0 | 5.4912 | 12.9754 | 0 | 0 | 0 | 7.2 | 120.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42764.1 | 0 | 42764.1 | 186909 | 0 | 35 | 39 | 186909 | -1000000
4 | 14 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 10.0107 | 0 | 5.904 | 12.9754 | 0 | 0 | 0 | 7.2 | 109.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37938.9 | 0 | 37938.9 | 165832 | -7597.34 | 35 | 39 | 165832 | -1007597.34
4 | 14 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 10.1472 | 0 | 5.9007 | 12.9754 | 0 | 0 | 0 | 7.2 | 98.9436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23224.8 | 0 | 23224.8 | 152412 | -11839.1 | 35 | 39 | 152412 | -1011839.1
4 | 14 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 9.586 | 0 | 5.8975 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.3894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12428 | 0 | 12428 | 141188 | -12398.3 | 35 | 39 | 141188 | -1012398.3
4 | 14 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 10.7828 | 0 | 5.9041 | 15.0234 | 0 | 0 | 0 | 5.6 | 90.1682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10795.5 | 0 | 10795.5 | 155935 | -15838.3 | 34 | 37 | 155935 | -1015838.3
4 | 14 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 11.5266 | 0 | 5.911 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10798.5 | 0 | 10798.5 | 162924 | -21905.4 | 33 | 35 | 162924 | -1021905.4
4 | 15 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7289 | 0 | 5.9109 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801 | 0 | 10801 | 159397 | -25620.8 | 33 | 35 | 159397 | -1025620.8
4 | 15 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.7289 | 0 | 5.9202 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10804.6 | 0 | 10804.6 | 162130 | -28673.1 | 31 | 33 | 162130 | -1028673.1
4 | 15 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0111 | 0 | 5.9048 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10807.9 | 0 | 10807.9 | 154135 | -30580.2 | 31 | 32 | 154135 | -1030580.2
4 | 15 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 13.2115 | 0 | 5.9238 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10810.8 | 0 | 10810.8 | 159616 | -43768.1 | 28 | 28 | 159616 | -1043768.1
4 | 15 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.6803 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 3.6 | 86.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10813.3 | 0 | 10813.3 | 149554 | -47782.5 | 27 | 27 | 149554 | -1047782.5
4 | 15 | 6 | 6 | 6.0661 | 0 | 42.7453 | 0 | 11.0807 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 1.2 | 84.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10816.2 | 0 | 10816.2 | 150656 | -51204.6 | 28 | 28 | 150656 | -1051204.6
4 | 15 | 7 | 6 | 4.7112 | 0 | 42.7453 | 35.097 | 0 | 0 | 6.264 | 18.8896 | 0 | 0 | 0 | 0 | 107.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818.6 | 0 | 10818.6 | 130991 | -586823 | 33 | 34 | 130991 | -1586823
4 | 15 | 8 | 6 | 4.9575 | 0 | 42.7453 | 31.3181 | 0 | 0 | 6.2684 | 18.8896 | 0 | 0 | 0 | 0 | 104.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.5 | 0 | 10820.5 | 184328 | -525564 | 35 | 39 | 184328 | -1525564
4 | 15 | 9 | 6 | 5.476 | 0 | 42.7453 | 22.2399 | 0 | 0 | 6.2781 | 18.8896 | 0 | 0 | 0 | 0 | 95.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10819.9 | 0 | 10819.9 | 168255 | -390632 | 37 | 42 | 168255 | -1390632
4 | 15 | 10 | 6 | 5.4689 | 0 | 42.7453 | 17.907 | 0 | 0 | 6.0534 | 18.8896 | 0 | 0 | 0 | 0 | 91.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.3 | 0 | 10817.3 | 184404 | -322175 | 40 | 47 | 184404 | -1322175
4 | 15 | 11 | 6 | 5.4689 | 0 | 42.7453 | 16.1208 | 0 | 0 | 5.9838 | 18.8896 | 0 | 0 | 0 | 0 | 89.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.3 | 0 | 10817.3 | 184963 | -267833 | 42 | 52 | 184963 | -1267833
4 | 15 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 14.7564 | 0 | 5.9593 | 18.8896 | 0 | 0 | 0 | 0 | 87.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.2 | 0 | 10817.2 | 185874 | -229381 | 42 | 54 | 185874 | -1229381
4 | 15 | 13 | 6 | 5.4722 | 0 | 42.7453 | 0 | 15.0105 | 0 | 5.9667 | 18.8896 | 0 | 0 | 0 | 0 | 88.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.5 | 0 | 10817.5 | 188465 | -218271 | 42 | 54 | 188465 | -1218271
4 | 15 | 14 | 6 | 5.4735 | 0 | 42.7453 | 0 | 6.3683 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 0 | 68.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.9 | 0 | 10817.9 | 125432 | 0 | 42 | 57 | 125432 | -1000000
4 | 15 | 15 | 6 | 5.4746 | 0 | 42.7453 | 0 | 6.3119 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 0 | 68.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818 | 0 | 10818 | 125243 | 0 | 41 | 55 | 125243 | -1000000
4 | 15 | 16 | 6 | 5.4765 | 0 | 42.7453 | 0 | 6.3091 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 0 | 68.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818 | 0 | 10818 | 125184 | 0 | 41 | 56 | 125184 | -1000000
4 | 15 | 17 | 6 | 5.476 | 0 | 42.7453 | 0 | 8.0566 | 0 | 5.8986 | 12.8287 | 0 | 0 | 0 | 2 | 77.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.6 | 0 | 10817.6 | 124946 | -5767.95 | 41 | 55 | 124946 | -1005767.95
4 | 15 | 18 | 6 | 5.6053 | 0 | 42.7453 | 0 | 6.2889 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 5.6 | 74.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10817.6 | 0 | 10817.6 | 124740 | 0 | 41 | 53 | 124740 | -1000000
4 | 15 | 19 | 6 | 8.0372 | 0 | 42.7453 | 0 | 6.2715 | 0 | 5.9044 | 12.8287 | 0 | 0 | 0 | 7.2 | 82.9871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818 | 0 | 10818 | 124357 | -1652.86 | 38 | 46 | 124357 | -1001652.86
4 | 15 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.2567 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 7.2 | 79.3037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10818.6 | 0 | 10818.6 | 124033 | 0 | 38 | 44 | 124033 | -1000000
4 | 15 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.7055 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 7.2 | 87.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10819.5 | 0 | 10819.5 | 123745 | -14520.4 | 37 | 40 | 123745 | -1014520.4
4 | 15 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.6254 | 0 | 5.8967 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10820.8 | 0 | 10820.8 | 154507 | -8982.5 | 37 | 39 | 154507 | -1008982.5
4 | 15 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3497 | 0 | 5.9083 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.7644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10822.3 | 0 | 10822.3 | 159011 | -18602.2 | 36 | 37 | 159011 | -1018602.2
4 | 15 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 10.0594 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.26 | 0 | 4014.26 | 147266 | -14128.3 | 35 | 37 | 147266 | -1014128.3
4 | 16 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.6872 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.5997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.6 | 0 | 4016.6 | 145005 | -20294.2 | 34 | 37 | 145005 | -1020294.2
4 | 16 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.6174 | 0 | 5.9072 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.27 | 0 | 4018.27 | 151244 | -30261.1 | 31 | 33 | 151244 | -1030261.1
4 | 16 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.9048 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.12 | 0 | 4020.12 | 141167 | -28889.7 | 31 | 33 | 141167 | -1028889.7
4 | 16 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 12.7217 | 0 | 5.9155 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.49 | 0 | 4022.49 | 151652 | -41528 | 32 | 33 | 151652 | -1041528
4 | 16 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1378 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 3.6 | 84.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4024.21 | 0 | 4024.21 | 138339 | -45169.4 | 28 | 29 | 138339 | -1045169.4
4 | 16 | 6 | 7 | 4.8804 | 0 | 42.7453 | 0 | 9.5942 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 1.2 | 81.6807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4026.77 | 0 | 4026.77 | 137586 | -48089.5 | 30 | 32 | 137586 | -1048089.5
4 | 16 | 7 | 7 | 3.7191 | 0 | 42.7453 | 0 | 12.1641 | 0 | 5.9096 | 17.3638 | 0 | 0 | 0 | 0 | 81.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.26 | 0 | 4028.26 | 147713 | -45567.3 | 35 | 38 | 147713 | -1045567.3
4 | 16 | 8 | 7 | 3.8 | 0 | 42.7453 | 0 | 6.9979 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 0 | 76.8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030 | 0 | 4030 | 140134 | -26976.6 | 37 | 42 | 140134 | -1026976.6
4 | 16 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.8147 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 0 | 80.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.23 | 0 | 4032.23 | 146880 | -26408.3 | 39 | 46 | 146880 | -1026408.3
4 | 16 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.6052 | 0 | 5.9009 | 14.8767 | 0 | 0 | 0 | 0 | 74.2721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.51 | 0 | 4032.51 | 131409 | -12424.8 | 41 | 52 | 131409 | -1012424.8
4 | 16 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.0891 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 76.7517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.94 | 0 | 4032.94 | 136109 | -11229.4 | 42 | 56 | 136109 | -1011229.4
4 | 16 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.6414 | 0 | 5.9006 | 10.866 | 0 | 0 | 0 | 0 | 70.2973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.54 | 0 | 4032.54 | 132397 | -944.089 | 42 | 58 | 132397 | -1000944.089
4 | 16 | 13 | 7 | 4.1481 | 0 | 42.7453 | 0 | 7.9606 | 0 | 5.8997 | 12.8287 | 0 | 0 | 0 | 0 | 73.5823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.51 | 0 | 4031.51 | 119915 | -9329.07 | 43 | 60 | 119915 | -1009329.07
4 | 16 | 14 | 7 | 4.1486 | 0 | 42.7453 | 0 | 6.3643 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 0 | 67.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.84 | 0 | 4030.84 | 120052 | 0 | 44 | 61 | 120052 | -1000000
4 | 16 | 15 | 7 | 4.1496 | 0 | 42.7453 | 0 | 6.1095 | 0 | 5.4878 | 8.818 | 0 | 0 | 0 | 0 | 67.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.08 | 0 | 4030.08 | 120116 | 0 | 44 | 61 | 120116 | -1000000
4 | 16 | 16 | 7 | 4.1494 | 0 | 42.7453 | 0 | 6.4081 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 0 | 67.6048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.38 | 0 | 4029.38 | 120262 | 0 | 45 | 62 | 120262 | -1000000
4 | 16 | 17 | 7 | 4.1502 | 0 | 42.7453 | 0 | 6.1555 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 2 | 69.3557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.64 | 0 | 4028.64 | 120405 | 0 | 46 | 62 | 120405 | -1000000
4 | 16 | 18 | 7 | 4.1921 | 0 | 42.7453 | 0 | 5.5741 | 0 | 5.4967 | 8.818 | 0 | 0 | 0 | 5.6 | 72.4263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.12 | 0 | 4028.12 | 120328 | 0 | 45 | 59 | 120328 | -1000000
4 | 16 | 19 | 7 | 6.1154 | 0 | 42.7453 | 0 | 8.1227 | 0 | 5.8984 | 12.8287 | 0 | 0 | 0 | 7.2 | 82.9104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.86 | 0 | 4027.86 | 125161 | -6830.33 | 41 | 52 | 125161 | -1006830.33
4 | 16 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6084 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.91 | 0 | 4027.91 | 158715 | -5572.93 | 40 | 48 | 158715 | -1005572.93
4 | 16 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.8464 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.25 | 0 | 4028.25 | 147262 | -10977.7 | 40 | 48 | 147262 | -1010977.7
4 | 16 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.673 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.45 | 0 | 4029.45 | 145096 | -13151.2 | 39 | 46 | 145096 | -1013151.2
4 | 16 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.7953 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.39 | 0 | 4031.39 | 147676 | -15315.6 | 39 | 43 | 147676 | -1015315.6
4 | 16 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.654 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10843.1 | 0 | 10843.1 | 145629 | -13298.5 | 37 | 40 | 145629 | -1013298.5
4 | 17 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.5515 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10844.7 | 0 | 10844.7 | 144180 | -15783.2 | 39 | 41 | 144180 | -1015783.2
4 | 17 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.4921 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10844.9 | 0 | 10844.9 | 143409 | -17370.2 | 38 | 40 | 143409 | -1017370.2
4 | 17 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3873 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10845.8 | 0 | 10845.8 | 141870 | -21027.8 | 37 | 38 | 141870 | -1021027.8
4 | 17 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.3081 | 0 | 5.8971 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.1601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12052.9 | 0 | 12052.9 | 140712 | -26514.2 | 36 | 37 | 140712 | -1026514.2
4 | 17 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.5171 | 0 | 5.9475 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14739 | 0 | 14739 | 192339 | -32314.5 | 36 | 37 | 192339 | -1032314.5
4 | 17 | 6 | 1 | 46.0964 | 0 | 140.608 | 24.7585 | 0 | 0 | 25.2812 | 19.0363 | 0 | 0 | 0 | 1.2 | 256.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40035.7 | 0 | 40035.7 | 315162 | -458853 | 36 | 37 | 315162 | -1458853
4 | 17 | 7 | 1 | 39.5458 | 0 | 168.222 | 0 | 29.5102 | 0 | 6.2966 | 19.0363 | 0 | 0 | 0 | 0 | 262.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43925.6 | 0 | 43925.6 | 414232 | -411356 | 40 | 42 | 414232 | -1411356
4 | 17 | 8 | 1 | 39.9546 | 0 | 173.795 | 0 | 31.2919 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55592.9 | 0 | 55592.9 | 442342 | -258604 | 43 | 48 | 442342 | -1258604
4 | 17 | 9 | 1 | 40.7086 | 0 | 172.186 | 0 | 32.9439 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86722.9 | 0 | 86722.9 | 424967 | -145029 | 46 | 56 | 424967 | -1145029
4 | 17 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 34.3514 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88665.1 | 0 | 88665.1 | 422151 | -89907.5 | 47 | 60 | 422151 | -1089907.5
4 | 17 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 30.3919 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88660.4 | 0 | 88660.4 | 420754 | -67739.2 | 48 | 61 | 420754 | -1067739.2
4 | 17 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 31.3064 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88656.8 | 0 | 88656.8 | 455821 | -50952.8 | 49 | 64 | 455821 | -1050952.8
4 | 17 | 13 | 1 | 41.2913 | 0 | 165.698 | 0 | 36.8016 | 0 | 6.332 | 19.2619 | 0 | 0 | 0 | 0 | 269.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88653.5 | 0 | 88653.5 | 532837 | -30602 | 50 | 66 | 532837 | -1030602
4 | 17 | 14 | 1 | 40.688 | 0 | 172.702 | 0 | 43.0275 | 0 | 6.332 | 19.4445 | 0 | 0 | 0 | 0 | 282.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86704.2 | 0 | 86704.2 | 609296 | -22381.2 | 51 | 68 | 609296 | -1022381.2
4 | 17 | 15 | 1 | 40.5916 | 0 | 173.986 | 0 | 42.9426 | 0 | 6.332 | 19.6539 | 0 | 0 | 0 | 0 | 283.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78917.9 | 0 | 78917.9 | 632738 | -20934 | 52 | 67 | 632738 | -1020934
4 | 17 | 16 | 1 | 40.3218 | 0 | 169.782 | 0 | 44.7464 | 0 | 6.332 | 19.7747 | 0 | 0 | 0 | 0 | 280.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65293.6 | 0 | 65293.6 | 638866 | -19641.4 | 52 | 68 | 638866 | -1019641.4
4 | 17 | 17 | 1 | 35.5 | 0 | 152.497 | 0 | 35.8268 | 0 | 6.332 | 19.5382 | 0 | 0 | 0 | 2 | 251.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49724.1 | 0 | 49724.1 | 534769 | -16074.7 | 51 | 66 | 534769 | -1016074.7
4 | 17 | 18 | 1 | 25.3547 | 0 | 93.4203 | 0 | 26.0358 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 175.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30263.7 | 0 | 30263.7 | 377457 | -20463.7 | 51 | 66 | 377457 | -1020463.7
4 | 17 | 19 | 1 | 22.3959 | 0 | 62.7906 | 0 | 7.5504 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 114.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21506.6 | 0 | 21506.6 | 182796 | 0 | 49 | 60 | 182796 | -1000000
4 | 17 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.0515 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 7.2 | 102.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20534.3 | 0 | 20534.3 | 162991 | 0 | 48 | 59 | 162991 | -1000000
4 | 17 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.4553 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12746.8 | 0 | 12746.8 | 150056 | 0 | 49 | 60 | 150056 | -1000000
4 | 17 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.2499 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12435.5 | 0 | 12435.5 | 139146 | 0 | 49 | 61 | 139146 | -1000000
4 | 17 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.4784 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 5.6 | 79.2384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.4 | 0 | 10801.4 | 134427 | 0 | 48 | 60 | 134427 | -1000000
4 | 17 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6777 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10802.4 | 0 | 10802.4 | 133232 | 0 | 48 | 58 | 133232 | -1000000
4 | 18 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6399 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.3 | 0 | 10803.3 | 132413 | 0 | 47 | 54 | 132413 | -1000000
4 | 18 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6025 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.9 | 0 | 10803.9 | 131594 | 0 | 46 | 52 | 131594 | -1000000
4 | 18 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5646 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10804.6 | 0 | 10804.6 | 130764 | 0 | 43 | 48 | 130764 | -1000000
4 | 18 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.7122 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12011.5 | 0 | 12011.5 | 134063 | 0 | 44 | 46 | 134063 | -1000000
4 | 18 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.4168 | 0 | 5.9324 | 12.9754 | 0 | 0 | 0 | 3.6 | 129.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14697.3 | 0 | 14697.3 | 188962 | -8544.7 | 42 | 44 | 188962 | -1008544.7
4 | 18 | 6 | 2 | 47.1923 | 0 | 140.608 | 0 | 23.5906 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 237.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39994.3 | 0 | 39994.3 | 325794 | -117891 | 43 | 45 | 325794 | -1117891
4 | 18 | 7 | 2 | 39.4662 | 0 | 168.222 | 0 | 30.4723 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43883.3 | 0 | 43883.3 | 444677 | -224034 | 42 | 45 | 444677 | -1224034
4 | 18 | 8 | 2 | 39.7301 | 0 | 173.795 | 0 | 32.6608 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55556.3 | 0 | 55556.3 | 465284 | -178139 | 41 | 46 | 465284 | -1178139
4 | 18 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 34.2957 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86691.5 | 0 | 86691.5 | 476379 | -168982 | 41 | 47 | 476379 | -1168982
4 | 18 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 33.2206 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88636.9 | 0 | 88636.9 | 446443 | -127914 | 42 | 50 | 446443 | -1127914
4 | 18 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 32.0793 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88636.2 | 0 | 88636.2 | 436877 | -84406 | 45 | 55 | 436877 | -1084406
4 | 18 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 29.3489 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88635.1 | 0 | 88635.1 | 433317 | -67588.7 | 44 | 55 | 433317 | -1067588.7
4 | 18 | 13 | 2 | 41.2772 | 0 | 165.698 | 0 | 32.3978 | 0 | 6.332 | 19.2205 | 0 | 0 | 0 | 0 | 264.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88633.9 | 0 | 88633.9 | 507170 | -35711.7 | 45 | 59 | 507170 | -1035711.7
4 | 18 | 14 | 2 | 40.6816 | 0 | 172.702 | 0 | 32.9907 | 0 | 6.332 | 19.5081 | 0 | 0 | 0 | 0 | 272.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86686.8 | 0 | 86686.8 | 522881 | -29567.5 | 44 | 56 | 522881 | -1029567.5
4 | 18 | 15 | 2 | 40.5844 | 0 | 173.986 | 0 | 35.4871 | 0 | 6.332 | 19.9343 | 0 | 0 | 0 | 0 | 276.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78901.5 | 0 | 78901.5 | 557385 | -17516.2 | 45 | 58 | 557385 | -1017516.2
4 | 18 | 16 | 2 | 40.3258 | 0 | 169.782 | 0 | 36.134 | 0 | 6.332 | 19.9238 | 0 | 0 | 0 | 0 | 272.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65278.2 | 0 | 65278.2 | 563097 | -18616 | 46 | 59 | 563097 | -1018616
4 | 18 | 17 | 2 | 35.4984 | 0 | 152.497 | 0 | 30.2127 | 0 | 6.332 | 19.7181 | 0 | 0 | 0 | 2 | 246.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49709.6 | 0 | 49709.6 | 468775 | -16555.3 | 44 | 57 | 468775 | -1016555.3
4 | 18 | 18 | 2 | 25.0739 | 0 | 93.4203 | 0 | 21.8434 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 171.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30249.9 | 0 | 30249.9 | 334415 | -53446.1 | 43 | 54 | 334415 | -1053446.1
4 | 18 | 19 | 2 | 21.8829 | 0 | 62.7906 | 0 | 9.2161 | 0 | 5.4909 | 8.818 | 0 | 0 | 0 | 7.2 | 115.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21493.7 | 0 | 21493.7 | 186351 | 0 | 40 | 49 | 186351 | -1000000
4 | 18 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.2312 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 7.2 | 103.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20522.1 | 0 | 20522.1 | 166933 | 0 | 39 | 47 | 166933 | -1000000
4 | 18 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.6102 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12733.4 | 0 | 12733.4 | 153436 | 0 | 39 | 45 | 153436 | -1000000
4 | 18 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.0924 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12422.8 | 0 | 12422.8 | 142141 | 0 | 37 | 43 | 142141 | -1000000
4 | 18 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 9.9908 | 0 | 5.8977 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10789.3 | 0 | 10789.3 | 137194 | -9003.49 | 35 | 40 | 137194 | -1009003.49
4 | 18 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.7824 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10790.8 | 0 | 10790.8 | 135515 | 0 | 33 | 37 | 135515 | -1000000
4 | 19 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3499 | 0 | 5.9014 | 12.8287 | 0 | 0 | 0 | 4.8 | 88.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10793.1 | 0 | 10793.1 | 134504 | -17279.7 | 31 | 35 | 134504 | -1017279.7
4 | 19 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.6465 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 4.8 | 86.3992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10795.2 | 0 | 10795.2 | 154794 | -7547.86 | 31 | 34 | 154794 | -1007547.86
4 | 19 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 8.1822 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.4237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10797.3 | 0 | 10797.3 | 166375 | -16323.7 | 30 | 33 | 166375 | -1016323.7
4 | 19 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.7871 | 0 | 5.9142 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12005.9 | 0 | 12005.9 | 165891 | -17710.1 | 28 | 32 | 165891 | -1017710.1
4 | 19 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 13.9896 | 0 | 5.9708 | 17.5105 | 0 | 0 | 0 | 3.6 | 135.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14693.8 | 0 | 14693.8 | 211313 | -14550 | 27 | 30 | 211313 | -1014550
4 | 19 | 6 | 3 | 45.7985 | 0 | 140.608 | 0 | 23.0132 | 0 | 6.2889 | 19.0363 | 0 | 0 | 0 | 1.2 | 235.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39992.4 | 0 | 39992.4 | 325980 | -409549 | 27 | 30 | 325980 | -1409549
4 | 19 | 7 | 3 | 39.4274 | 0 | 168.222 | 0 | 26.9892 | 0 | 6.3043 | 19.0363 | 0 | 0 | 0 | 0 | 259.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43882.5 | 0 | 43882.5 | 388114 | -369868 | 30 | 33 | 388114 | -1369868
4 | 19 | 8 | 3 | 39.9107 | 0 | 173.795 | 0 | 25.8441 | 0 | 6.3243 | 19.0363 | 0 | 0 | 0 | 0 | 264.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55555.4 | 0 | 55555.4 | 406438 | -275760 | 31 | 35 | 406438 | -1275760
4 | 19 | 9 | 3 | 40.6581 | 0 | 172.186 | 0 | 30.0259 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86689.5 | 0 | 86689.5 | 448210 | -235276 | 36 | 41 | 448210 | -1235276
4 | 19 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 31.6656 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88634.7 | 0 | 88634.7 | 454367 | -204067 | 39 | 45 | 454367 | -1204067
4 | 19 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 33.2178 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88633.4 | 0 | 88633.4 | 451139 | -159986 | 42 | 49 | 451139 | -1159986
4 | 19 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 31.9984 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88632.4 | 0 | 88632.4 | 417726 | -100248 | 45 | 53 | 417726 | -1100248
4 | 19 | 13 | 3 | 41.2864 | 0 | 165.698 | 0 | 34.1964 | 0 | 6.332 | 19.0478 | 0 | 0 | 0 | 0 | 266.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88631 | 0 | 88631 | 490743 | -68478.3 | 47 | 56 | 490743 | -1068478.3
4 | 19 | 14 | 3 | 40.6377 | 0 | 172.702 | 0 | 31.9868 | 0 | 6.332 | 19.1288 | 0 | 0 | 0 | 0 | 270.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86683.6 | 0 | 86683.6 | 503251 | -33103.6 | 48 | 58 | 503251 | -1033103.6
4 | 19 | 15 | 3 | 40.5897 | 0 | 173.986 | 0 | 35.142 | 0 | 6.332 | 19.5764 | 0 | 0 | 0 | 0 | 275.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78898.3 | 0 | 78898.3 | 548272 | -19688.6 | 50 | 60 | 548272 | -1019688.6
4 | 19 | 16 | 3 | 40.3227 | 0 | 169.782 | 0 | 38.8421 | 0 | 6.332 | 19.7693 | 0 | 0 | 0 | 0 | 275.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65275.1 | 0 | 65275.1 | 579998 | -17861.8 | 51 | 62 | 579998 | -1017861.8
4 | 19 | 17 | 3 | 35.4979 | 0 | 152.497 | 0 | 34.6431 | 0 | 6.332 | 19.7594 | 0 | 0 | 0 | 2 | 250.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49706.5 | 0 | 49706.5 | 522972 | -15447.8 | 51 | 62 | 522972 | -1015447.8
4 | 19 | 18 | 3 | 25.0294 | 0 | 93.4203 | 0 | 22.5671 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 171.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30246.9 | 0 | 30246.9 | 349703 | -18006.2 | 51 | 60 | 349703 | -1018006.2
4 | 19 | 19 | 3 | 21.5697 | 0 | 62.7906 | 0 | 9.2838 | 0 | 5.492 | 8.818 | 0 | 0 | 0 | 7.2 | 115.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21490.6 | 0 | 21490.6 | 187598 | 0 | 50 | 58 | 187598 | -1000000
4 | 19 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.2734 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 7.2 | 103.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20519 | 0 | 20519 | 167849 | 0 | 49 | 56 | 167849 | -1000000
4 | 19 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.6588 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12729.4 | 0 | 12729.4 | 154503 | 0 | 49 | 55 | 154503 | -1000000
4 | 19 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.1468 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12418.2 | 0 | 12418.2 | 143334 | 0 | 48 | 53 | 143334 | -1000000
4 | 19 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.9158 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10784.1 | 0 | 10784.1 | 138382 | 0 | 47 | 52 | 138382 | -1000000
4 | 19 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8468 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10785.5 | 0 | 10785.5 | 136930 | 0 | 47 | 51 | 136930 | -1000000
4 | 20 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.1881 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10786.9 | 0 | 10786.9 | 135865 | -6935.79 | 46 | 50 | 135865 | -1006935.79
4 | 20 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7582 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10788.3 | 0 | 10788.3 | 135000 | 0 | 46 | 50 | 135000 | -1000000
4 | 20 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.5054 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10789.5 | 0 | 10789.5 | 134298 | -9112.37 | 47 | 51 | 134298 | -1009112.37
4 | 20 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.854 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11997.2 | 0 | 11997.2 | 137160 | 0 | 47 | 49 | 137160 | -1000000
4 | 20 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 8.9403 | 0 | 5.9053 | 12.9754 | 0 | 0 | 0 | 3.6 | 125.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14683.6 | 0 | 14683.6 | 183553 | -2155.08 | 47 | 49 | 183553 | -1002155.08
4 | 20 | 6 | 4 | 48.1498 | 0 | 140.608 | 0 | 24.1197 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 239.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39980.6 | 0 | 39980.6 | 329482 | -78914.9 | 50 | 52 | 329482 | -1078914.9
4 | 20 | 7 | 4 | 46.7695 | 0 | 168.222 | 0 | 34.0739 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43869.5 | 0 | 43869.5 | 452265 | -108471 | 51 | 53 | 452265 | -1108471
4 | 20 | 8 | 4 | 39.6811 | 0 | 173.795 | 0 | 31.8817 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55545.7 | 0 | 55545.7 | 481047 | -81828.7 | 51 | 53 | 481047 | -1081828.7
4 | 20 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 35.5864 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86680.5 | 0 | 86680.5 | 523286 | -54422.2 | 54 | 57 | 523286 | -1054422.2
4 | 20 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 37.1942 | 0 | 6.332 | 19.2944 | 0 | 0 | 0 | 0 | 267.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88625.8 | 0 | 88625.8 | 555814 | -22017.7 | 57 | 62 | 555814 | -1022017.7
4 | 20 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 37.8641 | 0 | 6.332 | 19.3121 | 0 | 0 | 0 | 0 | 253.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88625 | 0 | 88625 | 549291 | -14408.7 | 57 | 64 | 549291 | -1014408.7
4 | 20 | 12 | 4 | 39.791 | 0 | 150.207 | 0 | 43.5154 | 0 | 6.332 | 19.429 | 0 | 0 | 0 | 0 | 259.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88624.4 | 0 | 88624.4 | 615335 | -10875 | 59 | 67 | 615335 | -1010875
4 | 20 | 13 | 4 | 41.2465 | 0 | 165.698 | 0 | 61.3113 | 0 | 6.332 | 19.99 | 0 | 0 | 0 | 0 | 294.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88623.9 | 0 | 88623.9 | 814957 | -9213.53 | 62 | 73 | 814957 | -1009213.53
4 | 20 | 14 | 4 | 40.634 | 0 | 172.702 | 0 | 44.7065 | 0 | 6.332 | 20.5518 | 0 | 0 | 0 | 0 | 284.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86677.3 | 0 | 86677.3 | 880358 | -9087.78 | 62 | 73 | 880358 | -1009087.78
4 | 20 | 15 | 4 | 40.7488 | 0 | 173.986 | 0 | 42.7548 | 0 | 6.332 | 20.6256 | 0 | 0 | 0 | 0 | 284.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78892.2 | 0 | 78892.2 | 874029 | -8630.7 | 61 | 70 | 874029 | -1008630.7
4 | 20 | 16 | 4 | 41.4173 | 0 | 169.782 | 0 | 43.6002 | 0 | 6.332 | 20.6067 | 0 | 0 | 0 | 0 | 281.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65269.2 | 0 | 65269.2 | 851572 | -7802.03 | 60 | 72 | 851572 | -1007802.03
4 | 20 | 17 | 4 | 37.3117 | 0 | 152.497 | 0 | 33.9069 | 0 | 6.332 | 20.177 | 0 | 0 | 0 | 2 | 252.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49700.7 | 0 | 49700.7 | 699641 | -6983.9 | 58 | 69 | 699641 | -1006983.9
4 | 20 | 18 | 4 | 27.4892 | 0 | 93.4203 | 0 | 26.6998 | 0 | 6.332 | 19.1169 | 0 | 0 | 0 | 5.6 | 178.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30241.4 | 0 | 30241.4 | 447310 | -7823.96 | 59 | 61 | 447310 | -1007823.96
4 | 20 | 19 | 4 | 23.2665 | 0 | 62.7906 | 0 | 9.1751 | 0 | 5.4903 | 8.818 | 0 | 0 | 0 | 7.2 | 116.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21485.3 | 0 | 21485.3 | 189235 | 0 | 56 | 60 | 189235 | -1000000
4 | 20 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.3581 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 7.2 | 103.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20513.9 | 0 | 20513.9 | 169708 | 0 | 56 | 58 | 169708 | -1000000
4 | 20 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.731 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12721.7 | 0 | 12721.7 | 156079 | 0 | 55 | 56 | 156079 | -1000000
4 | 20 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2227 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12410.2 | 0 | 12410.2 | 144996 | 0 | 55 | 56 | 144996 | -1000000
4 | 20 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.9922 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10775 | 0 | 10775 | 140054 | 0 | 55 | 55 | 140054 | -1000000
4 | 20 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9137 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776 | 0 | 10776 | 138389 | 0 | 55 | 55 | 138389 | -1000000
4 | 21 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8666 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776.4 | 0 | 10776.4 | 137369 | 0 | 55 | 55 | 137369 | -1000000
4 | 21 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.822 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776.9 | 0 | 10776.9 | 136395 | 0 | 55 | 57 | 136395 | -1000000
4 | 21 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7877 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10777.2 | 0 | 10777.2 | 135647 | 0 | 55 | 57 | 135647 | -1000000
4 | 21 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9172 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11984 | 0 | 11984 | 138543 | 0 | 54 | 57 | 138543 | -1000000
4 | 21 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 9.0162 | 0 | 5.4881 | 8.818 | 0 | 0 | 0 | 3.6 | 121.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14669.9 | 0 | 14669.9 | 185220 | 0 | 53 | 55 | 185220 | -1000000
4 | 21 | 6 | 5 | 46.6097 | 0 | 140.608 | 0 | 29.2283 | 0 | 6.332 | 19.2242 | 0 | 0 | 0 | 1.2 | 243.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39966.3 | 0 | 39966.3 | 376149 | -32935.3 | 53 | 55 | 376149 | -1032935.3
4 | 21 | 7 | 5 | 39.1792 | 0 | 168.222 | 0 | 23.7035 | 0 | 6.332 | 19.0723 | 0 | 0 | 0 | 0 | 256.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43854.8 | 0 | 43854.8 | 506179 | -24059 | 54 | 57 | 506179 | -1024059
4 | 21 | 8 | 5 | 39.672 | 0 | 173.795 | 0 | 38.5466 | 0 | 6.332 | 19.1586 | 0 | 0 | 0 | 0 | 277.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55537.1 | 0 | 55537.1 | 588002 | -19998.6 | 56 | 61 | 588002 | -1019998.6
4 | 21 | 9 | 5 | 41.4175 | 0 | 172.186 | 0 | 41.4978 | 0 | 6.332 | 19.3217 | 0 | 0 | 0 | 0 | 280.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86672.6 | 0 | 86672.6 | 635460 | -14842.2 | 57 | 62 | 635460 | -1014842.2
4 | 21 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 52.4739 | 0 | 6.332 | 19.7314 | 0 | 0 | 0 | 0 | 282.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88618.4 | 0 | 88618.4 | 738505 | -10392.9 | 60 | 67 | 738505 | -1010392.9
4 | 21 | 11 | 5 | 40.7113 | 0 | 149.692 | 0 | 47.4964 | 0 | 6.332 | 19.7712 | 0 | 0 | 0 | 0 | 264.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88617.8 | 0 | 88617.8 | 688659 | -9015.88 | 60 | 67 | 688659 | -1009015.88
4 | 21 | 12 | 5 | 39.7784 | 0 | 150.207 | 0 | 42.6202 | 0 | 6.332 | 19.9825 | 0 | 0 | 0 | 0 | 258.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88617.8 | 0 | 88617.8 | 638807 | -8599.18 | 57 | 65 | 638807 | -1008599.18
4 | 21 | 13 | 5 | 41.2546 | 0 | 165.698 | 0 | 46.0701 | 0 | 6.332 | 20.6076 | 0 | 0 | 0 | 0 | 279.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88617.7 | 0 | 88617.7 | 697655 | -9228.9 | 56 | 64 | 697655 | -1009228.9
4 | 21 | 14 | 5 | 40.7999 | 0 | 172.702 | 0 | 27.1257 | 0 | 6.332 | 20.3241 | 0 | 0 | 0 | 0 | 267.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86671.5 | 0 | 86671.5 | 598178 | -9970.13 | 51 | 58 | 598178 | -1009970.13
4 | 21 | 15 | 5 | 40.9169 | 0 | 173.986 | 0 | 35.169 | 0 | 6.332 | 20.2615 | 0 | 0 | 0 | 0 | 276.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78886.8 | 0 | 78886.8 | 581899 | -10838.7 | 50 | 57 | 581899 | -1010838.7
4 | 21 | 16 | 5 | 41.2803 | 0 | 169.782 | 0 | 34.6884 | 0 | 6.332 | 19.9575 | 0 | 0 | 0 | 0 | 272.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65264.2 | 0 | 65264.2 | 555846 | -12881 | 50 | 56 | 555846 | -1012881
4 | 21 | 17 | 5 | 36.4209 | 0 | 152.497 | 0 | 28.56 | 0 | 6.332 | 19.5225 | 0 | 0 | 0 | 2 | 245.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49696.3 | 0 | 49696.3 | 448931 | -15961.9 | 49 | 54 | 448931 | -1015961.9
4 | 21 | 18 | 5 | 27.2459 | 0 | 93.4203 | 0 | 22.3253 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 173.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30237.3 | 0 | 30237.3 | 345818 | -49923.7 | 48 | 53 | 345818 | -1049923.7
4 | 21 | 19 | 5 | 23.4068 | 0 | 62.7906 | 0 | 9.3552 | 0 | 5.4931 | 8.818 | 0 | 0 | 0 | 7.2 | 117.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21481.7 | 0 | 21481.7 | 189253 | 0 | 48 | 52 | 189253 | -1000000
4 | 21 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.3401 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 7.2 | 103.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20510.8 | 0 | 20510.8 | 169308 | 0 | 47 | 51 | 169308 | -1000000
4 | 21 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.7168 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12719.4 | 0 | 12719.4 | 155770 | 0 | 46 | 50 | 155770 | -1000000
4 | 21 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.2031 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12408.3 | 0 | 12408.3 | 144566 | 0 | 45 | 49 | 144566 | -1000000
4 | 21 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 8.8364 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10774 | 0 | 10774 | 139704 | -5256.62 | 45 | 48 | 139704 | -1005256.62
4 | 21 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.8784 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10775.6 | 0 | 10775.6 | 137610 | 0 | 44 | 47 | 137610 | -1000000
4 | 22 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8281 | 0 | 5.4811 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10777.1 | 0 | 10777.1 | 136526 | 0 | 43 | 46 | 136526 | -1000000
4 | 22 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7882 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10779.2 | 0 | 10779.2 | 135656 | 0 | 43 | 45 | 135656 | -1000000
4 | 22 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.0292 | 0 | 5.8975 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.6824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10780.9 | 0 | 10780.9 | 134669 | -11807.2 | 42 | 43 | 134669 | -1011807.2
4 | 22 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6915 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10782.8 | 0 | 10782.8 | 133536 | 0 | 39 | 40 | 133536 | -1000000
4 | 22 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7564 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 3.6 | 82.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10784.5 | 0 | 10784.5 | 132814 | -16238.9 | 38 | 40 | 132814 | -1016238.9
4 | 22 | 6 | 6 | 6.1914 | 0 | 42.7453 | 0 | 7.679 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 1.2 | 78.5891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10786.4 | 0 | 10786.4 | 155547 | -7200.33 | 37 | 39 | 155547 | -1007200.33
4 | 22 | 7 | 6 | 5.1941 | 0 | 42.7453 | 16.6695 | 0 | 0 | 6.0063 | 18.8896 | 0 | 0 | 0 | 0 | 89.5048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10788.4 | 0 | 10788.4 | 152451 | -336556 | 37 | 38 | 152451 | -1336556
4 | 22 | 8 | 6 | 5.777 | 0 | 42.7453 | 19.9666 | 0 | 0 | 6.167 | 18.8896 | 0 | 0 | 0 | 0 | 93.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10790.5 | 0 | 10790.5 | 171043 | -356370 | 37 | 38 | 171043 | -1356370
4 | 22 | 9 | 6 | 5.9424 | 0 | 42.7453 | 17.1796 | 0 | 0 | 6.0456 | 18.8896 | 0 | 0 | 0 | 0 | 90.8025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10794.1 | 0 | 10794.1 | 170414 | -316571 | 37 | 39 | 170414 | -1316571
4 | 22 | 10 | 6 | 5.737 | 0 | 42.7453 | 16.1256 | 0 | 0 | 6.0059 | 18.8896 | 0 | 0 | 0 | 0 | 89.5033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10794.8 | 0 | 10794.8 | 174068 | -300798 | 37 | 40 | 174068 | -1300798
4 | 22 | 11 | 6 | 5.6692 | 0 | 42.7453 | 15.3099 | 0 | 0 | 5.9798 | 18.8896 | 0 | 0 | 0 | 0 | 88.5937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10796.4 | 0 | 10796.4 | 179683 | -288780 | 38 | 41 | 179683 | -1288780
4 | 22 | 12 | 6 | 5.5916 | 0 | 42.7453 | 15.0256 | 0 | 0 | 5.9709 | 18.8896 | 0 | 0 | 0 | 0 | 88.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10797.6 | 0 | 10797.6 | 140507 | -289731 | 36 | 36 | 140507 | -1289731
4 | 22 | 13 | 6 | 5.6013 | 0 | 42.7453 | 15.0063 | 0 | 0 | 5.9747 | 18.8896 | 0 | 0 | 0 | 0 | 88.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10798.8 | 0 | 10798.8 | 168142 | -285461 | 37 | 40 | 168142 | -1285461
4 | 22 | 14 | 6 | 5.5916 | 0 | 42.7453 | 0 | 7.5305 | 0 | 6.6984 | 12.8287 | 0 | 0 | 0 | 0 | 75.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10799.9 | 0 | 10799.9 | 132721 | 0 | 37 | 40 | 132721 | -1000000
4 | 22 | 15 | 6 | 5.7321 | 0 | 42.7453 | 0 | 7.1018 | 0 | 6.5017 | 8.818 | 0 | 0 | 0 | 0 | 70.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.1 | 0 | 10801.1 | 126146 | 0 | 37 | 40 | 126146 | -1000000
4 | 22 | 16 | 6 | 5.9799 | 0 | 42.7453 | 0 | 10.5882 | 0 | 5.8977 | 12.8287 | 0 | 0 | 0 | 0 | 78.0397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10801.7 | 0 | 10801.7 | 125777 | -18428.9 | 37 | 40 | 125777 | -1018428.9
4 | 22 | 17 | 6 | 6.1934 | 0 | 42.7453 | 0 | 6.3183 | 0 | 6.3072 | 12.8287 | 0 | 0 | 0 | 2 | 76.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10803 | 0 | 10803 | 125380 | -6776.38 | 37 | 40 | 125380 | -1006776.38
4 | 22 | 18 | 6 | 6.8808 | 0 | 42.7453 | 0 | 10.2739 | 0 | 5.9002 | 14.8767 | 0 | 0 | 0 | 5.6 | 86.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10804.2 | 0 | 10804.2 | 148890 | -14160.9 | 36 | 40 | 148890 | -1014160.9
4 | 22 | 19 | 6 | 8.3513 | 0 | 42.7453 | 0 | 9.7648 | 0 | 5.8981 | 14.8767 | 0 | 0 | 0 | 7.2 | 88.8361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10805.9 | 0 | 10805.9 | 143599 | -12645.2 | 35 | 40 | 143599 | -1012645.2
4 | 22 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7683 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10807.5 | 0 | 10807.5 | 155785 | -17846.8 | 35 | 40 | 155785 | -1017846.8
4 | 22 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6113 | 0 | 5.9025 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.6201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10809.4 | 0 | 10809.4 | 152782 | -19624.6 | 35 | 39 | 152782 | -1019624.6
4 | 22 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7399 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10811.7 | 0 | 10811.7 | 150925 | -21857.4 | 35 | 39 | 150925 | -1021857.4
4 | 22 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9161 | 0 | 5.9029 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.3253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10814.4 | 0 | 10814.4 | 149105 | -24588.2 | 34 | 37 | 149105 | -1024588.2
4 | 22 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 10.9006 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.33 | 0 | 4006.33 | 146709 | -27731.3 | 31 | 35 | 146709 | -1027731.3
4 | 23 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.4166 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.67 | 0 | 4008.67 | 144950 | -32259.5 | 30 | 34 | 144950 | -1032259.5
4 | 23 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.6489 | 0 | 5.905 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.5684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4011.14 | 0 | 4011.14 | 143455 | -40008.3 | 31 | 34 | 143455 | -1040008.3
4 | 23 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.655 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4013.7 | 0 | 4013.7 | 142203 | -47632.7 | 31 | 34 | 142203 | -1047632.7
4 | 23 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.5645 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4016.31 | 0 | 4016.31 | 141186 | -55041.4 | 31 | 34 | 141186 | -1055041.4
4 | 23 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.4931 | 0 | 5.9034 | 17.3638 | 0 | 0 | 0 | 3.6 | 86.2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.81 | 0 | 4018.81 | 140391 | -62527 | 31 | 34 | 140391 | -1062527
4 | 23 | 6 | 7 | 4.8529 | 0 | 42.7453 | 0 | 11.4236 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 1.2 | 83.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.22 | 0 | 4021.22 | 139658 | -64198.4 | 32 | 35 | 139658 | -1064198.4
4 | 23 | 7 | 7 | 4.0826 | 0 | 42.7453 | 0 | 11.4057 | 0 | 5.9027 | 17.3638 | 0 | 0 | 0 | 0 | 81.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023.49 | 0 | 4023.49 | 139451 | -64689.6 | 32 | 35 | 139451 | -1064689.6
4 | 23 | 8 | 7 | 4.0908 | 0 | 42.7453 | 0 | 11.3783 | 0 | 5.9024 | 17.3638 | 0 | 0 | 0 | 0 | 81.4806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4025.7 | 0 | 4025.7 | 138957 | -55318.2 | 33 | 36 | 138957 | -1055318.2
4 | 23 | 9 | 7 | 4.5334 | 0 | 42.7453 | 0 | 11.491 | 0 | 5.9034 | 17.3638 | 0 | 0 | 0 | 0 | 82.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4027.81 | 0 | 4027.81 | 140526 | -49522.4 | 33 | 36 | 140526 | -1049522.4
4 | 23 | 10 | 7 | 4.3773 | 0 | 42.7453 | 0 | 10.8145 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 0 | 81.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4029.79 | 0 | 4029.79 | 139542 | -37587.4 | 35 | 40 | 139542 | -1037587.4
4 | 23 | 11 | 7 | 4.3054 | 0 | 42.7453 | 0 | 11.0154 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 0 | 81.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4031.44 | 0 | 4031.44 | 142919 | -32060.6 | 37 | 42 | 142919 | -1032060.6
4 | 23 | 12 | 7 | 4.2664 | 0 | 42.7453 | 0 | 10.0696 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 80.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.95 | 0 | 4032.95 | 140657 | -26339.6 | 37 | 43 | 140657 | -1026339.6
4 | 23 | 13 | 7 | 4.1459 | 0 | 42.7453 | 0 | 9.9566 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 0 | 80.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4034.3 | 0 | 4034.3 | 142997 | -23765.8 | 40 | 47 | 142997 | -1023765.8
4 | 23 | 14 | 7 | 4.1483 | 0 | 42.7453 | 0 | 9.6746 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 0 | 79.8298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.38 | 0 | 4035.38 | 143303 | -20038 | 40 | 50 | 143303 | -1020038
4 | 23 | 15 | 7 | 4.1494 | 0 | 42.7453 | 0 | 8.9787 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 76.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.32 | 0 | 4036.32 | 133150 | -11323.7 | 42 | 53 | 133150 | -1011323.7
4 | 23 | 16 | 7 | 4.1489 | 0 | 42.7453 | 0 | 8.748 | 0 | 5.8969 | 15.3158 | 0 | 0 | 0 | 0 | 76.8549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.92 | 0 | 4036.92 | 131408 | -10654.8 | 42 | 55 | 131408 | -1010654.8
4 | 23 | 17 | 7 | 4.1494 | 0 | 42.7453 | 0 | 7.8391 | 0 | 5.9001 | 12.8287 | 0 | 0 | 0 | 2 | 75.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037 | 0 | 4037 | 119487 | -6270.46 | 41 | 55 | 119487 | -1006270.46
4 | 23 | 18 | 7 | 4.1601 | 0 | 42.7453 | 0 | 9.9331 | 0 | 5.899 | 13.3531 | 0 | 0 | 0 | 5.6 | 81.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.08 | 0 | 4037.08 | 147642 | -2729.47 | 41 | 53 | 147642 | -1002729.47
4 | 23 | 19 | 7 | 5.9575 | 0 | 42.7453 | 0 | 10.241 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.62 | 0 | 4037.62 | 144501 | -16385.4 | 38 | 49 | 144501 | -1016385.4
4 | 23 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5185 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.95 | 0 | 4037.95 | 141518 | -16169 | 33 | 39 | 141518 | -1016169
4 | 23 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.4011 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.3 | 0 | 4039.3 | 138715 | -26541.8 | 32 | 38 | 138715 | -1026541.8
4 | 23 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4055 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.4765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.56 | 0 | 4040.56 | 137331 | -37350.5 | 32 | 36 | 137331 | -1037350.5
4 | 23 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1661 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.4363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4042.51 | 0 | 4042.51 | 135790 | -41761.1 | 32 | 37 | 135790 | -1041761.1
4 | 23 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 11.8177 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10854.7 | 0 | 10854.7 | 142272 | -53352 | 29 | 34 | 142272 | -1053352
4 | 24 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.5084 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10856.6 | 0 | 10856.6 | 134771 | -49601.9 | 30 | 36 | 134771 | -1049601.9
4 | 24 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 12.0663 | 0 | 5.9077 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10857.7 | 0 | 10857.7 | 143853 | -67723.5 | 28 | 33 | 143853 | -1067723.5
4 | 24 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.3703 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10858.5 | 0 | 10858.5 | 133647 | -63507.6 | 28 | 33 | 133647 | -1063507.6
4 | 24 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.6996 | 0 | 5.8997 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12066.5 | 0 | 12066.5 | 138562 | -86036.3 | 24 | 27 | 138562 | -1086036.3
4 | 24 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.9375 | 0 | 5.9345 | 17.5105 | 0 | 0 | 0 | 3.6 | 134.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14752.6 | 0 | 14752.6 | 183867 | -70400.9 | 24 | 26 | 183867 | -1070400.9
4 | 24 | 6 | 1 | 44.3548 | 0 | 140.608 | 36.8396 | 0 | 0 | 7.7016 | 19.0363 | 0 | 0 | 0 | 1.2 | 249.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40049.4 | 0 | 40049.4 | 314107 | -663051 | 28 | 30 | 314107 | -1663051
4 | 24 | 7 | 1 | 39.1264 | 0 | 168.222 | 30.3574 | 0 | 0 | 20.8938 | 19.0363 | 0 | 0 | 0 | 0 | 277.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43938.5 | 0 | 43938.5 | 376611 | -539877 | 31 | 35 | 376611 | -1539877
4 | 24 | 8 | 1 | 39.7305 | 0 | 173.795 | 0 | 27.4955 | 0 | 6.2928 | 19.0363 | 0 | 0 | 0 | 0 | 266.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55600.7 | 0 | 55600.7 | 413627 | -386801 | 32 | 38 | 413627 | -1386801
4 | 24 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 31.6392 | 0 | 6.3223 | 19.0363 | 0 | 0 | 0 | 0 | 269.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86731.5 | 0 | 86731.5 | 455251 | -306068 | 36 | 45 | 455251 | -1306068
4 | 24 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 30.8625 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88674.9 | 0 | 88674.9 | 422896 | -221582 | 38 | 50 | 422896 | -1221582
4 | 24 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 30.8776 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88670.2 | 0 | 88670.2 | 411094 | -180998 | 40 | 52 | 411094 | -1180998
4 | 24 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 29.5825 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88667.2 | 0 | 88667.2 | 388292 | -137625 | 40 | 54 | 388292 | -1137625
4 | 24 | 13 | 1 | 41.2604 | 0 | 165.698 | 0 | 32.3247 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88664 | 0 | 88664 | 434595 | -88323 | 41 | 58 | 434595 | -1088323
4 | 24 | 14 | 1 | 40.63 | 0 | 172.702 | 0 | 30.8885 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 269.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86714.6 | 0 | 86714.6 | 468833 | -54579.6 | 43 | 60 | 468833 | -1054579.6
4 | 24 | 15 | 1 | 40.5449 | 0 | 173.986 | 0 | 30.9826 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78926.9 | 0 | 78926.9 | 477751 | -32419.6 | 43 | 61 | 477751 | -1032419.6
4 | 24 | 16 | 1 | 40.297 | 0 | 169.782 | 0 | 30.2718 | 0 | 6.332 | 19.0773 | 0 | 0 | 0 | 0 | 265.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65301.2 | 0 | 65301.2 | 473716 | -27342.9 | 45 | 61 | 473716 | -1027342.9
4 | 24 | 17 | 1 | 35.4897 | 0 | 152.497 | 0 | 28.2016 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2 | 243.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49730.9 | 0 | 49730.9 | 436332 | -26151.1 | 45 | 61 | 436332 | -1026151.1
4 | 24 | 18 | 1 | 24.6497 | 0 | 93.4203 | 0 | 21.3525 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 5.6 | 170.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30270 | 0 | 30270 | 325521 | -63942.5 | 45 | 61 | 325521 | -1063942.5
4 | 24 | 19 | 1 | 21.1412 | 0 | 62.7906 | 0 | 8.7374 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 114.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21512.7 | 0 | 21512.7 | 181553 | 0 | 43 | 57 | 181553 | -1000000
4 | 24 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.0051 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 102.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20540.1 | 0 | 20540.1 | 161979 | 0 | 43 | 56 | 161979 | -1000000
4 | 24 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.4011 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12754.7 | 0 | 12754.7 | 148866 | 0 | 42 | 55 | 148866 | -1000000
4 | 24 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.9081 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12444.1 | 0 | 12444.1 | 138117 | 0 | 43 | 55 | 138117 | -1000000
4 | 24 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.6868 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 5.6 | 79.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10810.7 | 0 | 10810.7 | 133373 | 0 | 42 | 53 | 133373 | -1000000
4 | 24 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6249 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10812.3 | 0 | 10812.3 | 132075 | 0 | 42 | 53 | 132075 | -1000000
4 | 25 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.8024 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10813.6 | 0 | 10813.6 | 131324 | -6669.81 | 42 | 53 | 131324 | -1006669.81
4 | 25 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5567 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10814.8 | 0 | 10814.8 | 130592 | 0 | 41 | 52 | 130592 | -1000000
4 | 25 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.7754 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10815.7 | 0 | 10815.7 | 130072 | -8133.96 | 41 | 52 | 130072 | -1008133.96
4 | 25 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.676 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12023.1 | 0 | 12023.1 | 133268 | 0 | 42 | 51 | 133268 | -1000000
4 | 25 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.164 | 0 | 5.9243 | 12.9754 | 0 | 0 | 0 | 3.6 | 128.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14709.2 | 0 | 14709.2 | 179994 | -9878.59 | 42 | 51 | 179994 | -1009878.59
4 | 25 | 6 | 2 | 46.8135 | 0 | 140.608 | 0 | 24.3994 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 238.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40006 | 0 | 40006 | 325439 | -153959 | 43 | 52 | 325439 | -1153959
4 | 25 | 7 | 2 | 39.3901 | 0 | 168.222 | 0 | 31.5104 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43894.7 | 0 | 43894.7 | 425449 | -169849 | 43 | 52 | 425449 | -1169849
4 | 25 | 8 | 2 | 39.6631 | 0 | 173.795 | 0 | 31.7469 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55565.5 | 0 | 55565.5 | 444729 | -82336.7 | 46 | 56 | 444729 | -1082336.7
4 | 25 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 34.017 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86697.5 | 0 | 86697.5 | 463664 | -54274.3 | 47 | 59 | 463664 | -1054274.3
4 | 25 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 32.8085 | 0 | 6.332 | 19.13 | 0 | 0 | 0 | 0 | 262.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88641.7 | 0 | 88641.7 | 480080 | -27102.8 | 50 | 63 | 480080 | -1027102.8
4 | 25 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 32.0193 | 0 | 6.332 | 19.1848 | 0 | 0 | 0 | 0 | 247.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88639.8 | 0 | 88639.8 | 477656 | -19692.1 | 51 | 64 | 477656 | -1019692.1
4 | 25 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 40.144 | 0 | 6.332 | 19.2898 | 0 | 0 | 0 | 0 | 255.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88638.3 | 0 | 88638.3 | 566658 | -16569.9 | 53 | 67 | 566658 | -1016569.9
4 | 25 | 13 | 2 | 41.2647 | 0 | 165.698 | 0 | 44.5055 | 0 | 6.332 | 20.0236 | 0 | 0 | 0 | 0 | 277.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88637.2 | 0 | 88637.2 | 634043 | -13368.3 | 53 | 68 | 634043 | -1013368.3
4 | 25 | 14 | 2 | 40.6608 | 0 | 172.702 | 0 | 50.9607 | 0 | 6.332 | 20.2977 | 0 | 0 | 0 | 0 | 290.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86690 | 0 | 86690 | 718830 | -11703.9 | 55 | 70 | 718830 | -1011703.9
4 | 25 | 15 | 2 | 40.5593 | 0 | 173.986 | 0 | 46.6346 | 0 | 25.335 | 20.6648 | 0 | 0 | 0 | 0 | 307.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78904.5 | 0 | 78904.5 | 809125 | -12518.9 | 57 | 73 | 809125 | -1012518.9
4 | 25 | 16 | 2 | 40.3056 | 0 | 169.782 | 0 | 45.4585 | 0 | 25.335 | 20.7584 | 0 | 0 | 0 | 0 | 301.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65281.6 | 0 | 65281.6 | 805540 | -11874.7 | 57 | 74 | 805540 | -1011874.7
4 | 25 | 17 | 2 | 35.4857 | 0 | 152.497 | 0 | 38.3531 | 0 | 25.335 | 20.252 | 0 | 0 | 0 | 2 | 273.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49712.9 | 0 | 49712.9 | 742616 | -9793.18 | 57 | 74 | 742616 | -1009793.18
4 | 25 | 18 | 2 | 24.6107 | 0 | 93.4203 | 0 | 25.5327 | 0 | 6.332 | 19.243 | 0 | 0 | 0 | 5.6 | 174.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30252.6 | 0 | 30252.6 | 504812 | -14863 | 57 | 73 | 504812 | -1014863
4 | 25 | 19 | 2 | 21.0207 | 0 | 62.7906 | 0 | 7.8877 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 7.2 | 113.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21495.8 | 0 | 21495.8 | 188221 | 0 | 54 | 66 | 188221 | -1000000
4 | 25 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 6.7488 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 7.2 | 101.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20523.9 | 0 | 20523.9 | 168158 | 0 | 51 | 59 | 168158 | -1000000
4 | 25 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.6855 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12733.2 | 0 | 12733.2 | 155091 | 0 | 52 | 58 | 155091 | -1000000
4 | 25 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.1694 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12421.2 | 0 | 12421.2 | 143827 | 0 | 51 | 55 | 143827 | -1000000
4 | 25 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9351 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10786.4 | 0 | 10786.4 | 138802 | 0 | 49 | 52 | 138802 | -1000000
4 | 25 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8605 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10786.9 | 0 | 10786.9 | 137228 | 0 | 48 | 50 | 137228 | -1000000
4 | 26 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.814 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10787.5 | 0 | 10787.5 | 136218 | 0 | 47 | 49 | 136218 | -1000000
4 | 26 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7765 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10788.1 | 0 | 10788.1 | 135400 | 0 | 47 | 48 | 135400 | -1000000
4 | 26 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7314 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10788.5 | 0 | 10788.5 | 134412 | 0 | 46 | 47 | 134412 | -1000000
4 | 26 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.8554 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11995.4 | 0 | 11995.4 | 137189 | 0 | 45 | 46 | 137189 | -1000000
4 | 26 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.9443 | 0 | 5.4872 | 8.818 | 0 | 0 | 0 | 3.6 | 121.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14681.1 | 0 | 14681.1 | 183640 | 0 | 45 | 45 | 183640 | -1000000
4 | 26 | 6 | 3 | 44.2504 | 0 | 140.608 | 0 | 23.9659 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 235.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39977.4 | 0 | 39977.4 | 328908 | -48406.3 | 46 | 47 | 328908 | -1048406.3
4 | 26 | 7 | 3 | 39.1304 | 0 | 168.222 | 0 | 32.019 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43865.7 | 0 | 43865.7 | 473654 | -77280.6 | 48 | 51 | 473654 | -1077280.6
4 | 26 | 8 | 3 | 39.7798 | 0 | 173.795 | 0 | 32.5499 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55545.1 | 0 | 55545.1 | 515557 | -41105 | 51 | 57 | 515557 | -1041105
4 | 26 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 42.6264 | 0 | 6.332 | 19.3981 | 0 | 0 | 0 | 0 | 281.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86680 | 0 | 86680 | 616933 | -15382.9 | 55 | 64 | 616933 | -1015382.9
4 | 26 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 55.0921 | 0 | 6.332 | 20.2484 | 0 | 0 | 0 | 0 | 285.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88625.2 | 0 | 88625.2 | 740250 | -11532.2 | 58 | 70 | 740250 | -1011532.2
4 | 26 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 60.3438 | 0 | 6.332 | 20.2939 | 0 | 0 | 0 | 0 | 277.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88624.3 | 0 | 88624.3 | 772347 | -8927.79 | 60 | 76 | 772347 | -1008927.79
4 | 26 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 65.7613 | 0 | 6.332 | 20.2263 | 0 | 0 | 0 | 0 | 282.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88623.7 | 0 | 88623.7 | 927057 | -23136.7 | 62 | 78 | 927057 | -1023136.7
4 | 26 | 13 | 3 | 41.2585 | 0 | 165.698 | 0 | 58.3743 | 0 | 25.335 | 21.497 | 0 | 0 | 0 | 0 | 312.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88624.1 | 0 | 88624.1 | 1008010 | -7221.23 | 62 | 79 | 1008010 | -1007221.23
4 | 26 | 14 | 3 | 40.6549 | 0 | 172.702 | 0 | 63.0615 | 0 | 25.335 | 21.7957 | 0 | 0 | 0 | 0 | 323.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86678.2 | 0 | 86678.2 | 1084730 | -6446.93 | 63 | 81 | 1084730 | -1006446.93
4 | 26 | 15 | 3 | 40.5641 | 0 | 173.986 | 0 | 68.4998 | 0 | 25.335 | 21.8847 | 0 | 0 | 0 | 0 | 330.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78894.1 | 0 | 78894.1 | 1178750 | -7719.72 | 64 | 81 | 1178750 | -1007719.72
4 | 26 | 16 | 3 | 40.2977 | 0 | 169.782 | 0 | 66.3681 | 0 | 25.335 | 21.7905 | 0 | 0 | 0 | 0 | 323.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65271.6 | 0 | 65271.6 | 1163830 | -12156.5 | 64 | 81 | 1163830 | -1012156.5
4 | 26 | 17 | 3 | 35.4843 | 0 | 152.497 | 0 | 58.3845 | 0 | 25.335 | 21.2702 | 0 | 0 | 0 | 2 | 294.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49703.3 | 0 | 49703.3 | 1083840 | -16955.4 | 64 | 79 | 1083840 | -1016955.4
4 | 26 | 18 | 3 | 24.685 | 0 | 93.4203 | 0 | 37.4987 | 0 | 6.332 | 19.7865 | 0 | 0 | 0 | 5.6 | 187.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30243.5 | 0 | 30243.5 | 723599 | -11342.8 | 64 | 77 | 723599 | -1011342.8
4 | 26 | 19 | 3 | 21.1964 | 0 | 62.7906 | 0 | 9.9163 | 0 | 5.5218 | 8.818 | 0 | 0 | 0 | 7.2 | 115.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21486.4 | 0 | 21486.4 | 191111 | 0 | 62 | 73 | 191111 | -1000000
4 | 26 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 7.4484 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 102.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20514.1 | 0 | 20514.1 | 170834 | 0 | 60 | 68 | 170834 | -1000000
4 | 26 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 8.473 | 0 | 5.4867 | 8.818 | 0 | 0 | 0 | 7.2 | 92.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12720.2 | 0 | 12720.2 | 157703 | 0 | 61 | 69 | 157703 | -1000000
4 | 26 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.0435 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12407.3 | 0 | 12407.3 | 146507 | 0 | 60 | 67 | 146507 | -1000000
4 | 26 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.7225 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 79.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10771.5 | 0 | 10771.5 | 141454 | 0 | 59 | 65 | 141454 | -1000000
4 | 26 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8731 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10771.4 | 0 | 10771.4 | 139919 | 0 | 59 | 64 | 139919 | -1000000
4 | 27 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.398 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10771.2 | 0 | 10771.2 | 139071 | 0 | 60 | 65 | 139071 | -1000000
4 | 27 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.4962 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10770.9 | 0 | 10770.9 | 138235 | 0 | 60 | 63 | 138235 | -1000000
4 | 27 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.962 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10770.5 | 0 | 10770.5 | 137033 | 0 | 58 | 63 | 137033 | -1000000
4 | 27 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.5056 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 4.8 | 82.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11976.5 | 0 | 11976.5 | 140014 | 0 | 56 | 61 | 140014 | -1000000
4 | 27 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 8.8247 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 3.6 | 121.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14661.4 | 0 | 14661.4 | 186640 | 0 | 54 | 57 | 186640 | -1000000
4 | 27 | 6 | 4 | 46.3263 | 0 | 140.608 | 0 | 42.0618 | 0 | 6.332 | 19.7922 | 0 | 0 | 0 | 1.2 | 256.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39957 | 0 | 39957 | 615549 | -10510.4 | 56 | 62 | 615549 | -1010510.4
4 | 27 | 7 | 4 | 42.754 | 0 | 168.222 | 0 | 48.5823 | 0 | 6.332 | 19.7417 | 0 | 0 | 0 | 0 | 285.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43845.1 | 0 | 43845.1 | 709022 | -13724.4 | 56 | 64 | 709022 | -1013724.4
4 | 27 | 8 | 4 | 39.7338 | 0 | 173.795 | 0 | 54.7187 | 0 | 6.332 | 20.1871 | 0 | 0 | 0 | 0 | 294.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55532.3 | 0 | 55532.3 | 759185 | -9847.12 | 57 | 68 | 759185 | -1009847.12
4 | 27 | 9 | 4 | 40.6398 | 0 | 172.186 | 0 | 37.9305 | 0 | 6.332 | 20.7436 | 0 | 0 | 0 | 0 | 277.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86668.5 | 0 | 86668.5 | 791740 | -9181.02 | 58 | 66 | 791740 | -1009181.02
4 | 27 | 10 | 4 | 41.3694 | 0 | 163.102 | 0 | 46.3454 | 0 | 6.332 | 20.508 | 0 | 0 | 0 | 0 | 277.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88614.5 | 0 | 88614.5 | 753595 | -8129.06 | 58 | 62 | 753595 | -1008129.06
4 | 27 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 51.7717 | 0 | 6.332 | 21.0317 | 0 | 0 | 0 | 0 | 269.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88614.3 | 0 | 88614.3 | 784898 | -6821.89 | 61 | 67 | 784898 | -1006821.89
4 | 27 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 57.3616 | 0 | 25.335 | 21.2012 | 0 | 0 | 0 | 0 | 293.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88614.4 | 0 | 88614.4 | 956344 | -7460.02 | 63 | 75 | 956344 | -1007460.02
4 | 27 | 13 | 4 | 41.2653 | 0 | 165.698 | 0 | 67.2905 | 0 | 25.335 | 22.6525 | 0 | 0 | 0 | 0 | 322.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88614.7 | 0 | 88614.7 | 1157040 | -4849.29 | 66 | 81 | 1157040 | -1004849.29
4 | 27 | 14 | 4 | 40.9652 | 0 | 172.702 | 0 | 66.7626 | 0 | 25.335 | 22.4622 | 0 | 0 | 0 | 0 | 328.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86669.5 | 0 | 86669.5 | 1158660 | -5227.35 | 66 | 80 | 1158660 | -1005227.35
4 | 27 | 15 | 4 | 40.9006 | 0 | 173.986 | 0 | 68.7519 | 0 | 25.335 | 22.871 | 0 | 0 | 0 | 0 | 331.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78885.8 | 0 | 78885.8 | 1196110 | -4887.94 | 66 | 80 | 1196110 | -1004887.94
4 | 27 | 16 | 4 | 40.3022 | 0 | 169.782 | 0 | 68.5293 | 0 | 25.335 | 23.2635 | 0 | 0 | 0 | 0 | 327.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65262.9 | 0 | 65262.9 | 1211690 | -4106.4 | 66 | 78 | 1211690 | -1004106.4
4 | 27 | 17 | 4 | 35.4906 | 0 | 152.497 | 0 | 60.4981 | 0 | 6.7322 | 22.4127 | 0 | 0 | 0 | 2 | 279.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49694.8 | 0 | 49694.8 | 1166590 | -4063.36 | 66 | 79 | 1166590 | -1004063.36
4 | 27 | 18 | 4 | 24.6091 | 0 | 93.4203 | 0 | 41.21 | 0 | 6.332 | 20.2515 | 0 | 0 | 0 | 5.6 | 191.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30235.7 | 0 | 30235.7 | 794890 | -14884.7 | 65 | 77 | 794890 | -1014884.7
4 | 27 | 19 | 4 | 21.0416 | 0 | 62.7906 | 0 | 10.7168 | 0 | 5.5539 | 8.818 | 0 | 0 | 0 | 7.2 | 116.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21479.1 | 0 | 21479.1 | 192352 | 0 | 64 | 75 | 192352 | -1000000
4 | 27 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.2338 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 7.2 | 103.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20507.4 | 0 | 20507.4 | 172048 | 0 | 63 | 72 | 172048 | -1000000
4 | 27 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7507 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12712.2 | 0 | 12712.2 | 158555 | 0 | 62 | 70 | 158555 | -1000000
4 | 27 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.4539 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12399 | 0 | 12399 | 147746 | 0 | 63 | 69 | 147746 | -1000000
4 | 27 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.4735 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 5.6 | 80.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10762.7 | 0 | 10762.7 | 142635 | 0 | 63 | 69 | 142635 | -1000000
4 | 27 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.7149 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10762.5 | 0 | 10762.5 | 141171 | 0 | 64 | 70 | 141171 | -1000000
4 | 28 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.3942 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10762.3 | 0 | 10762.3 | 140153 | 0 | 64 | 70 | 140153 | -1000000
4 | 28 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0418 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10762.1 | 0 | 10762.1 | 139332 | 0 | 64 | 69 | 139332 | -1000000
4 | 28 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.0391 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10761.8 | 0 | 10761.8 | 138190 | 0 | 62 | 65 | 138190 | -1000000
4 | 28 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.0375 | 0 | 5.4888 | 8.818 | 0 | 0 | 0 | 4.8 | 81.7888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11967.8 | 0 | 11967.8 | 141051 | 0 | 59 | 61 | 141051 | -1000000
4 | 28 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 8.8647 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 3.6 | 121.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14652.8 | 0 | 14652.8 | 187513 | 0 | 56 | 57 | 187513 | -1000000
4 | 28 | 6 | 5 | 45.1529 | 0 | 140.608 | 0 | 42.5973 | 0 | 6.332 | 20.2141 | 0 | 0 | 0 | 1.2 | 256.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39948.6 | 0 | 39948.6 | 658443 | -9409.22 | 57 | 57 | 658443 | -1009409.22
4 | 28 | 7 | 5 | 39.4375 | 0 | 168.222 | 0 | 62.3306 | 0 | 6.332 | 20.2538 | 0 | 0 | 0 | 0 | 296.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43836.6 | 0 | 43836.6 | 889864 | -12344.3 | 61 | 65 | 889864 | -1012344.3
4 | 28 | 8 | 5 | 40.0112 | 0 | 173.795 | 0 | 44.7385 | 0 | 6.332 | 20.7338 | 0 | 0 | 0 | 0 | 285.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55526.4 | 0 | 55526.4 | 912983 | -9553.83 | 62 | 66 | 912983 | -1009553.83
4 | 28 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 48.2752 | 0 | 6.332 | 21.4422 | 0 | 0 | 0 | 0 | 288.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86663.4 | 0 | 86663.4 | 955862 | -7889.68 | 61 | 69 | 955862 | -1007889.68
4 | 28 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 51.1795 | 0 | 10.1665 | 22.1489 | 0 | 0 | 0 | 0 | 287.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88609.7 | 0 | 88609.7 | 1018550 | -8285.28 | 62 | 70 | 1018550 | -1008285.28
4 | 28 | 11 | 5 | 40.9564 | 0 | 149.692 | 0 | 48.3444 | 0 | 25.335 | 22.3446 | 0 | 0 | 0 | 0 | 286.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88611.2 | 0 | 88611.2 | 902453 | -4645.58 | 62 | 73 | 902453 | -1004645.58
4 | 28 | 12 | 5 | 39.7723 | 0 | 150.207 | 0 | 53.2742 | 0 | 25.335 | 22.4737 | 0 | 0 | 0 | 0 | 291.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88611.4 | 0 | 88611.4 | 945456 | -4339.56 | 62 | 76 | 945456 | -1004339.56
4 | 28 | 13 | 5 | 41.2575 | 0 | 165.698 | 0 | 60.6714 | 0 | 25.335 | 23.3115 | 0 | 0 | 0 | 0 | 316.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88610.9 | 0 | 88610.9 | 1110680 | -4428.48 | 63 | 79 | 1110680 | -1004428.48
4 | 28 | 14 | 5 | 40.6596 | 0 | 172.702 | 0 | 63.9217 | 0 | 25.335 | 23.0677 | 0 | 0 | 0 | 0 | 325.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86665.4 | 0 | 86665.4 | 1164470 | -6399.56 | 63 | 79 | 1164470 | -1006399.56
4 | 28 | 15 | 5 | 40.5577 | 0 | 173.986 | 0 | 69.3665 | 0 | 13.6754 | 22.9468 | 0 | 0 | 0 | 0 | 320.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78882.2 | 0 | 78882.2 | 1228960 | -11385.9 | 63 | 81 | 1228960 | -1011385.9
4 | 28 | 16 | 5 | 40.3038 | 0 | 169.782 | 0 | 67.4398 | 0 | 25.335 | 22.4692 | 0 | 0 | 0 | 0 | 325.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65260.5 | 0 | 65260.5 | 1209400 | -20663.6 | 62 | 82 | 1209400 | -1020663.6
4 | 28 | 17 | 5 | 35.4832 | 0 | 152.497 | 0 | 53.3118 | 0 | 8.0258 | 22.3821 | 0 | 0 | 0 | 2 | 273.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49692.9 | 0 | 49692.9 | 1013730 | -15952.5 | 60 | 77 | 1013730 | -1015952.5
4 | 28 | 18 | 5 | 24.9205 | 0 | 93.4203 | 0 | 34.7813 | 0 | 6.332 | 20.7355 | 0 | 0 | 0 | 5.6 | 185.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30233.7 | 0 | 30233.7 | 671341 | -7940.12 | 60 | 76 | 671341 | -1007940.12
4 | 28 | 19 | 5 | 22.7674 | 0 | 62.7906 | 0 | 8.9823 | 0 | 5.4954 | 8.818 | 0 | 0 | 0 | 7.2 | 116.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21477 | 0 | 21477 | 193162 | 0 | 60 | 70 | 193162 | -1000000
4 | 28 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 9.3267 | 0 | 5.5035 | 8.818 | 0 | 0 | 0 | 7.2 | 104.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20504.8 | 0 | 20504.8 | 173098 | 0 | 62 | 71 | 173098 | -1000000
4 | 28 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.089 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 7.2 | 92.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12709.2 | 0 | 12709.2 | 159952 | 0 | 64 | 70 | 159952 | -1000000
4 | 28 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.1494 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12395.8 | 0 | 12395.8 | 147864 | 0 | 60 | 68 | 147864 | -1000000
4 | 28 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.7356 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 5.6 | 80.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10759.2 | 0 | 10759.2 | 142475 | 0 | 56 | 69 | 142475 | -1000000
4 | 28 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 5.881 | 0 | 5.4897 | 8.818 | 0 | 0 | 0 | 4.8 | 74.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10758.9 | 0 | 10758.9 | 141127 | 0 | 55 | 64 | 141127 | -1000000
4 | 29 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8407 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 75.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10758.6 | 0 | 10758.6 | 140037 | 0 | 55 | 63 | 140037 | -1000000
4 | 29 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7619 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10759 | 0 | 10759 | 139133 | 0 | 55 | 62 | 139133 | -1000000
4 | 29 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6813 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10759.3 | 0 | 10759.3 | 138160 | 0 | 54 | 61 | 138160 | -1000000
4 | 29 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6053 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10759.7 | 0 | 10759.7 | 137268 | 0 | 53 | 60 | 137268 | -1000000
4 | 29 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8278 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 3.6 | 73.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10760 | 0 | 10760 | 136526 | 0 | 52 | 57 | 136526 | -1000000
4 | 29 | 6 | 6 | 5.9284 | 0 | 42.7453 | 0 | 6.7919 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 1.2 | 70.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10760.4 | 0 | 10760.4 | 135739 | 0 | 52 | 56 | 135739 | -1000000
4 | 29 | 7 | 6 | 4.6506 | 0 | 42.7453 | 0 | 16.9507 | 0 | 6.0726 | 18.8896 | 0 | 0 | 0 | 0 | 89.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10760.6 | 0 | 10760.6 | 249385 | -8252.47 | 55 | 60 | 249385 | -1008252.47
4 | 29 | 8 | 6 | 4.9873 | 0 | 42.7453 | 0 | 19.85 | 0 | 6.2643 | 18.8896 | 0 | 0 | 0 | 0 | 92.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10760.9 | 0 | 10760.9 | 264048 | -12061.2 | 55 | 64 | 264048 | -1012061.2
4 | 29 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 20.1421 | 0 | 6.308 | 18.8896 | 0 | 0 | 0 | 0 | 93.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10773.3 | 0 | 10773.3 | 279056 | -16162 | 55 | 66 | 279056 | -1016162
4 | 29 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 23.8045 | 0 | 6.332 | 18.9501 | 0 | 0 | 0 | 0 | 97.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10774.7 | 0 | 10774.7 | 319537 | -17092.2 | 57 | 69 | 319537 | -1017092.2
4 | 29 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 27.8893 | 0 | 6.332 | 18.9954 | 0 | 0 | 0 | 0 | 101.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776.1 | 0 | 10776.1 | 360201 | -17235.7 | 59 | 73 | 360201 | -1017235.7
4 | 29 | 12 | 6 | 5.4691 | 0 | 42.7453 | 0 | 27.8309 | 0 | 6.332 | 19.047 | 0 | 0 | 0 | 0 | 101.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10776.8 | 0 | 10776.8 | 388189 | -17098.2 | 59 | 76 | 388189 | -1017098.2
4 | 29 | 13 | 6 | 5.4703 | 0 | 42.7453 | 0 | 28.1724 | 0 | 6.332 | 19.2705 | 0 | 0 | 0 | 0 | 101.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10777.3 | 0 | 10777.3 | 424895 | -21070.6 | 58 | 76 | 424895 | -1021070.6
4 | 29 | 14 | 6 | 5.4886 | 0 | 42.7453 | 0 | 7.9237 | 0 | 7.5677 | 8.818 | 0 | 0 | 0 | 0 | 72.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10777.9 | 0 | 10777.9 | 131509 | 0 | 58 | 76 | 131509 | -1000000
4 | 29 | 15 | 6 | 5.4728 | 0 | 42.7453 | 0 | 10.7221 | 0 | 10.9105 | 12.8287 | 0 | 0 | 0 | 0 | 82.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10778.4 | 0 | 10778.4 | 193902 | 0 | 59 | 76 | 193902 | -1000000
4 | 29 | 16 | 6 | 5.474 | 0 | 42.7453 | 0 | 6.7563 | 0 | 6.7817 | 8.818 | 0 | 0 | 0 | 0 | 70.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10772.3 | 0 | 10772.3 | 130722 | 0 | 57 | 73 | 130722 | -1000000
4 | 29 | 17 | 6 | 5.4755 | 0 | 42.7453 | 0 | 6.7372 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 2 | 71.2552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10769.5 | 0 | 10769.5 | 130534 | 0 | 56 | 72 | 130534 | -1000000
4 | 29 | 18 | 6 | 5.4912 | 0 | 42.7453 | 0 | 6.075 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 5.6 | 74.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10767.1 | 0 | 10767.1 | 130440 | 0 | 56 | 69 | 130440 | -1000000
4 | 29 | 19 | 6 | 7.5 | 0 | 42.7453 | 0 | 5.362 | 0 | 5.4985 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10765.5 | 0 | 10765.5 | 130027 | 0 | 55 | 64 | 130027 | -1000000
4 | 29 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.4789 | 0 | 5.4985 | 8.818 | 0 | 0 | 0 | 7.2 | 78.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10764.7 | 0 | 10764.7 | 129463 | 0 | 53 | 60 | 129463 | -1000000
4 | 29 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4855 | 0 | 5.4839 | 8.818 | 0 | 0 | 0 | 7.2 | 79.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10764.2 | 0 | 10764.2 | 129040 | 0 | 51 | 56 | 129040 | -1000000
4 | 29 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.463 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 6.4 | 78.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10764.3 | 0 | 10764.3 | 128547 | 0 | 49 | 54 | 128547 | -1000000
4 | 29 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4448 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 5.6 | 77.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10764.8 | 0 | 10764.8 | 128149 | 0 | 47 | 52 | 128149 | -1000000
4 | 29 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.4216 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3955.29 | 0 | 3955.29 | 127640 | 0 | 45 | 50 | 127640 | -1000000
4 | 30 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4036 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 4.8 | 73.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3956.26 | 0 | 3956.26 | 127247 | 0 | 44 | 49 | 127247 | -1000000
4 | 30 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3877 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3957.56 | 0 | 3957.56 | 126900 | 0 | 43 | 46 | 126900 | -1000000
4 | 30 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.0759 | 0 | 5.8981 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3958.91 | 0 | 3958.91 | 127553 | -5307.6 | 41 | 44 | 127553 | -1005307.6
4 | 30 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3445 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3960.33 | 0 | 3960.33 | 125935 | 0 | 41 | 43 | 125935 | -1000000
4 | 30 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.32 | 0 | 5.4857 | 12.8287 | 0 | 0 | 0 | 3.6 | 76.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3961.89 | 0 | 3961.89 | 125416 | 0 | 39 | 40 | 125416 | -1000000
4 | 30 | 6 | 7 | 4.4729 | 0 | 42.7453 | 0 | 6.3027 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 1.2 | 69.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3963.69 | 0 | 3963.69 | 125040 | 0 | 40 | 42 | 125040 | -1000000
4 | 30 | 7 | 7 | 3.6856 | 0 | 42.7453 | 0 | 6.2895 | 0 | 5.9042 | 12.8287 | 0 | 0 | 0 | 0 | 71.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.36 | 0 | 3965.36 | 124752 | -1475.95 | 41 | 45 | 124752 | -1001475.95
4 | 30 | 8 | 7 | 3.7897 | 0 | 42.7453 | 0 | 6.2797 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 0 | 67.1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.32 | 0 | 3967.32 | 124539 | 0 | 43 | 48 | 124539 | -1000000
4 | 30 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.2661 | 0 | 5.9045 | 12.8287 | 0 | 0 | 0 | 0 | 71.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3968.64 | 0 | 3968.64 | 124239 | -1530.28 | 44 | 51 | 124239 | -1001530.28
4 | 30 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.2487 | 0 | 5.4865 | 8.818 | 0 | 0 | 0 | 0 | 67.4425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3968.99 | 0 | 3968.99 | 123857 | 0 | 43 | 52 | 123857 | -1000000
4 | 30 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.2579 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 0 | 67.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3968.87 | 0 | 3968.87 | 124069 | 0 | 46 | 54 | 124069 | -1000000
4 | 30 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.2463 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 0 | 67.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3968.47 | 0 | 3968.47 | 123807 | 0 | 47 | 56 | 123807 | -1000000
4 | 30 | 13 | 7 | 4.147 | 0 | 42.7453 | 0 | 8.2703 | 0 | 5.8977 | 12.8287 | 0 | 0 | 0 | 0 | 73.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.9 | 0 | 3967.9 | 128072 | -5320.75 | 48 | 60 | 128072 | -1005320.75
4 | 30 | 14 | 7 | 4.1466 | 0 | 42.7453 | 0 | 7.1302 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 0 | 68.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.5 | 0 | 3967.5 | 123763 | 0 | 50 | 63 | 123763 | -1000000
4 | 30 | 15 | 7 | 4.1474 | 0 | 42.7453 | 0 | 6.9407 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 0 | 68.1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.26 | 0 | 3967.26 | 123730 | 0 | 51 | 65 | 123730 | -1000000
4 | 30 | 16 | 7 | 4.1476 | 0 | 42.7453 | 0 | 6.4239 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 0 | 67.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3966.87 | 0 | 3966.87 | 123953 | 0 | 53 | 65 | 123953 | -1000000
4 | 30 | 17 | 7 | 4.1485 | 0 | 42.7453 | 0 | 6.4056 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 2 | 69.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3966.55 | 0 | 3966.55 | 123553 | 0 | 52 | 65 | 123553 | -1000000
4 | 30 | 18 | 7 | 4.1516 | 0 | 42.7453 | 0 | 5.5281 | 0 | 5.4965 | 8.818 | 0 | 0 | 0 | 5.6 | 72.3393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3966.01 | 0 | 3966.01 | 123661 | 0 | 51 | 62 | 123661 | -1000000
4 | 30 | 19 | 7 | 5.6302 | 0 | 42.7453 | 0 | 5.7164 | 0 | 5.4943 | 8.818 | 0 | 0 | 0 | 7.2 | 75.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.7 | 0 | 3965.7 | 123439 | 0 | 49 | 58 | 123439 | -1000000
4 | 30 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2264 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.52 | 0 | 3965.52 | 123376 | 0 | 47 | 53 | 123376 | -1000000
4 | 30 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2229 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.81 | 0 | 3965.81 | 123297 | 0 | 47 | 51 | 123297 | -1000000
4 | 30 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2124 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 6.4 | 76.3259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3966.47 | 0 | 3966.47 | 123065 | 0 | 46 | 49 | 123065 | -1000000
4 | 30 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 8.4389 | 0 | 5.8972 | 12.8287 | 0 | 0 | 0 | 5.6 | 82.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.52 | 0 | 3967.52 | 130480 | -7932.14 | 45 | 47 | 130480 | -1007932.14
4 | 30 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.2111 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10778.9 | 0 | 10778.9 | 122915 | 0 | 45 | 48 | 122915 | -1000000
5 | 1 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2198 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 4.8 | 78.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.91 | 0 | 9951.91 | 123237 | 0 | 45 | 47 | 123237 | -1000000
5 | 1 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 8.0318 | 0 | 5.8986 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.7384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.26 | 0 | 9952.26 | 125131 | -8363.95 | 46 | 47 | 125131 | -1008363.95
5 | 1 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5651 | 0 | 5.9013 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.86 | 0 | 9952.86 | 130883 | -3747.64 | 46 | 47 | 130883 | -1003747.64
5 | 1 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.9575 | 0 | 5.9053 | 15.0234 | 0 | 0 | 0 | 3.2 | 91.7307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11057.3 | 0 | 11057.3 | 157123 | -4562.25 | 45 | 47 | 157123 | -1004562.25
5 | 1 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 8.9027 | 0 | 5.9048 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13514.9 | 0 | 13514.9 | 182376 | -3992.16 | 44 | 46 | 182376 | -1003992.16
5 | 1 | 6 | 1 | 46.3547 | 0 | 140.608 | 0 | 24.1308 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 236.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36658.3 | 0 | 36658.3 | 332712 | -81147.5 | 43 | 45 | 332712 | -1081147.5
5 | 1 | 7 | 1 | 41.433 | 0 | 168.222 | 0 | 30.224 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40216 | 0 | 40216 | 440632 | -170281 | 42 | 44 | 440632 | -1170281
5 | 1 | 8 | 1 | 40.1372 | 0 | 173.795 | 0 | 31.8956 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50900.5 | 0 | 50900.5 | 461172 | -156341 | 42 | 44 | 461172 | -1156341
5 | 1 | 9 | 1 | 41.1873 | 0 | 172.186 | 0 | 33.3357 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79385.8 | 0 | 79385.8 | 474628 | -159570 | 43 | 44 | 474628 | -1159570
5 | 1 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 32.8685 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81166.6 | 0 | 81166.6 | 448586 | -116525 | 44 | 48 | 448586 | -1116525
5 | 1 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 34.4172 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 250.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81166.8 | 0 | 81166.8 | 461282 | -97650.1 | 46 | 51 | 461282 | -1097650.1
5 | 1 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 29.8185 | 0 | 6.332 | 19.0904 | 0 | 0 | 0 | 0 | 245.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81166.3 | 0 | 81166.3 | 450456 | -54819.2 | 47 | 55 | 450456 | -1054819.2
5 | 1 | 13 | 1 | 41.2656 | 0 | 165.698 | 0 | 32.8096 | 0 | 6.332 | 19.6395 | 0 | 0 | 0 | 0 | 265.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81165.6 | 0 | 81165.6 | 513948 | -31160.9 | 47 | 57 | 513948 | -1031160.9
5 | 1 | 14 | 1 | 40.6712 | 0 | 172.702 | 0 | 37.2154 | 0 | 6.332 | 20.2216 | 0 | 0 | 0 | 0 | 277.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79384.9 | 0 | 79384.9 | 579988 | -16011.3 | 47 | 59 | 579988 | -1016011.3
5 | 1 | 15 | 1 | 40.5652 | 0 | 173.986 | 0 | 41.6693 | 0 | 6.332 | 20.5801 | 0 | 0 | 0 | 0 | 283.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72262.6 | 0 | 72262.6 | 634666 | -13346.3 | 46 | 61 | 634666 | -1013346.3
5 | 1 | 16 | 1 | 40.3079 | 0 | 169.782 | 0 | 39.7423 | 0 | 6.332 | 20.6133 | 0 | 0 | 0 | 0 | 276.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59799.6 | 0 | 59799.6 | 620262 | -12610.2 | 46 | 60 | 620262 | -1012610.2
5 | 1 | 17 | 1 | 35.4857 | 0 | 152.497 | 0 | 34.7509 | 0 | 6.332 | 20.291 | 0 | 0 | 0 | 0 | 249.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45556.6 | 0 | 45556.6 | 533379 | -11533.7 | 46 | 59 | 533379 | -1011533.7
5 | 1 | 18 | 1 | 24.6284 | 0 | 93.4203 | 0 | 23.7835 | 0 | 6.332 | 19.1342 | 0 | 0 | 0 | 0 | 167.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27753.9 | 0 | 27753.9 | 356243 | -11478.8 | 45 | 58 | 356243 | -1011478.8
5 | 1 | 19 | 1 | 20.1623 | 0 | 62.7906 | 0 | 9.1279 | 0 | 5.4896 | 8.818 | 0 | 0 | 0 | 1.2 | 107.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19743.4 | 0 | 19743.4 | 184017 | 0 | 45 | 54 | 184017 | -1000000
5 | 1 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.1059 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4 | 99.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18855 | 0 | 18855 | 164183 | 0 | 43 | 51 | 164183 | -1000000
5 | 1 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.4988 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11726.1 | 0 | 11726.1 | 151004 | 0 | 41 | 47 | 151004 | -1000000
5 | 1 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.0018 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11441.3 | 0 | 11441.3 | 140165 | 0 | 41 | 45 | 140165 | -1000000
5 | 1 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.7751 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 5.6 | 79.5324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.07 | 0 | 9946.07 | 135302 | 0 | 40 | 44 | 135302 | -1000000
5 | 1 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.7144 | 0 | 5.9 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.63 | 0 | 9947.63 | 134035 | -7845.88 | 39 | 42 | 134035 | -1007845.88
5 | 2 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6645 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9948.82 | 0 | 9948.82 | 132945 | 0 | 38 | 40 | 132945 | -1000000
5 | 2 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3859 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9950.46 | 0 | 9950.46 | 132134 | -14676.8 | 37 | 39 | 132134 | -1014676.8
5 | 2 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5934 | 0 | 5.901 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.21 | 0 | 9952.21 | 131395 | -4123.26 | 36 | 37 | 131395 | -1004123.26
5 | 2 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 8.6514 | 0 | 5.8968 | 12.9754 | 0 | 0 | 0 | 3.2 | 87.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11057.7 | 0 | 11057.7 | 135739 | -11244.8 | 37 | 38 | 135739 | -1011244.8
5 | 2 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.2835 | 0 | 5.9711 | 15.0234 | 0 | 0 | 0 | 1.6 | 131.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13516.3 | 0 | 13516.3 | 207537 | -11189.4 | 37 | 38 | 207537 | -1011189.4
5 | 2 | 6 | 2 | 42.7248 | 0 | 140.608 | 0 | 23.5785 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 232.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36660.7 | 0 | 36660.7 | 331320 | -149616 | 38 | 39 | 331320 | -1149616
5 | 2 | 7 | 2 | 39.0363 | 0 | 168.222 | 0 | 30.0501 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40219.2 | 0 | 40219.2 | 442318 | -208887 | 43 | 44 | 442318 | -1208887
5 | 2 | 8 | 2 | 39.6631 | 0 | 173.795 | 0 | 33.5331 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50902.8 | 0 | 50902.8 | 458538 | -123089 | 47 | 50 | 458538 | -1123089
5 | 2 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 39.0027 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 277.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79387.8 | 0 | 79387.8 | 498778 | -74967 | 52 | 55 | 498778 | -1074967
5 | 2 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 32.4668 | 0 | 6.332 | 19.2417 | 0 | 0 | 0 | 0 | 262.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81167.2 | 0 | 81167.2 | 488808 | -36268.3 | 52 | 58 | 488808 | -1036268.3
5 | 2 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 31.1307 | 0 | 6.332 | 19.3149 | 0 | 0 | 0 | 0 | 247.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81166.3 | 0 | 81166.3 | 474787 | -19095.2 | 51 | 60 | 474787 | -1019095.2
5 | 2 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 37.6244 | 0 | 6.332 | 19.6117 | 0 | 0 | 0 | 0 | 253.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81165.7 | 0 | 81165.7 | 546287 | -20870.1 | 51 | 63 | 546287 | -1020870.1
5 | 2 | 13 | 2 | 41.2447 | 0 | 165.698 | 0 | 41.8419 | 0 | 6.332 | 20.5111 | 0 | 0 | 0 | 0 | 275.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81165.5 | 0 | 81165.5 | 616430 | -11733.8 | 52 | 64 | 616430 | -1011733.8
5 | 2 | 14 | 2 | 40.6461 | 0 | 172.702 | 0 | 47.1481 | 0 | 6.332 | 20.912 | 0 | 0 | 0 | 0 | 287.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79384.7 | 0 | 79384.7 | 698980 | -10949 | 52 | 66 | 698980 | -1010949
5 | 2 | 15 | 2 | 40.5399 | 0 | 173.986 | 0 | 36.3318 | 0 | 6.3549 | 21.2549 | 0 | 0 | 0 | 0 | 278.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72262.5 | 0 | 72262.5 | 737924 | -10243.5 | 53 | 67 | 737924 | -1010243.5
5 | 2 | 16 | 2 | 40.2923 | 0 | 169.782 | 0 | 43.9325 | 0 | 6.332 | 21.1887 | 0 | 0 | 0 | 0 | 281.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59799.4 | 0 | 59799.4 | 718699 | -9693.95 | 53 | 66 | 718699 | -1009693.95
5 | 2 | 17 | 2 | 35.4824 | 0 | 152.497 | 0 | 36.9362 | 0 | 6.332 | 20.8109 | 0 | 0 | 0 | 0 | 252.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45556.4 | 0 | 45556.4 | 621915 | -8635.93 | 53 | 65 | 621915 | -1008635.93
5 | 2 | 18 | 2 | 24.626 | 0 | 93.4203 | 0 | 27.0821 | 0 | 6.332 | 19.3123 | 0 | 0 | 0 | 0 | 170.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27753.6 | 0 | 27753.6 | 425633 | -8276.62 | 53 | 64 | 425633 | -1008276.62
5 | 2 | 19 | 2 | 20.6122 | 0 | 62.7906 | 0 | 9.2678 | 0 | 5.4942 | 8.818 | 0 | 0 | 0 | 1.2 | 108.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19743.1 | 0 | 19743.1 | 188390 | 0 | 52 | 63 | 188390 | -1000000
5 | 2 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.1431 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4 | 99.8063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18854.6 | 0 | 18854.6 | 168734 | 0 | 52 | 62 | 168734 | -1000000
5 | 2 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.4794 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11724.3 | 0 | 11724.3 | 155329 | 0 | 52 | 61 | 155329 | -1000000
5 | 2 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.228 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11438.8 | 0 | 11438.8 | 144282 | 0 | 52 | 61 | 144282 | -1000000
5 | 2 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.7088 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 5.6 | 79.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.74 | 0 | 9942.74 | 139468 | 0 | 52 | 60 | 139468 | -1000000
5 | 2 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8923 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9943.44 | 0 | 9943.44 | 137923 | 0 | 52 | 60 | 137923 | -1000000
5 | 3 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.852 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9944.01 | 0 | 9944.01 | 137052 | 0 | 52 | 60 | 137052 | -1000000
5 | 3 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8182 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9944.54 | 0 | 9944.54 | 136314 | 0 | 52 | 59 | 136314 | -1000000
5 | 3 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.775 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9945 | 0 | 9945 | 135366 | 0 | 51 | 59 | 135366 | -1000000
5 | 3 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9217 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 3.2 | 81.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.1 | 0 | 11049.1 | 138647 | 0 | 51 | 59 | 138647 | -1000000
5 | 3 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 9.0284 | 0 | 5.4883 | 8.818 | 0 | 0 | 0 | 1.6 | 119.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13506.2 | 0 | 13506.2 | 185489 | 0 | 51 | 59 | 185489 | -1000000
5 | 3 | 6 | 3 | 46.473 | 0 | 140.608 | 0 | 31.659 | 0 | 6.332 | 19.4516 | 0 | 0 | 0 | 0 | 244.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36649.1 | 0 | 36649.1 | 392415 | -28296.9 | 51 | 59 | 392415 | -1028296.9
5 | 3 | 7 | 3 | 38.976 | 0 | 168.222 | 0 | 26.7068 | 0 | 6.332 | 19.2669 | 0 | 0 | 0 | 0 | 259.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40206.1 | 0 | 40206.1 | 562491 | -16907.7 | 53 | 61 | 562491 | -1016907.7
5 | 3 | 8 | 3 | 39.6656 | 0 | 173.795 | 0 | 29.9871 | 0 | 6.332 | 19.5409 | 0 | 0 | 0 | 0 | 269.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50896 | 0 | 50896 | 617544 | -15960.9 | 54 | 63 | 617544 | -1015960.9
5 | 3 | 9 | 3 | 40.7431 | 0 | 172.186 | 0 | 33.7877 | 0 | 6.332 | 19.8669 | 0 | 0 | 0 | 0 | 272.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79380.8 | 0 | 79380.8 | 689225 | -11690.3 | 56 | 65 | 689225 | -1011690.3
5 | 3 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 35.7062 | 0 | 6.332 | 20.5678 | 0 | 0 | 0 | 0 | 266.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81161 | 0 | 81161 | 729551 | -9486.3 | 57 | 66 | 729551 | -1009486.3
5 | 3 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 34.2847 | 0 | 6.332 | 20.8491 | 0 | 0 | 0 | 0 | 251.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81160.7 | 0 | 81160.7 | 704994 | -8257.26 | 58 | 66 | 704994 | -1008257.26
5 | 3 | 12 | 3 | 39.8094 | 0 | 150.207 | 0 | 35.774 | 0 | 6.332 | 20.658 | 0 | 0 | 0 | 0 | 252.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81160.7 | 0 | 81160.7 | 726293 | -7659.32 | 59 | 67 | 726293 | -1007659.32
5 | 3 | 13 | 3 | 41.233 | 0 | 165.698 | 0 | 40.1293 | 0 | 6.332 | 21.5584 | 0 | 0 | 0 | 0 | 274.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81160.8 | 0 | 81160.8 | 842759 | -8476.31 | 60 | 65 | 842759 | -1008476.31
5 | 3 | 14 | 3 | 40.9351 | 0 | 172.702 | 0 | 39.984 | 0 | 6.332 | 21.1416 | 0 | 0 | 0 | 0 | 281.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79380.4 | 0 | 79380.4 | 847443 | -11529.4 | 60 | 63 | 847443 | -1011529.4
5 | 3 | 15 | 3 | 41.6593 | 0 | 173.986 | 0 | 39.1511 | 0 | 7.3682 | 20.6721 | 0 | 0 | 0 | 0 | 282.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72258.5 | 0 | 72258.5 | 839175 | -13998.1 | 60 | 61 | 839175 | -1013998.1
5 | 3 | 16 | 3 | 41.1082 | 0 | 169.782 | 0 | 44.281 | 0 | 6.332 | 20.4373 | 0 | 0 | 0 | 0 | 281.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59795.6 | 0 | 59795.6 | 857556 | -14884.6 | 61 | 61 | 857556 | -1014884.6
5 | 3 | 17 | 3 | 36.2219 | 0 | 152.497 | 0 | 41.1678 | 0 | 6.332 | 20.1321 | 0 | 0 | 0 | 0 | 256.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45553 | 0 | 45553 | 755410 | -12589.9 | 61 | 62 | 755410 | -1012589.9
5 | 3 | 18 | 3 | 26.0026 | 0 | 93.4203 | 0 | 29.0967 | 0 | 6.332 | 19.1992 | 0 | 0 | 0 | 0 | 174.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27750.6 | 0 | 27750.6 | 490991 | -10419.5 | 61 | 62 | 490991 | -1010419.5
5 | 3 | 19 | 3 | 22.0086 | 0 | 62.7906 | 0 | 9.3264 | 0 | 5.4935 | 8.818 | 0 | 0 | 0 | 1.2 | 109.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19740.3 | 0 | 19740.3 | 190772 | 0 | 61 | 61 | 190772 | -1000000
5 | 3 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.4501 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 4 | 100.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18851.9 | 0 | 18851.9 | 170743 | 0 | 61 | 61 | 170743 | -1000000
5 | 3 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.522 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11721 | 0 | 11721 | 157119 | 0 | 60 | 60 | 157119 | -1000000
5 | 3 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.8681 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 84.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11435.5 | 0 | 11435.5 | 146079 | 0 | 60 | 62 | 146079 | -1000000
5 | 3 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.4169 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 80.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.15 | 0 | 9939.15 | 141156 | 0 | 60 | 63 | 141156 | -1000000
5 | 3 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.6841 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.69 | 0 | 9939.69 | 139539 | 0 | 60 | 65 | 139539 | -1000000
5 | 4 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8179 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.01 | 0 | 9940.01 | 138750 | 0 | 60 | 64 | 138750 | -1000000
5 | 4 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7355 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.24 | 0 | 9940.24 | 137775 | 0 | 59 | 63 | 137775 | -1000000
5 | 4 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.6616 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.27 | 0 | 9940.27 | 136962 | 0 | 58 | 62 | 136962 | -1000000
5 | 4 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0663 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11044 | 0 | 11044 | 140181 | 0 | 58 | 62 | 140181 | -1000000
5 | 4 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 9.2017 | 0 | 5.4923 | 8.818 | 0 | 0 | 0 | 1.6 | 119.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500.7 | 0 | 13500.7 | 187161 | 0 | 58 | 62 | 187161 | -1000000
5 | 4 | 6 | 4 | 44.9896 | 0 | 140.608 | 0 | 40.1443 | 0 | 6.332 | 19.7352 | 0 | 0 | 0 | 0 | 251.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36643.3 | 0 | 36643.3 | 573040 | -20379.4 | 58 | 62 | 573040 | -1020379.4
5 | 4 | 7 | 4 | 39.2237 | 0 | 168.222 | 0 | 52.9903 | 0 | 6.332 | 19.5584 | 0 | 0 | 0 | 0 | 286.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40200.1 | 0 | 40200.1 | 771878 | -14220.6 | 60 | 64 | 771878 | -1014220.6
5 | 4 | 8 | 4 | 39.6728 | 0 | 173.795 | 0 | 39.6774 | 0 | 6.332 | 20.0111 | 0 | 0 | 0 | 0 | 279.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50892.3 | 0 | 50892.3 | 815399 | -11879.2 | 61 | 65 | 815399 | -1011879.2
5 | 4 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 44.901 | 0 | 6.332 | 20.7604 | 0 | 0 | 0 | 0 | 284.796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79377.3 | 0 | 79377.3 | 906347 | -11493.7 | 62 | 67 | 906347 | -1011493.7
5 | 4 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 47.6162 | 0 | 6.332 | 21.4174 | 0 | 0 | 0 | 0 | 279.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158 | 0 | 81158 | 960079 | -10177 | 63 | 68 | 960079 | -1010177
5 | 4 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 42.9519 | 0 | 6.332 | 21.6137 | 0 | 0 | 0 | 0 | 261.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.4 | 0 | 81158.4 | 870138 | -6965.12 | 63 | 68 | 870138 | -1006965.12
5 | 4 | 12 | 4 | 39.8421 | 0 | 150.207 | 0 | 45.0188 | 0 | 6.332 | 21.3391 | 0 | 0 | 0 | 0 | 262.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.5 | 0 | 81158.5 | 902409 | -6495 | 64 | 69 | 902409 | -1006495
5 | 4 | 13 | 4 | 41.5743 | 0 | 165.698 | 0 | 49.4201 | 0 | 25.335 | 21.69 | 0 | 0 | 0 | 0 | 303.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.3 | 0 | 81158.3 | 994172 | -7350.15 | 64 | 68 | 994172 | -1007350.15
5 | 4 | 14 | 4 | 40.891 | 0 | 172.702 | 0 | 55.2109 | 0 | 25.335 | 21.8111 | 0 | 0 | 0 | 0 | 315.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79378 | 0 | 79378 | 1038850 | -13586.2 | 65 | 66 | 1038850 | -1013586.2
5 | 4 | 15 | 4 | 41.2549 | 0 | 173.986 | 0 | 56.4028 | 0 | 25.335 | 21.4813 | 0 | 0 | 0 | 0 | 318.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72256.2 | 0 | 72256.2 | 1046060 | -15324.9 | 65 | 65 | 1046060 | -1015324.9
5 | 4 | 16 | 4 | 41.4622 | 0 | 169.782 | 0 | 52.8836 | 0 | 25.335 | 20.9579 | 0 | 0 | 0 | 0 | 310.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59793.4 | 0 | 59793.4 | 1005460 | -16102.7 | 64 | 64 | 1005460 | -1016102.7
5 | 4 | 17 | 4 | 36.5195 | 0 | 152.497 | 0 | 43.7854 | 0 | 25.335 | 20.4148 | 0 | 0 | 0 | 0 | 278.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45550.9 | 0 | 45550.9 | 887699 | -13694.9 | 64 | 64 | 887699 | -1013694.9
5 | 4 | 18 | 4 | 29.0127 | 0 | 93.4203 | 0 | 30.4247 | 0 | 6.332 | 19.2347 | 0 | 0 | 0 | 0 | 178.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27748.5 | 0 | 27748.5 | 562705 | -11746.9 | 63 | 63 | 562705 | -1011746.9
5 | 4 | 19 | 4 | 22.2104 | 0 | 62.7906 | 0 | 9.7816 | 0 | 5.5043 | 8.818 | 0 | 0 | 0 | 1.2 | 110.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19738.2 | 0 | 19738.2 | 191614 | 0 | 63 | 63 | 191614 | -1000000
5 | 4 | 20 | 4 | 18.7119 | 0 | 54.6418 | 0 | 8.2659 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4 | 99.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18850 | 0 | 18850 | 171384 | 0 | 62 | 62 | 171384 | -1000000
5 | 4 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.9051 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11718.3 | 0 | 11718.3 | 158071 | 0 | 62 | 62 | 158071 | -1000000
5 | 4 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 6.7848 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 6.4 | 83.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11432.6 | 0 | 11432.6 | 146635 | 0 | 60 | 60 | 146635 | -1000000
5 | 4 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0606 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.05 | 0 | 9936.05 | 141548 | 0 | 57 | 57 | 141548 | -1000000
5 | 4 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9785 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.53 | 0 | 9936.53 | 139806 | 0 | 55 | 55 | 139806 | -1000000
5 | 5 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9269 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.98 | 0 | 9936.98 | 138688 | 0 | 53 | 54 | 138688 | -1000000
5 | 5 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8899 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.63 | 0 | 9937.63 | 137884 | 0 | 52 | 52 | 137884 | -1000000
5 | 5 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8428 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.4 | 0 | 9938.4 | 136848 | 0 | 50 | 51 | 136848 | -1000000
5 | 5 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9779 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.9 | 0 | 11042.9 | 139873 | 0 | 50 | 51 | 139873 | -1000000
5 | 5 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 9.0611 | 0 | 5.4887 | 8.818 | 0 | 0 | 0 | 1.6 | 119.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13500.5 | 0 | 13500.5 | 186196 | 0 | 49 | 51 | 186196 | -1000000
5 | 5 | 6 | 5 | 42.1899 | 0 | 140.608 | 0 | 27.5196 | 0 | 6.332 | 19.19 | 0 | 0 | 0 | 0 | 235.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36644 | 0 | 36644 | 365793 | -35750.5 | 49 | 51 | 365793 | -1035750.5
5 | 5 | 7 | 5 | 39.1506 | 0 | 168.222 | 0 | 30.3055 | 0 | 6.332 | 19.1383 | 0 | 0 | 0 | 0 | 263.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40201.6 | 0 | 40201.6 | 459932 | -41492.4 | 49 | 52 | 459932 | -1041492.4
5 | 5 | 8 | 5 | 39.7156 | 0 | 173.795 | 0 | 32.182 | 0 | 6.332 | 19.1507 | 0 | 0 | 0 | 0 | 271.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50892.6 | 0 | 50892.6 | 518340 | -53159.6 | 50 | 54 | 518340 | -1053159.6
5 | 5 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 33.9636 | 0 | 6.332 | 19.4731 | 0 | 0 | 0 | 0 | 272.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79377.9 | 0 | 79377.9 | 543384 | -34435.9 | 51 | 55 | 543384 | -1034435.9
5 | 5 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 35.7579 | 0 | 6.332 | 19.8221 | 0 | 0 | 0 | 0 | 266.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.5 | 0 | 81158.5 | 561994 | -23398.2 | 52 | 57 | 561994 | -1023398.2
5 | 5 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 35.0582 | 0 | 6.332 | 19.9438 | 0 | 0 | 0 | 0 | 251.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.4 | 0 | 81158.4 | 556823 | -15853 | 53 | 59 | 556823 | -1015853
5 | 5 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 36.7541 | 0 | 6.332 | 20.4017 | 0 | 0 | 0 | 0 | 253.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.4 | 0 | 81158.4 | 596190 | -12222.1 | 54 | 61 | 596190 | -1012222.1
5 | 5 | 13 | 5 | 41.254 | 0 | 165.698 | 0 | 39.6025 | 0 | 6.332 | 20.6884 | 0 | 0 | 0 | 0 | 273.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81158.7 | 0 | 81158.7 | 670247 | -14292.8 | 54 | 62 | 670247 | -1014292.8
5 | 5 | 14 | 5 | 40.6507 | 0 | 172.702 | 0 | 39.1449 | 0 | 25.335 | 21.2319 | 0 | 0 | 0 | 0 | 299.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79378.4 | 0 | 79378.4 | 734039 | -15993 | 54 | 64 | 734039 | -1015993
5 | 5 | 15 | 5 | 40.5484 | 0 | 173.986 | 0 | 42.8687 | 0 | 25.335 | 21.629 | 0 | 0 | 0 | 0 | 304.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72256.5 | 0 | 72256.5 | 791375 | -16477.7 | 54 | 65 | 791375 | -1016477.7
5 | 5 | 16 | 5 | 40.3021 | 0 | 169.782 | 0 | 40.5669 | 0 | 25.335 | 21.4162 | 0 | 0 | 0 | 0 | 297.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59793.8 | 0 | 59793.8 | 764958 | -16087.5 | 53 | 65 | 764958 | -1016087.5
5 | 5 | 17 | 5 | 35.4808 | 0 | 152.497 | 0 | 33.3053 | 0 | 25.335 | 20.7864 | 0 | 0 | 0 | 0 | 267.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45551.1 | 0 | 45551.1 | 663943 | -13655.8 | 52 | 64 | 663943 | -1013655.8
5 | 5 | 18 | 5 | 24.6041 | 0 | 93.4203 | 0 | 24.4182 | 0 | 6.332 | 19.5176 | 0 | 0 | 0 | 0 | 168.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27748.6 | 0 | 27748.6 | 453723 | -10648.6 | 51 | 64 | 453723 | -1010648.6
5 | 5 | 19 | 5 | 19.5557 | 0 | 62.7906 | 0 | 8.7757 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 1.2 | 106.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19738.3 | 0 | 19738.3 | 190628 | 0 | 48 | 61 | 190628 | -1000000
5 | 5 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.1564 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4 | 99.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18850 | 0 | 18850 | 170904 | 0 | 46 | 57 | 170904 | -1000000
5 | 5 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.7833 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11718.7 | 0 | 11718.7 | 157223 | 0 | 43 | 54 | 157223 | -1000000
5 | 5 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.279 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11433.2 | 0 | 11433.2 | 146230 | 0 | 43 | 53 | 146230 | -1000000
5 | 5 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.0469 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.22 | 0 | 9937.22 | 141249 | 0 | 42 | 51 | 141249 | -1000000
5 | 5 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.9541 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.37 | 0 | 9938.37 | 139269 | 0 | 41 | 50 | 139269 | -1000000
5 | 6 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9049 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.49 | 0 | 9939.49 | 138207 | 0 | 40 | 48 | 138207 | -1000000
5 | 6 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.0899 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.7424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9941.35 | 0 | 9941.35 | 137263 | -6335.29 | 39 | 47 | 137263 | -1006335.29
5 | 6 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8107 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.89 | 0 | 9942.89 | 136145 | 0 | 38 | 45 | 136145 | -1000000
5 | 6 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7753 | 0 | 5.8996 | 12.8287 | 0 | 0 | 0 | 3.2 | 77.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9944.54 | 0 | 9944.54 | 135376 | -1209.88 | 38 | 44 | 135376 | -1001209.88
5 | 6 | 5 | 6 | 6.3769 | 0 | 42.7453 | 0 | 6.7309 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.26 | 0 | 9946.26 | 134400 | 0 | 37 | 42 | 134400 | -1000000
5 | 6 | 6 | 6 | 5.3444 | 0 | 42.7453 | 0 | 10.2133 | 0 | 5.8977 | 12.8287 | 0 | 0 | 0 | 0 | 77.0294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.92 | 0 | 9947.92 | 133598 | -13075.2 | 36 | 41 | 133598 | -1013075.2
5 | 6 | 7 | 6 | 4.6133 | 0 | 42.7453 | 0 | 12.9509 | 0 | 5.9253 | 18.8896 | 0 | 0 | 0 | 0 | 85.1244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9949.77 | 0 | 9949.77 | 168423 | -177086 | 38 | 44 | 168423 | -1177086
5 | 6 | 8 | 6 | 4.9464 | 0 | 42.7453 | 0 | 16.0908 | 0 | 6.0187 | 18.8896 | 0 | 0 | 0 | 0 | 88.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.31 | 0 | 9951.31 | 221868 | -216190 | 40 | 46 | 221868 | -1216190
5 | 6 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.925 | 0 | 6.0044 | 18.8896 | 0 | 0 | 0 | 0 | 89.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.45 | 0 | 9956.45 | 210896 | -178341 | 41 | 49 | 210896 | -1178341
5 | 6 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 16.4237 | 0 | 6.0152 | 18.8896 | 0 | 0 | 0 | 0 | 89.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.75 | 0 | 9957.75 | 211787 | -152811 | 42 | 52 | 211787 | -1152811
5 | 6 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 17.037 | 0 | 6.0305 | 18.8896 | 0 | 0 | 0 | 0 | 90.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.12 | 0 | 9959.12 | 213372 | -125492 | 43 | 54 | 213372 | -1125492
5 | 6 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 16.194 | 0 | 6.0095 | 18.8896 | 0 | 0 | 0 | 0 | 89.3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960 | 0 | 9960 | 210783 | -95255.6 | 44 | 57 | 210783 | -1095255.6
5 | 6 | 13 | 6 | 5.4733 | 0 | 42.7453 | 0 | 15.0062 | 0 | 5.9866 | 18.8896 | 0 | 0 | 0 | 0 | 88.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.69 | 0 | 9960.69 | 210148 | -76720.9 | 45 | 59 | 210148 | -1076720.9
5 | 6 | 14 | 6 | 5.4753 | 0 | 42.7453 | 0 | 7.2594 | 0 | 6.597 | 8.818 | 0 | 0 | 0 | 0 | 70.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9961.31 | 0 | 9961.31 | 129083 | 0 | 46 | 60 | 129083 | -1000000
5 | 6 | 15 | 6 | 5.476 | 0 | 42.7453 | 0 | 7.868 | 0 | 6.9731 | 8.818 | 0 | 0 | 0 | 0 | 71.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9961.97 | 0 | 9961.97 | 128882 | 0 | 47 | 62 | 128882 | -1000000
5 | 6 | 16 | 6 | 5.475 | 0 | 42.7453 | 0 | 6.7832 | 0 | 6.4246 | 8.818 | 0 | 0 | 0 | 0 | 70.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.45 | 0 | 9959.45 | 128613 | 0 | 47 | 61 | 128613 | -1000000
5 | 6 | 17 | 6 | 5.4756 | 0 | 42.7453 | 0 | 6.4888 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 0 | 69.0112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9958 | 0 | 9958 | 128368 | 0 | 46 | 61 | 128368 | -1000000
5 | 6 | 18 | 6 | 5.4777 | 0 | 42.7453 | 0 | 6.1858 | 0 | 5.4873 | 8.818 | 0 | 0 | 0 | 0 | 68.7141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.26 | 0 | 9957.26 | 128098 | 0 | 46 | 60 | 128098 | -1000000
5 | 6 | 19 | 6 | 7.1806 | 0 | 42.7453 | 0 | 6.4336 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 1.2 | 71.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.84 | 0 | 9956.84 | 127906 | 0 | 45 | 56 | 127906 | -1000000
5 | 6 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4139 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4 | 76.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.88 | 0 | 9956.88 | 127472 | 0 | 43 | 52 | 127472 | -1000000
5 | 6 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3963 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.09 | 0 | 9957.09 | 127088 | 0 | 41 | 48 | 127088 | -1000000
5 | 6 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4313 | 0 | 5.9026 | 12.8287 | 0 | 0 | 0 | 6.4 | 83.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.73 | 0 | 9957.73 | 127873 | -5858.13 | 40 | 46 | 127873 | -1005858.13
5 | 6 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3622 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 5.6 | 77.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9958.72 | 0 | 9958.72 | 126322 | 0 | 39 | 44 | 126322 | -1000000
5 | 6 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 9.6073 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3729.43 | 0 | 3729.43 | 125872 | -12310.8 | 38 | 42 | 125872 | -1012310.8
5 | 7 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3182 | 0 | 5.4857 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3730.94 | 0 | 3730.94 | 125377 | 0 | 37 | 41 | 125377 | -1000000
5 | 7 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3978 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3732.6 | 0 | 3732.6 | 125130 | -16758.5 | 37 | 39 | 125130 | -1016758.5
5 | 7 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2797 | 0 | 5.9043 | 12.8287 | 0 | 0 | 0 | 4.8 | 77.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.42 | 0 | 3734.42 | 124532 | -5403.07 | 36 | 38 | 124532 | -1005403.07
5 | 7 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3469 | 0 | 5.9035 | 12.8287 | 0 | 0 | 0 | 3.2 | 76.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.21 | 0 | 3736.21 | 126037 | -12775.1 | 36 | 38 | 126037 | -1012775.1
5 | 7 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3615 | 0 | 5.9004 | 14.8767 | 0 | 0 | 0 | 1.6 | 80.5892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3738.23 | 0 | 3738.23 | 148314 | -12405.2 | 36 | 37 | 148314 | -1012405.2
5 | 7 | 6 | 7 | 4.2817 | 0 | 42.7453 | 0 | 10.0027 | 0 | 5.8988 | 14.8767 | 0 | 0 | 0 | 0 | 77.8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.29 | 0 | 3740.29 | 144809 | -14034.6 | 36 | 37 | 144809 | -1014034.6
5 | 7 | 7 | 7 | 3.6888 | 0 | 42.7453 | 0 | 8.2981 | 0 | 5.8982 | 12.8287 | 0 | 0 | 0 | 0 | 73.4591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.4 | 0 | 3742.4 | 123217 | -12008.7 | 39 | 42 | 123217 | -1012008.7
5 | 7 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 8.1796 | 0 | 5.8981 | 12.8287 | 0 | 0 | 0 | 0 | 73.4364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.43 | 0 | 3744.43 | 126302 | -11731.6 | 42 | 47 | 126302 | -1011731.6
5 | 7 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.8193 | 0 | 5.8995 | 12.8287 | 0 | 0 | 0 | 0 | 73.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3745.68 | 0 | 3745.68 | 122876 | -7380.41 | 44 | 52 | 122876 | -1007380.41
5 | 7 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.1979 | 0 | 5.4872 | 8.818 | 0 | 0 | 0 | 0 | 67.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3745.96 | 0 | 3745.96 | 122751 | 0 | 45 | 55 | 122751 | -1000000
5 | 7 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.3828 | 0 | 5.8982 | 12.8287 | 0 | 0 | 0 | 0 | 73.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3745.89 | 0 | 3745.89 | 122815 | -10106.4 | 47 | 59 | 122815 | -1010106.4
5 | 7 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.7831 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 0 | 67.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3745.03 | 0 | 3745.03 | 122764 | 0 | 48 | 62 | 122764 | -1000000
5 | 7 | 13 | 7 | 4.1464 | 0 | 42.7453 | 0 | 6.5641 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 0 | 67.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.3 | 0 | 3744.3 | 122872 | 0 | 49 | 63 | 122872 | -1000000
5 | 7 | 14 | 7 | 4.1466 | 0 | 42.7453 | 0 | 6.599 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 0 | 67.7905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3743.61 | 0 | 3743.61 | 122846 | 0 | 49 | 64 | 122846 | -1000000
5 | 7 | 15 | 7 | 4.1474 | 0 | 42.7453 | 0 | 6.6442 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 0 | 67.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.86 | 0 | 3742.86 | 123031 | 0 | 50 | 65 | 123031 | -1000000
5 | 7 | 16 | 7 | 4.1472 | 0 | 42.7453 | 0 | 6.0788 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 0 | 67.2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.1 | 0 | 3742.1 | 122929 | 0 | 49 | 64 | 122929 | -1000000
5 | 7 | 17 | 7 | 4.1479 | 0 | 42.7453 | 0 | 6.0465 | 0 | 5.4878 | 8.818 | 0 | 0 | 0 | 0 | 67.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.35 | 0 | 3741.35 | 122952 | 0 | 48 | 63 | 122952 | -1000000
5 | 7 | 18 | 7 | 4.2141 | 0 | 42.7453 | 0 | 6.0193 | 0 | 5.4886 | 8.818 | 0 | 0 | 0 | 0 | 67.2852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.74 | 0 | 3740.74 | 123069 | 0 | 48 | 62 | 123069 | -1000000
5 | 7 | 19 | 7 | 5.4454 | 0 | 42.7453 | 0 | 5.7005 | 0 | 5.4945 | 8.818 | 0 | 0 | 0 | 1.2 | 69.4037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.34 | 0 | 3740.34 | 123095 | 0 | 47 | 59 | 123095 | -1000000
5 | 7 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2035 | 0 | 5.4871 | 8.818 | 0 | 0 | 0 | 4 | 73.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.2 | 0 | 3740.2 | 122872 | 0 | 45 | 56 | 122872 | -1000000
5 | 7 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2039 | 0 | 5.4871 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.27 | 0 | 3740.27 | 122885 | 0 | 44 | 53 | 122885 | -1000000
5 | 7 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 8.5134 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 6.4 | 83.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.72 | 0 | 3740.72 | 128676 | -7172.09 | 43 | 51 | 128676 | -1007172.09
5 | 7 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.7129 | 0 | 5.9001 | 12.8287 | 0 | 0 | 0 | 5.6 | 80.4503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.41 | 0 | 3741.41 | 134114 | -3370.17 | 43 | 50 | 134114 | -1003370.17
5 | 7 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.4763 | 0 | 5.9022 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9972.82 | 0 | 9972.82 | 128755 | -3394.26 | 42 | 48 | 128755 | -1003394.26
5 | 8 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3856 | 0 | 5.9031 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9973.87 | 0 | 9973.87 | 126828 | -3521.98 | 42 | 48 | 126828 | -1003521.98
5 | 8 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.9843 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9974.12 | 0 | 9974.12 | 123984 | -5445.47 | 42 | 49 | 123984 | -1005445.47
5 | 8 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.9973 | 0 | 5.8988 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9974.87 | 0 | 9974.87 | 124095 | -5263.2 | 42 | 49 | 124095 | -1005263.2
5 | 8 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.4465 | 0 | 5.9013 | 15.0234 | 0 | 0 | 0 | 3.2 | 91.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11079.4 | 0 | 11079.4 | 151161 | -6562.49 | 42 | 49 | 151161 | -1006562.49
5 | 8 | 5 | 1 | 24.2847 | 0 | 69.9783 | 0 | 8.6179 | 0 | 5.9017 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13536.8 | 0 | 13536.8 | 176137 | -5524.38 | 42 | 49 | 176137 | -1005524.38
5 | 8 | 6 | 1 | 43.5376 | 0 | 140.608 | 0 | 24.3963 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 233.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36680.1 | 0 | 36680.1 | 332230 | -119302 | 42 | 49 | 332230 | -1119302
5 | 8 | 7 | 1 | 39.1789 | 0 | 168.222 | 0 | 31.1089 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40237.5 | 0 | 40237.5 | 427736 | -152504 | 43 | 50 | 427736 | -1152504
5 | 8 | 8 | 1 | 39.7943 | 0 | 173.795 | 0 | 33.2614 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50917.2 | 0 | 50917.2 | 447656 | -113838 | 44 | 51 | 447656 | -1113838
5 | 8 | 9 | 1 | 40.7917 | 0 | 172.186 | 0 | 34.3506 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79399.5 | 0 | 79399.5 | 458701 | -101143 | 45 | 52 | 458701 | -1101143
5 | 8 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 30.1955 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 259.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81178.3 | 0 | 81178.3 | 441860 | -84026.6 | 46 | 53 | 441860 | -1084026.6
5 | 8 | 11 | 1 | 40.9396 | 0 | 149.692 | 0 | 28.7028 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81177 | 0 | 81177 | 445071 | -80352.7 | 47 | 54 | 445071 | -1080352.7
5 | 8 | 12 | 1 | 39.7873 | 0 | 150.207 | 0 | 27.2593 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 242.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81176 | 0 | 81176 | 431156 | -64862.3 | 48 | 55 | 431156 | -1064862.3
5 | 8 | 13 | 1 | 41.6677 | 0 | 165.698 | 0 | 30.4731 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81175.4 | 0 | 81175.4 | 487019 | -56563.1 | 48 | 56 | 487019 | -1056563.1
5 | 8 | 14 | 1 | 40.9471 | 0 | 172.702 | 0 | 31.31 | 0 | 6.332 | 19.0485 | 0 | 0 | 0 | 0 | 270.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79394.5 | 0 | 79394.5 | 501569 | -40306 | 49 | 56 | 501569 | -1040306
5 | 8 | 15 | 1 | 40.8605 | 0 | 173.986 | 0 | 31.3867 | 0 | 6.332 | 19.2763 | 0 | 0 | 0 | 0 | 271.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72272 | 0 | 72272 | 500222 | -23737 | 49 | 57 | 500222 | -1023737
5 | 8 | 16 | 1 | 40.2925 | 0 | 169.782 | 0 | 32.2823 | 0 | 6.332 | 19.4896 | 0 | 0 | 0 | 0 | 268.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59808.7 | 0 | 59808.7 | 507994 | -15585.7 | 50 | 58 | 507994 | -1015585.7
5 | 8 | 17 | 1 | 35.5107 | 0 | 152.497 | 0 | 29.0997 | 0 | 6.332 | 19.3632 | 0 | 0 | 0 | 0 | 242.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45565.5 | 0 | 45565.5 | 452573 | -15063.5 | 50 | 58 | 452573 | -1015063.5
5 | 8 | 18 | 1 | 24.6219 | 0 | 93.4203 | 0 | 23.0909 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 166.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27762.4 | 0 | 27762.4 | 349995 | -35902.6 | 50 | 59 | 349995 | -1035902.6
5 | 8 | 19 | 1 | 19.6836 | 0 | 62.7906 | 0 | 9.1161 | 0 | 5.4895 | 8.818 | 0 | 0 | 0 | 1.2 | 107.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19751.5 | 0 | 19751.5 | 183859 | 0 | 50 | 58 | 183859 | -1000000
5 | 8 | 20 | 1 | 18.6905 | 0 | 54.6418 | 0 | 8.1104 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4 | 99.7406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18862.8 | 0 | 18862.8 | 164285 | 0 | 50 | 56 | 164285 | -1000000
5 | 8 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.5013 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11735.5 | 0 | 11735.5 | 151058 | 0 | 50 | 55 | 151058 | -1000000
5 | 8 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.9969 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11450.5 | 0 | 11450.5 | 140056 | 0 | 49 | 53 | 140056 | -1000000
5 | 8 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.7775 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 5.6 | 79.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.27 | 0 | 9955.27 | 135359 | 0 | 48 | 51 | 135359 | -1000000
5 | 8 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.712 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.53 | 0 | 9956.53 | 133979 | 0 | 47 | 49 | 133979 | -1000000
5 | 9 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.9228 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.77 | 0 | 9957.77 | 133127 | -7744.75 | 46 | 48 | 133127 | -1007744.75
5 | 9 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.645 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9958.99 | 0 | 9958.99 | 132527 | 0 | 46 | 46 | 132527 | -1000000
5 | 9 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.4489 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.23 | 0 | 9960.23 | 131696 | -10812.9 | 45 | 45 | 131696 | -1010812.9
5 | 9 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.7395 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 3.2 | 80.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11065.2 | 0 | 11065.2 | 134654 | 0 | 45 | 45 | 134654 | -1000000
5 | 9 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.3391 | 0 | 5.9372 | 12.9754 | 0 | 0 | 0 | 1.6 | 128.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13523.1 | 0 | 13523.1 | 181221 | -13775.8 | 45 | 45 | 181221 | -1013775.8
5 | 9 | 6 | 2 | 40.8061 | 0 | 140.608 | 0 | 24.1713 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 230.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36667 | 0 | 36667 | 339187 | -109379 | 45 | 45 | 339187 | -1109379
5 | 9 | 7 | 2 | 39.0162 | 0 | 168.222 | 0 | 31.9458 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40224.8 | 0 | 40224.8 | 448546 | -159311 | 47 | 48 | 448546 | -1159311
5 | 9 | 8 | 2 | 39.7843 | 0 | 173.795 | 0 | 33.8627 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50907.4 | 0 | 50907.4 | 463029 | -112728 | 49 | 50 | 463029 | -1112728
5 | 9 | 9 | 2 | 41.1896 | 0 | 172.186 | 0 | 37.9325 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 276.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79391.9 | 0 | 79391.9 | 496572 | -88202.4 | 51 | 53 | 496572 | -1088202.4
5 | 9 | 10 | 2 | 41.2234 | 0 | 163.102 | 0 | 31.1819 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81171.4 | 0 | 81171.4 | 485461 | -44950.9 | 53 | 57 | 485461 | -1044950.9
5 | 9 | 11 | 2 | 40.7154 | 0 | 149.692 | 0 | 32.4638 | 0 | 6.332 | 19.0789 | 0 | 0 | 0 | 0 | 248.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81170.6 | 0 | 81170.6 | 490366 | -23145.4 | 55 | 61 | 490366 | -1023145.4
5 | 9 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 38.6003 | 0 | 6.332 | 19.236 | 0 | 0 | 0 | 0 | 254.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81170.2 | 0 | 81170.2 | 547930 | -13767.1 | 57 | 65 | 547930 | -1013767.1
5 | 9 | 13 | 2 | 41.2653 | 0 | 165.698 | 0 | 36.7757 | 0 | 6.332 | 19.431 | 0 | 0 | 0 | 0 | 269.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81169.9 | 0 | 81169.9 | 579044 | -11673.9 | 55 | 62 | 579044 | -1011673.9
5 | 9 | 14 | 2 | 40.6158 | 0 | 172.702 | 0 | 35.5855 | 0 | 6.332 | 19.6282 | 0 | 0 | 0 | 0 | 274.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79389.1 | 0 | 79389.1 | 573982 | -11762 | 53 | 58 | 573982 | -1011762
5 | 9 | 15 | 2 | 41.2226 | 0 | 173.986 | 0 | 31.9764 | 0 | 6.332 | 19.6367 | 0 | 0 | 0 | 0 | 273.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72266.6 | 0 | 72266.6 | 526312 | -12789 | 51 | 55 | 526312 | -1012789
5 | 9 | 16 | 2 | 41.2523 | 0 | 169.782 | 0 | 30.7568 | 0 | 6.332 | 19.5524 | 0 | 0 | 0 | 0 | 267.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59803.4 | 0 | 59803.4 | 495797 | -18641.2 | 49 | 54 | 495797 | -1018641.2
5 | 9 | 17 | 2 | 36.5338 | 0 | 152.497 | 0 | 26.7774 | 0 | 6.332 | 19.1447 | 0 | 0 | 0 | 0 | 241.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45560.4 | 0 | 45560.4 | 425436 | -39414.9 | 48 | 52 | 425436 | -1039414.9
5 | 9 | 18 | 2 | 27.634 | 0 | 93.4203 | 0 | 22.2678 | 0 | 9.1093 | 19.0363 | 0 | 0 | 0 | 0 | 171.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27757.8 | 0 | 27757.8 | 348668 | -92480.9 | 46 | 51 | 348668 | -1092480.9
5 | 9 | 19 | 2 | 22.4825 | 0 | 62.7906 | 0 | 9.5829 | 0 | 8.5613 | 8.818 | 0 | 0 | 0 | 1.2 | 113.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19747.3 | 0 | 19747.3 | 187134 | 0 | 44 | 49 | 187134 | -1000000
5 | 9 | 20 | 2 | 18.6899 | 0 | 54.6418 | 0 | 8.2547 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4 | 99.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18859.1 | 0 | 18859.1 | 167441 | 0 | 41 | 46 | 167441 | -1000000
5 | 9 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.6366 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11731.7 | 0 | 11731.7 | 154016 | 0 | 39 | 44 | 154016 | -1000000
5 | 9 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 10.3962 | 0 | 5.8995 | 12.9754 | 0 | 0 | 0 | 6.4 | 91.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11447.5 | 0 | 11447.5 | 142900 | -9161.18 | 37 | 42 | 142900 | -1009161.18
5 | 9 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.8933 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.92 | 0 | 9952.92 | 137888 | 0 | 35 | 39 | 137888 | -1000000
5 | 9 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 11.2558 | 0 | 5.9013 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.9651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.07 | 0 | 9955.07 | 136220 | -16531.4 | 33 | 37 | 136220 | -1016531.4
5 | 10 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7688 | 0 | 5.8996 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.28 | 0 | 9957.28 | 135230 | -6077.12 | 32 | 36 | 135230 | -1006077.12
5 | 10 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 9.5872 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.2922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.37 | 0 | 9959.37 | 135635 | -13828.9 | 31 | 34 | 135635 | -1013828.9
5 | 10 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9935 | 0 | 5.9056 | 14.8767 | 0 | 0 | 0 | 4.8 | 89.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9961.66 | 0 | 9961.66 | 157401 | -14087.9 | 30 | 33 | 157401 | -1014087.9
5 | 10 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.3869 | 0 | 5.9078 | 15.0234 | 0 | 0 | 0 | 3.2 | 92.1625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11067.6 | 0 | 11067.6 | 156846 | -18567.6 | 29 | 33 | 156846 | -1018567.6
5 | 10 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 15.2766 | 0 | 5.9966 | 17.5105 | 0 | 0 | 0 | 1.6 | 134.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13526.6 | 0 | 13526.6 | 216186 | -26326.2 | 29 | 32 | 216186 | -1026326.2
5 | 10 | 6 | 3 | 40.1399 | 0 | 140.608 | 0 | 22.7404 | 0 | 6.2899 | 19.0363 | 0 | 0 | 0 | 0 | 228.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36671.5 | 0 | 36671.5 | 326670 | -399890 | 28 | 32 | 326670 | -1399890
5 | 10 | 7 | 3 | 38.9934 | 0 | 168.222 | 0 | 26.2896 | 0 | 25.3133 | 19.0363 | 0 | 0 | 0 | 0 | 277.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40231.4 | 0 | 40231.4 | 388950 | -345302 | 30 | 35 | 388950 | -1345302
5 | 10 | 8 | 3 | 39.6631 | 0 | 173.795 | 0 | 25.8999 | 0 | 25.3333 | 19.0363 | 0 | 0 | 0 | 0 | 283.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50912.6 | 0 | 50912.6 | 407213 | -260216 | 31 | 37 | 407213 | -1260216
5 | 10 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 28.9152 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 286.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79397 | 0 | 79397 | 437297 | -238988 | 32 | 40 | 437297 | -1238988
5 | 10 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 31.1476 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 279.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81177.3 | 0 | 81177.3 | 453145 | -208831 | 36 | 44 | 453145 | -1208831
5 | 10 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 32.2188 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 266.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81176.2 | 0 | 81176.2 | 441949 | -154135 | 38 | 49 | 441949 | -1154135
5 | 10 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 31.6415 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81174.7 | 0 | 81174.7 | 416554 | -99081.6 | 40 | 53 | 416554 | -1099081.6
5 | 10 | 13 | 3 | 41.233 | 0 | 165.698 | 0 | 33.4091 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81173.5 | 0 | 81173.5 | 477001 | -73916.9 | 42 | 55 | 477001 | -1073916.9
5 | 10 | 14 | 3 | 40.6429 | 0 | 172.702 | 0 | 32.6472 | 0 | 6.332 | 19.0837 | 0 | 0 | 0 | 0 | 271.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79391.8 | 0 | 79391.8 | 515934 | -38289.6 | 43 | 58 | 515934 | -1038289.6
5 | 10 | 15 | 3 | 40.5556 | 0 | 173.986 | 0 | 33.8145 | 0 | 6.332 | 19.3446 | 0 | 0 | 0 | 0 | 274.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72269.2 | 0 | 72269.2 | 527040 | -17231 | 44 | 60 | 527040 | -1017231
5 | 10 | 16 | 3 | 40.3053 | 0 | 169.782 | 0 | 33.3471 | 0 | 6.332 | 19.4764 | 0 | 0 | 0 | 0 | 269.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59805.7 | 0 | 59805.7 | 521854 | -14478.3 | 44 | 59 | 521854 | -1014478.3
5 | 10 | 17 | 3 | 35.4772 | 0 | 152.497 | 0 | 30.1039 | 0 | 6.332 | 19.3955 | 0 | 0 | 0 | 0 | 243.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45562.5 | 0 | 45562.5 | 464947 | -13610.3 | 43 | 58 | 464947 | -1013610.3
5 | 10 | 18 | 3 | 24.6103 | 0 | 93.4203 | 0 | 23.1879 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 166.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27759.5 | 0 | 27759.5 | 352994 | -40661.7 | 42 | 57 | 352994 | -1040661.7
5 | 10 | 19 | 3 | 19.1398 | 0 | 62.7906 | 0 | 9.9745 | 0 | 8.7303 | 8.818 | 0 | 0 | 0 | 1.2 | 110.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19748.7 | 0 | 19748.7 | 188045 | 0 | 41 | 54 | 188045 | -1000000
5 | 10 | 20 | 3 | 18.6742 | 0 | 54.6418 | 0 | 8.345 | 0 | 7.6068 | 8.818 | 0 | 0 | 0 | 4 | 102.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18860.1 | 0 | 18860.1 | 168257 | 0 | 40 | 52 | 168257 | -1000000
5 | 10 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.6703 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11732.8 | 0 | 11732.8 | 154753 | 0 | 38 | 49 | 154753 | -1000000
5 | 10 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.1635 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11448.3 | 0 | 11448.3 | 143700 | 0 | 38 | 47 | 143700 | -1000000
5 | 10 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 9.6873 | 0 | 5.8974 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953.56 | 0 | 9953.56 | 138716 | -7909.94 | 37 | 44 | 138716 | -1007909.94
5 | 10 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8488 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.39 | 0 | 9955.39 | 136967 | 0 | 35 | 42 | 136967 | -1000000
5 | 11 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.7512 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9957.22 | 0 | 9957.22 | 135952 | -14354.2 | 34 | 41 | 135952 | -1014354.2
5 | 11 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7566 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.16 | 0 | 9959.16 | 134963 | 0 | 33 | 39 | 134963 | -1000000
5 | 11 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.3516 | 0 | 5.9013 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.98 | 0 | 9960.98 | 134041 | -18690.4 | 31 | 38 | 134041 | -1018690.4
5 | 11 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.8324 | 0 | 5.8992 | 12.9754 | 0 | 0 | 0 | 3.2 | 85.5515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11066.6 | 0 | 11066.6 | 136683 | -7958.03 | 31 | 37 | 136683 | -1007958.03
5 | 11 | 5 | 4 | 24.2587 | 0 | 69.9783 | 0 | 14.4448 | 0 | 5.9804 | 15.0234 | 0 | 0 | 0 | 1.6 | 131.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13525.2 | 0 | 13525.2 | 214431 | -15796.1 | 31 | 37 | 214431 | -1015796.1
5 | 11 | 6 | 4 | 39.553 | 0 | 140.608 | 0 | 22.9176 | 0 | 6.3127 | 19.0363 | 0 | 0 | 0 | 0 | 228.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36669.7 | 0 | 36669.7 | 327722 | -305915 | 30 | 36 | 327722 | -1305915
5 | 11 | 7 | 4 | 39.0861 | 0 | 168.222 | 0 | 27.7916 | 0 | 25.3321 | 19.0363 | 0 | 0 | 0 | 0 | 279.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40228.3 | 0 | 40228.3 | 417285 | -263732 | 33 | 41 | 417285 | -1263732
5 | 11 | 8 | 4 | 39.7135 | 0 | 173.795 | 0 | 32.1994 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 290.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50910.2 | 0 | 50910.2 | 467730 | -200719 | 37 | 45 | 467730 | -1200719
5 | 11 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 34.4365 | 0 | 8.5125 | 19.0363 | 0 | 0 | 0 | 0 | 274.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79394 | 0 | 79394 | 468231 | -141021 | 39 | 50 | 468231 | -1141021
5 | 11 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 34.1961 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81173.6 | 0 | 81173.6 | 447933 | -99850.2 | 41 | 53 | 447933 | -1099850.2
5 | 11 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 33.6069 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81172.2 | 0 | 81172.2 | 461049 | -64736 | 43 | 57 | 461049 | -1064736
5 | 11 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 29.2934 | 0 | 6.332 | 19.109 | 0 | 0 | 0 | 0 | 244.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81170.9 | 0 | 81170.9 | 457291 | -30406.6 | 44 | 60 | 457291 | -1030406.6
5 | 11 | 13 | 4 | 41.2725 | 0 | 165.698 | 0 | 35.9398 | 0 | 6.332 | 19.5609 | 0 | 0 | 0 | 0 | 268.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81170.4 | 0 | 81170.4 | 539471 | -16787.4 | 45 | 62 | 539471 | -1016787.4
5 | 11 | 14 | 4 | 40.6752 | 0 | 172.702 | 0 | 40.5557 | 0 | 6.332 | 19.9528 | 0 | 0 | 0 | 0 | 280.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79389.4 | 0 | 79389.4 | 606764 | -12222.7 | 46 | 63 | 606764 | -1012222.7
5 | 11 | 15 | 4 | 40.5707 | 0 | 173.986 | 0 | 36.8132 | 0 | 25.335 | 20.2241 | 0 | 0 | 0 | 0 | 296.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72267 | 0 | 72267 | 660829 | -10925.8 | 46 | 65 | 660829 | -1010925.8
5 | 11 | 16 | 4 | 40.3104 | 0 | 169.782 | 0 | 36.0498 | 0 | 25.335 | 20.3853 | 0 | 0 | 0 | 0 | 291.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59803.8 | 0 | 59803.8 | 665510 | -10304.9 | 47 | 65 | 665510 | -1010304.9
5 | 11 | 17 | 4 | 35.4859 | 0 | 152.497 | 0 | 35.7565 | 0 | 6.332 | 20.2447 | 0 | 0 | 0 | 0 | 250.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45560.7 | 0 | 45560.7 | 602971 | -9406.8 | 47 | 65 | 602971 | -1009406.8
5 | 11 | 18 | 4 | 24.6683 | 0 | 93.4203 | 0 | 26.2316 | 0 | 6.332 | 19.1856 | 0 | 0 | 0 | 0 | 169.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27757.7 | 0 | 27757.7 | 430015 | -9082.37 | 46 | 65 | 430015 | -1009082.37
5 | 11 | 19 | 4 | 19.6151 | 0 | 62.7906 | 0 | 8.5013 | 0 | 7.5774 | 8.818 | 0 | 0 | 0 | 1.2 | 108.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19747 | 0 | 19747 | 189631 | 0 | 46 | 60 | 189631 | -1000000
5 | 11 | 20 | 4 | 18.6192 | 0 | 54.6418 | 0 | 8.3734 | 0 | 7.6429 | 8.818 | 0 | 0 | 0 | 4 | 102.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18858.4 | 0 | 18858.4 | 169429 | 0 | 44 | 54 | 169429 | -1000000
5 | 11 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7192 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11729.3 | 0 | 11729.3 | 155821 | 0 | 41 | 49 | 155821 | -1000000
5 | 11 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2097 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11444.2 | 0 | 11444.2 | 144711 | 0 | 41 | 47 | 144711 | -1000000
5 | 11 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.9764 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9948.93 | 0 | 9948.93 | 139706 | 0 | 40 | 45 | 139706 | -1000000
5 | 11 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 9.0448 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9950.58 | 0 | 9950.58 | 138053 | -6235.87 | 39 | 43 | 138053 | -1006235.87
5 | 12 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8434 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.24 | 0 | 9952.24 | 136858 | 0 | 38 | 42 | 136858 | -1000000
5 | 12 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.237 | 0 | 5.898 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953.91 | 0 | 9953.91 | 135847 | -12198.8 | 36 | 40 | 135847 | -1012198.8
5 | 12 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7513 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.66 | 0 | 9955.66 | 134846 | 0 | 35 | 39 | 134846 | -1000000
5 | 12 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.0606 | 0 | 5.9008 | 12.9754 | 0 | 0 | 0 | 3.2 | 89.7812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11061 | 0 | 11061 | 137612 | -16023.9 | 35 | 39 | 137612 | -1016023.9
5 | 12 | 5 | 5 | 24.2503 | 0 | 69.9783 | 0 | 8.95 | 0 | 5.9054 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13519.5 | 0 | 13519.5 | 183762 | -4530.58 | 36 | 40 | 183762 | -1004530.58
5 | 12 | 6 | 5 | 37.8702 | 0 | 140.608 | 0 | 23.2229 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 227.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36663.6 | 0 | 36663.6 | 331848 | -159939 | 36 | 40 | 331848 | -1159939
5 | 12 | 7 | 5 | 38.8069 | 0 | 168.222 | 0 | 31.0127 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 282.413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40221.9 | 0 | 40221.9 | 452101 | -208456 | 39 | 45 | 452101 | -1208456
5 | 12 | 8 | 5 | 39.6631 | 0 | 173.795 | 0 | 33.5088 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50905 | 0 | 50905 | 462705 | -132401 | 42 | 49 | 462705 | -1132401
5 | 12 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 36.987 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79389.9 | 0 | 79389.9 | 477661 | -84365.8 | 44 | 54 | 477661 | -1084365.8
5 | 12 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 31.704 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81169.6 | 0 | 81169.6 | 463502 | -52799.2 | 45 | 56 | 463502 | -1052799.2
5 | 12 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 30.3046 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81168.4 | 0 | 81168.4 | 467387 | -34443 | 46 | 59 | 467387 | -1034443
5 | 12 | 12 | 5 | 39.8598 | 0 | 150.207 | 0 | 30.2589 | 0 | 6.332 | 19.0985 | 0 | 0 | 0 | 0 | 245.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81167.8 | 0 | 81167.8 | 459412 | -17012.8 | 47 | 61 | 459412 | -1017012.8
5 | 12 | 13 | 5 | 41.8763 | 0 | 165.698 | 0 | 33.2364 | 0 | 6.332 | 19.2216 | 0 | 0 | 0 | 0 | 266.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81167.6 | 0 | 81167.6 | 516908 | -14032.3 | 47 | 61 | 516908 | -1014032.3
5 | 12 | 14 | 5 | 40.8964 | 0 | 172.702 | 0 | 36.2968 | 0 | 6.332 | 19.37 | 0 | 0 | 0 | 0 | 275.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79386.9 | 0 | 79386.9 | 567612 | -11548.1 | 47 | 62 | 567612 | -1011548.1
5 | 12 | 15 | 5 | 40.7617 | 0 | 173.986 | 0 | 35.9069 | 0 | 6.332 | 19.7256 | 0 | 0 | 0 | 0 | 276.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72264.8 | 0 | 72264.8 | 587768 | -10750.2 | 47 | 62 | 587768 | -1010750.2
5 | 12 | 16 | 5 | 41.3266 | 0 | 169.782 | 0 | 34.1096 | 0 | 6.332 | 19.7941 | 0 | 0 | 0 | 0 | 271.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59801.7 | 0 | 59801.7 | 575452 | -10639.3 | 47 | 61 | 575452 | -1010639.3
5 | 12 | 17 | 5 | 36.4735 | 0 | 152.497 | 0 | 30.384 | 0 | 6.332 | 19.5772 | 0 | 0 | 0 | 0 | 245.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45558.7 | 0 | 45558.7 | 495879 | -10237 | 47 | 60 | 495879 | -1010237
5 | 12 | 18 | 5 | 26.3637 | 0 | 93.4203 | 0 | 23.0874 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 168.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27755.8 | 0 | 27755.8 | 352848 | -11458.7 | 47 | 59 | 352848 | -1011458.7
5 | 12 | 19 | 5 | 22.0086 | 0 | 62.7906 | 0 | 9.3751 | 0 | 5.4934 | 8.818 | 0 | 0 | 0 | 1.2 | 109.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19745.3 | 0 | 19745.3 | 189578 | 0 | 47 | 58 | 189578 | -1000000
5 | 12 | 20 | 5 | 18.6878 | 0 | 54.6418 | 0 | 8.3585 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4 | 99.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18856.8 | 0 | 18856.8 | 169712 | 0 | 47 | 57 | 169712 | -1000000
5 | 12 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.7325 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11727.9 | 0 | 11727.9 | 156113 | 0 | 46 | 56 | 156113 | -1000000
5 | 12 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.2354 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11442.9 | 0 | 11442.9 | 145279 | 0 | 47 | 53 | 145279 | -1000000
5 | 12 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 6.9945 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.38 | 0 | 9947.38 | 140100 | 0 | 47 | 51 | 140100 | -1000000
5 | 12 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.9014 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9948.57 | 0 | 9948.57 | 138116 | 0 | 46 | 48 | 138116 | -1000000
5 | 13 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8515 | 0 | 5.8991 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9949.79 | 0 | 9949.79 | 137039 | -5474.69 | 46 | 48 | 137039 | -1005474.69
5 | 13 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8068 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.69 | 0 | 9951.69 | 136063 | 0 | 46 | 48 | 136063 | -1000000
5 | 13 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7682 | 0 | 5.8996 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953.34 | 0 | 9953.34 | 135220 | -1208.94 | 46 | 48 | 135220 | -1001208.94
5 | 13 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7306 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 3.2 | 73.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.09 | 0 | 9955.09 | 134397 | 0 | 46 | 47 | 134397 | -1000000
5 | 13 | 5 | 6 | 6.366 | 0 | 42.7453 | 0 | 6.6868 | 0 | 5.9003 | 12.8287 | 0 | 0 | 0 | 1.6 | 76.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.57 | 0 | 9956.57 | 133436 | -2099.4 | 45 | 47 | 133436 | -1002099.4
5 | 13 | 6 | 6 | 5.1255 | 0 | 42.7453 | 0 | 6.6584 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 0 | 68.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9958.16 | 0 | 9958.16 | 132819 | 0 | 45 | 46 | 132819 | -1000000
5 | 13 | 7 | 6 | 4.609 | 0 | 42.7453 | 0 | 12.6602 | 0 | 5.9175 | 18.8896 | 0 | 0 | 0 | 0 | 84.8216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.63 | 0 | 9959.63 | 158021 | -123416 | 47 | 49 | 158021 | -1123416
5 | 13 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 16.191 | 0 | 6.0053 | 18.8896 | 0 | 0 | 0 | 0 | 88.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9961.02 | 0 | 9961.02 | 207691 | -191088 | 49 | 53 | 207691 | -1191088
5 | 13 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 16.2142 | 0 | 5.9994 | 18.8896 | 0 | 0 | 0 | 0 | 89.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9964.1 | 0 | 9964.1 | 200236 | -144947 | 51 | 56 | 200236 | -1144947
5 | 13 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.3753 | 0 | 5.9823 | 18.8896 | 0 | 0 | 0 | 0 | 88.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9964.9 | 0 | 9964.9 | 199235 | -109917 | 51 | 59 | 199235 | -1109917
5 | 13 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.9614 | 0 | 6.0165 | 18.8896 | 0 | 0 | 0 | 0 | 89.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9965.75 | 0 | 9965.75 | 201320 | -77702.7 | 52 | 62 | 201320 | -1077702.7
5 | 13 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.7376 | 0 | 6.0509 | 18.8896 | 0 | 0 | 0 | 0 | 88.8923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9966.11 | 0 | 9966.11 | 212998 | -58699.7 | 53 | 65 | 212998 | -1058699.7
5 | 13 | 13 | 6 | 5.4707 | 0 | 42.7453 | 0 | 16.0494 | 0 | 6.0681 | 18.8896 | 0 | 0 | 0 | 0 | 89.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9966.27 | 0 | 9966.27 | 226621 | -52867.8 | 53 | 66 | 226621 | -1052867.8
5 | 13 | 14 | 6 | 5.4712 | 0 | 42.7453 | 0 | 7.5959 | 0 | 6.8959 | 8.818 | 0 | 0 | 0 | 0 | 71.5263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9966.4 | 0 | 9966.4 | 129132 | 0 | 53 | 66 | 129132 | -1000000
5 | 13 | 15 | 6 | 5.4711 | 0 | 42.7453 | 0 | 7.8142 | 0 | 7.0683 | 8.818 | 0 | 0 | 0 | 0 | 71.9169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9966.5 | 0 | 9966.5 | 128889 | 0 | 53 | 67 | 128889 | -1000000
5 | 13 | 16 | 6 | 5.4741 | 0 | 42.7453 | 0 | 7.057 | 0 | 6.6349 | 8.818 | 0 | 0 | 0 | 0 | 70.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9964.18 | 0 | 9964.18 | 128636 | 0 | 52 | 66 | 128636 | -1000000
5 | 13 | 17 | 6 | 5.4752 | 0 | 42.7453 | 0 | 7.263 | 0 | 6.7772 | 8.818 | 0 | 0 | 0 | 0 | 71.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9962.25 | 0 | 9962.25 | 128494 | 0 | 52 | 66 | 128494 | -1000000
5 | 13 | 18 | 6 | 5.4926 | 0 | 42.7453 | 0 | 6.4157 | 0 | 6.4725 | 8.818 | 0 | 0 | 0 | 0 | 69.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9961.25 | 0 | 9961.25 | 128320 | 0 | 52 | 65 | 128320 | -1000000
5 | 13 | 19 | 6 | 6.9886 | 0 | 42.7453 | 0 | 5.4428 | 0 | 5.4986 | 8.818 | 0 | 0 | 0 | 1.2 | 70.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.48 | 0 | 9960.48 | 128053 | 0 | 51 | 61 | 128053 | -1000000
5 | 13 | 20 | 6 | 8.7459 | 0 | 42.7453 | 0 | 6.1683 | 0 | 5.4875 | 8.818 | 0 | 0 | 0 | 4 | 75.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.08 | 0 | 9960.08 | 127712 | 0 | 50 | 58 | 127712 | -1000000
5 | 13 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4057 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9959.95 | 0 | 9959.95 | 127293 | 0 | 48 | 54 | 127293 | -1000000
5 | 13 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3941 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.17 | 0 | 9960.17 | 127041 | 0 | 47 | 51 | 127041 | -1000000
5 | 13 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.376 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 5.6 | 77.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9960.67 | 0 | 9960.67 | 126644 | 0 | 46 | 49 | 126644 | -1000000
5 | 13 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.3513 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3730.79 | 0 | 3730.79 | 126100 | 0 | 44 | 46 | 126100 | -1000000
5 | 14 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3349 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.34 | 0 | 3731.34 | 125745 | 0 | 43 | 45 | 125745 | -1000000
5 | 14 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.1539 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.5301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3732.6 | 0 | 3732.6 | 125440 | -10105.3 | 43 | 45 | 125440 | -1010105.3
5 | 14 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2991 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3733.99 | 0 | 3733.99 | 124959 | 0 | 42 | 44 | 124959 | -1000000
5 | 14 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.7097 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 3.2 | 79.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3735.59 | 0 | 3735.59 | 124676 | -13555.4 | 42 | 44 | 124676 | -1013555.4
5 | 14 | 5 | 7 | 5.0914 | 0 | 42.7453 | 0 | 6.2698 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 1.6 | 70.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3737.23 | 0 | 3737.23 | 124320 | 0 | 42 | 43 | 124320 | -1000000
5 | 14 | 6 | 7 | 3.9811 | 0 | 42.7453 | 0 | 9.8732 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 75.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3738.8 | 0 | 3738.8 | 123971 | -15352.4 | 42 | 43 | 123971 | -1015352.4
5 | 14 | 7 | 7 | 3.6827 | 0 | 42.7453 | 0 | 6.2462 | 0 | 5.9047 | 12.8287 | 0 | 0 | 0 | 0 | 71.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.49 | 0 | 3740.49 | 123806 | -3495.37 | 45 | 49 | 123806 | -1003495.37
5 | 14 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 6.2431 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 0 | 67.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.99 | 0 | 3741.99 | 123741 | 0 | 48 | 54 | 123741 | -1000000
5 | 14 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.2777 | 0 | 5.8983 | 12.8287 | 0 | 0 | 0 | 0 | 73.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3743.13 | 0 | 3743.13 | 123431 | -8948.45 | 49 | 60 | 123431 | -1008948.45
5 | 14 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.8159 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 0 | 68.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3743.42 | 0 | 3743.42 | 123475 | 0 | 50 | 62 | 123475 | -1000000
5 | 14 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.5874 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 0 | 67.7767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.63 | 0 | 3742.63 | 123370 | 0 | 50 | 63 | 123370 | -1000000
5 | 14 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.9221 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 0 | 68.1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.75 | 0 | 3741.75 | 123332 | 0 | 50 | 65 | 123332 | -1000000
5 | 14 | 13 | 7 | 4.1442 | 0 | 42.7453 | 0 | 6.704 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 0 | 67.8919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.26 | 0 | 3740.26 | 123506 | 0 | 51 | 66 | 123506 | -1000000
5 | 14 | 14 | 7 | 4.1466 | 0 | 42.7453 | 0 | 6.4367 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 0 | 67.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3739.43 | 0 | 3739.43 | 123455 | 0 | 51 | 66 | 123455 | -1000000
5 | 14 | 15 | 7 | 4.1468 | 0 | 42.7453 | 0 | 6.7389 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 0 | 67.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3738.46 | 0 | 3738.46 | 123435 | 0 | 51 | 67 | 123435 | -1000000
5 | 14 | 16 | 7 | 4.1472 | 0 | 42.7453 | 0 | 6.4772 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 0 | 67.6695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3737.52 | 0 | 3737.52 | 123540 | 0 | 51 | 67 | 123540 | -1000000
5 | 14 | 17 | 7 | 4.1481 | 0 | 42.7453 | 0 | 6.7833 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 0 | 67.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.79 | 0 | 3736.79 | 123555 | 0 | 51 | 68 | 123555 | -1000000
5 | 14 | 18 | 7 | 4.3556 | 0 | 42.7453 | 0 | 6.5258 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 0 | 67.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.05 | 0 | 3736.05 | 123779 | 0 | 52 | 68 | 123779 | -1000000
5 | 14 | 19 | 7 | 5.2881 | 0 | 42.7453 | 0 | 5.3317 | 0 | 5.4991 | 8.818 | 0 | 0 | 0 | 1.2 | 68.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3735.47 | 0 | 3735.47 | 123771 | 0 | 52 | 64 | 123771 | -1000000
5 | 14 | 20 | 7 | 6.6404 | 0 | 42.7453 | 0 | 5.2098 | 0 | 5.504 | 8.818 | 0 | 0 | 0 | 4 | 72.9174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.98 | 0 | 3734.98 | 123581 | 0 | 51 | 59 | 123581 | -1000000
5 | 14 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2282 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.7 | 0 | 3734.7 | 123413 | 0 | 50 | 55 | 123413 | -1000000
5 | 14 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2185 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 6.4 | 76.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.73 | 0 | 3734.73 | 123199 | 0 | 49 | 53 | 123199 | -1000000
5 | 14 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2129 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 5.6 | 75.5265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3735.17 | 0 | 3735.17 | 123079 | 0 | 48 | 51 | 123079 | -1000000
5 | 14 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.2184 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9966.43 | 0 | 9966.43 | 123202 | 0 | 47 | 49 | 123202 | -1000000
5 | 15 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 8.2682 | 0 | 5.8984 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9967.31 | 0 | 9967.31 | 123032 | -9975.08 | 45 | 47 | 123032 | -1009975.08
5 | 15 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5263 | 0 | 5.9017 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9967.48 | 0 | 9967.48 | 130057 | -3913.07 | 44 | 44 | 130057 | -1003913.07
5 | 15 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2918 | 0 | 5.9041 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9968.25 | 0 | 9968.25 | 124718 | -4027.24 | 42 | 42 | 124718 | -1004027.24
5 | 15 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.4531 | 0 | 5.9013 | 15.0234 | 0 | 0 | 0 | 3.2 | 91.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11072.9 | 0 | 11072.9 | 151085 | -6741.51 | 43 | 44 | 151085 | -1006741.51
5 | 15 | 5 | 1 | 24.2319 | 0 | 69.9783 | 0 | 8.754 | 0 | 5.9031 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13530.7 | 0 | 13530.7 | 179168 | -7004.56 | 44 | 45 | 179168 | -1007004.56
5 | 15 | 6 | 1 | 38.9807 | 0 | 140.608 | 0 | 24.6554 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 229.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36674.4 | 0 | 36674.4 | 336473 | -113877 | 46 | 47 | 336473 | -1113877
5 | 15 | 7 | 1 | 38.9833 | 0 | 168.222 | 0 | 31.4842 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40232 | 0 | 40232 | 423144 | -124222 | 49 | 52 | 423144 | -1124222
5 | 15 | 8 | 1 | 39.6631 | 0 | 173.795 | 0 | 32.8922 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50912.3 | 0 | 50912.3 | 457959 | -61868.4 | 51 | 57 | 457959 | -1061868.4
5 | 15 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 35.9874 | 0 | 6.332 | 19.0593 | 0 | 0 | 0 | 0 | 274.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79395.5 | 0 | 79395.5 | 516050 | -29610.7 | 52 | 62 | 516050 | -1029610.7
5 | 15 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 40.3335 | 0 | 6.332 | 19.5161 | 0 | 0 | 0 | 0 | 270.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81174.3 | 0 | 81174.3 | 573719 | -17442.3 | 53 | 66 | 573719 | -1017442.3
5 | 15 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 42.5163 | 0 | 6.332 | 19.744 | 0 | 0 | 0 | 0 | 258.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81173.6 | 0 | 81173.6 | 587295 | -11536.4 | 54 | 69 | 587295 | -1011536.4
5 | 15 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 51.6585 | 0 | 6.332 | 19.9034 | 0 | 0 | 0 | 0 | 267.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81172.7 | 0 | 81172.7 | 682585 | -11172.2 | 54 | 73 | 682585 | -1011172.2
5 | 15 | 13 | 1 | 41.2425 | 0 | 165.698 | 0 | 55.8822 | 0 | 6.332 | 20.9802 | 0 | 0 | 0 | 0 | 290.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81171.6 | 0 | 81171.6 | 776261 | -9438.92 | 54 | 74 | 776261 | -1009438.92
5 | 15 | 14 | 1 | 40.642 | 0 | 172.702 | 0 | 43.4292 | 0 | 6.332 | 21.0789 | 0 | 0 | 0 | 0 | 284.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79390.6 | 0 | 79390.6 | 839105 | -9206.26 | 54 | 75 | 839105 | -1009206.26
5 | 15 | 15 | 1 | 40.5314 | 0 | 173.986 | 0 | 45.5225 | 0 | 6.332 | 21.4845 | 0 | 0 | 0 | 0 | 287.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72268.7 | 0 | 72268.7 | 884506 | -8677.27 | 54 | 76 | 884506 | -1008677.27
5 | 15 | 16 | 1 | 40.2873 | 0 | 169.782 | 0 | 44.9421 | 0 | 6.332 | 21.6458 | 0 | 0 | 0 | 0 | 282.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59805.7 | 0 | 59805.7 | 872449 | -7725.13 | 53 | 75 | 872449 | -1007725.13
5 | 15 | 17 | 1 | 35.4713 | 0 | 152.497 | 0 | 39.9185 | 0 | 6.332 | 21.2665 | 0 | 0 | 0 | 0 | 255.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45562.7 | 0 | 45562.7 | 785418 | -6734.86 | 53 | 74 | 785418 | -1006734.86
5 | 15 | 18 | 1 | 24.6268 | 0 | 93.4203 | 0 | 27.6107 | 0 | 6.332 | 19.6531 | 0 | 0 | 0 | 0 | 171.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27759.3 | 0 | 27759.3 | 545998 | -9925 | 52 | 73 | 545998 | -1009925
5 | 15 | 19 | 1 | 19.0659 | 0 | 62.7906 | 0 | 8.4545 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 1.2 | 105.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19747.8 | 0 | 19747.8 | 186254 | 0 | 53 | 68 | 186254 | -1000000
5 | 15 | 20 | 1 | 18.6484 | 0 | 54.6418 | 0 | 6.7197 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4 | 98.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18859 | 0 | 18859 | 165965 | 0 | 51 | 62 | 165965 | -1000000
5 | 15 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.0663 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 7.2 | 91.2843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11728.3 | 0 | 11728.3 | 152766 | 0 | 50 | 57 | 152766 | -1000000
5 | 15 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.0704 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11442.3 | 0 | 11442.3 | 141661 | 0 | 49 | 55 | 141661 | -1000000
5 | 15 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.8457 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9945.82 | 0 | 9945.82 | 136850 | 0 | 47 | 52 | 136850 | -1000000
5 | 15 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.7798 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.16 | 0 | 9946.16 | 135465 | 0 | 46 | 50 | 135465 | -1000000
5 | 16 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7426 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.43 | 0 | 9946.43 | 134660 | 0 | 46 | 49 | 134660 | -1000000
5 | 16 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7031 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.28 | 0 | 9947.28 | 133795 | 0 | 45 | 47 | 133795 | -1000000
5 | 16 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6654 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9948.18 | 0 | 9948.18 | 132970 | 0 | 44 | 46 | 132970 | -1000000
5 | 16 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.798 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 3.2 | 80.9417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11053 | 0 | 11053 | 135934 | 0 | 44 | 46 | 135934 | -1000000
5 | 16 | 5 | 2 | 24.1569 | 0 | 69.9783 | 0 | 11.3783 | 0 | 5.9192 | 12.9754 | 0 | 0 | 0 | 1.6 | 126.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13510.8 | 0 | 13510.8 | 182473 | -7408.76 | 44 | 45 | 182473 | -1007408.76
5 | 16 | 6 | 2 | 39.0719 | 0 | 140.608 | 0 | 22.93 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 227.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36654.4 | 0 | 36654.4 | 327613 | -50991.9 | 44 | 45 | 327613 | -1050991.9
5 | 16 | 7 | 2 | 38.9703 | 0 | 168.222 | 0 | 34.1567 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40212.2 | 0 | 40212.2 | 458881 | -96848.5 | 48 | 51 | 458881 | -1096848.5
5 | 16 | 8 | 2 | 39.7499 | 0 | 173.795 | 0 | 32.3928 | 0 | 6.332 | 19.0526 | 0 | 0 | 0 | 0 | 271.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50900.1 | 0 | 50900.1 | 500175 | -45801.9 | 51 | 57 | 500175 | -1045801.9
5 | 16 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 39.5643 | 0 | 6.332 | 19.4089 | 0 | 0 | 0 | 0 | 278.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79385 | 0 | 79385 | 585971 | -19392.1 | 54 | 63 | 585971 | -1019392.1
5 | 16 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 49.1186 | 0 | 6.332 | 20.0037 | 0 | 0 | 0 | 0 | 279.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81165.1 | 0 | 81165.1 | 675625 | -11136.2 | 56 | 68 | 675625 | -1011136.2
5 | 16 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 48.5163 | 0 | 6.332 | 20.583 | 0 | 0 | 0 | 0 | 265.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81164.6 | 0 | 81164.6 | 676533 | -8839.05 | 57 | 72 | 676533 | -1008839.05
5 | 16 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 42.2635 | 0 | 25.335 | 20.8595 | 0 | 0 | 0 | 0 | 278.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81164.4 | 0 | 81164.4 | 787089 | -8450.17 | 57 | 77 | 787089 | -1008450.17
5 | 16 | 13 | 2 | 41.2693 | 0 | 165.698 | 0 | 50.2758 | 0 | 25.335 | 21.959 | 0 | 0 | 0 | 0 | 304.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81163.9 | 0 | 81163.9 | 874145 | -6871.06 | 57 | 77 | 874145 | -1006871.06
5 | 16 | 14 | 2 | 40.6342 | 0 | 172.702 | 0 | 53.3326 | 0 | 25.335 | 22.0717 | 0 | 0 | 0 | 0 | 314.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79383.3 | 0 | 79383.3 | 922610 | -6981.64 | 56 | 77 | 922610 | -1006981.64
5 | 16 | 15 | 2 | 40.5504 | 0 | 173.986 | 0 | 53.8769 | 0 | 25.335 | 22.3661 | 0 | 0 | 0 | 0 | 316.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72262 | 0 | 72262 | 932548 | -6680.32 | 56 | 77 | 932548 | -1006680.32
5 | 16 | 16 | 2 | 40.2907 | 0 | 169.782 | 0 | 51.6191 | 0 | 25.335 | 22.6381 | 0 | 0 | 0 | 0 | 309.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59799.4 | 0 | 59799.4 | 905878 | -5747.32 | 56 | 76 | 905878 | -1005747.32
5 | 16 | 17 | 2 | 35.7156 | 0 | 152.497 | 0 | 45.7164 | 0 | 25.335 | 22.5203 | 0 | 0 | 0 | 0 | 281.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45556.4 | 0 | 45556.4 | 811524 | -4427.02 | 56 | 75 | 811524 | -1004427.02
5 | 16 | 18 | 2 | 24.9781 | 0 | 93.4203 | 0 | 29.1643 | 0 | 25.335 | 19.9225 | 0 | 0 | 0 | 0 | 192.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27753.4 | 0 | 27753.4 | 568856 | -3739.63 | 55 | 74 | 568856 | -1003739.63
5 | 16 | 19 | 2 | 20.925 | 0 | 62.7906 | 0 | 9.387 | 0 | 5.5049 | 8.818 | 0 | 0 | 0 | 1.2 | 108.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19742 | 0 | 19742 | 190835 | 0 | 55 | 71 | 190835 | -1000000
5 | 16 | 20 | 2 | 18.6702 | 0 | 54.6418 | 0 | 8.2895 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 4 | 99.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18853.4 | 0 | 18853.4 | 170607 | 0 | 55 | 69 | 170607 | -1000000
5 | 16 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.2402 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11721.3 | 0 | 11721.3 | 157094 | 0 | 54 | 66 | 157094 | -1000000
5 | 16 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.1995 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11434.9 | 0 | 11434.9 | 145898 | 0 | 53 | 65 | 145898 | -1000000
5 | 16 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9274 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 5.6 | 79.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.98 | 0 | 9937.98 | 141028 | 0 | 52 | 64 | 141028 | -1000000
5 | 16 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8144 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.09 | 0 | 9938.09 | 139464 | 0 | 51 | 63 | 139464 | -1000000
5 | 17 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.1528 | 0 | 5.4877 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.22 | 0 | 9938.22 | 138592 | 0 | 50 | 60 | 138592 | -1000000
5 | 17 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8778 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.4 | 0 | 9938.4 | 137616 | 0 | 49 | 58 | 137616 | -1000000
5 | 17 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8415 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.57 | 0 | 9938.57 | 136825 | 0 | 48 | 55 | 136825 | -1000000
5 | 17 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9672 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.6 | 0 | 11042.6 | 139635 | 0 | 47 | 53 | 139635 | -1000000
5 | 17 | 5 | 3 | 24.2472 | 0 | 69.9783 | 0 | 9.0578 | 0 | 5.4887 | 8.818 | 0 | 0 | 0 | 1.6 | 119.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13499.7 | 0 | 13499.7 | 186128 | 0 | 46 | 50 | 186128 | -1000000
5 | 17 | 6 | 3 | 44.9383 | 0 | 140.608 | 0 | 27.0709 | 0 | 6.332 | 19.4228 | 0 | 0 | 0 | 0 | 238.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36642.8 | 0 | 36642.8 | 359326 | -29870.1 | 45 | 48 | 359326 | -1029870.1
5 | 17 | 7 | 3 | 39.2141 | 0 | 168.222 | 0 | 30.0611 | 0 | 6.332 | 19.1954 | 0 | 0 | 0 | 0 | 263.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40200.2 | 0 | 40200.2 | 445006 | -34349.6 | 46 | 50 | 445006 | -1034349.6
5 | 17 | 8 | 3 | 39.8278 | 0 | 173.795 | 0 | 30.9353 | 0 | 6.332 | 19.161 | 0 | 0 | 0 | 0 | 270.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50893 | 0 | 50893 | 508494 | -63113.8 | 46 | 51 | 508494 | -1063113.8
5 | 17 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 32.4086 | 0 | 6.332 | 19.2621 | 0 | 0 | 0 | 0 | 270.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79378.3 | 0 | 79378.3 | 521421 | -45081.1 | 46 | 53 | 521421 | -1045081.1
5 | 17 | 10 | 3 | 41.5039 | 0 | 163.102 | 0 | 32.2755 | 0 | 6.332 | 19.5313 | 0 | 0 | 0 | 0 | 262.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81159.2 | 0 | 81159.2 | 507850 | -22775.9 | 48 | 56 | 507850 | -1022775.9
5 | 17 | 11 | 3 | 40.9509 | 0 | 149.692 | 0 | 32.0105 | 0 | 6.332 | 19.4766 | 0 | 0 | 0 | 0 | 248.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81159.1 | 0 | 81159.1 | 495420 | -12282 | 49 | 58 | 495420 | -1012282
5 | 17 | 12 | 3 | 39.8278 | 0 | 150.207 | 0 | 33.3548 | 0 | 6.332 | 19.7049 | 0 | 0 | 0 | 0 | 249.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81159.3 | 0 | 81159.3 | 527077 | -9700.83 | 50 | 61 | 527077 | -1009700.83
5 | 17 | 13 | 3 | 41.233 | 0 | 165.698 | 0 | 33.2282 | 0 | 25.335 | 20.4215 | 0 | 0 | 0 | 0 | 285.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81159.7 | 0 | 81159.7 | 617065 | -9877.04 | 51 | 62 | 617065 | -1009877.04
5 | 17 | 14 | 3 | 40.6469 | 0 | 172.702 | 0 | 36.513 | 0 | 25.335 | 20.8039 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79379.4 | 0 | 79379.4 | 670678 | -11236.7 | 51 | 63 | 670678 | -1011236.7
5 | 17 | 15 | 3 | 40.544 | 0 | 173.986 | 0 | 38.4711 | 0 | 25.335 | 21.321 | 0 | 0 | 0 | 0 | 299.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72257.5 | 0 | 72257.5 | 704453 | -11920.8 | 51 | 64 | 704453 | -1011920.8
5 | 17 | 16 | 3 | 40.2938 | 0 | 169.782 | 0 | 36.6156 | 0 | 25.335 | 21.1068 | 0 | 0 | 0 | 0 | 293.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59794.7 | 0 | 59794.7 | 695323 | -12255.1 | 51 | 63 | 695323 | -1012255.1
5 | 17 | 17 | 3 | 35.482 | 0 | 152.497 | 0 | 31.4698 | 0 | 25.335 | 20.7168 | 0 | 0 | 0 | 0 | 265.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45552 | 0 | 45552 | 608125 | -10634.5 | 50 | 62 | 608125 | -1010634.5
5 | 17 | 18 | 3 | 24.8153 | 0 | 93.4203 | 0 | 22.0524 | 0 | 6.332 | 19.31 | 0 | 0 | 0 | 0 | 165.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27749.5 | 0 | 27749.5 | 405391 | -9162.53 | 49 | 61 | 405391 | -1009162.53
5 | 17 | 19 | 3 | 20.5016 | 0 | 62.7906 | 0 | 9.2033 | 0 | 5.4907 | 8.818 | 0 | 0 | 0 | 1.2 | 108.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19739.2 | 0 | 19739.2 | 190573 | 0 | 48 | 59 | 190573 | -1000000
5 | 17 | 20 | 3 | 18.6063 | 0 | 54.6418 | 0 | 8.4018 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4 | 99.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18850.8 | 0 | 18850.8 | 170659 | 0 | 47 | 58 | 170659 | -1000000
5 | 17 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.7814 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11719.9 | 0 | 11719.9 | 157184 | 0 | 46 | 56 | 157184 | -1000000
5 | 17 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.264 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11434.5 | 0 | 11434.5 | 145896 | 0 | 44 | 55 | 145896 | -1000000
5 | 17 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.0329 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.5 | 0 | 9938.5 | 140945 | 0 | 42 | 53 | 140945 | -1000000
5 | 17 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.9532 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.5 | 0 | 9939.5 | 139255 | 0 | 40 | 52 | 139255 | -1000000
5 | 18 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.914 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.46 | 0 | 9940.46 | 138409 | 0 | 39 | 50 | 138409 | -1000000
5 | 18 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8689 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9941.51 | 0 | 9941.51 | 137420 | 0 | 38 | 49 | 137420 | -1000000
5 | 18 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.1007 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.57 | 0 | 9942.57 | 136509 | -6464.48 | 37 | 47 | 136509 | -1006464.48
5 | 18 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.9515 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 3.2 | 81.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11047.4 | 0 | 11047.4 | 139291 | 0 | 37 | 46 | 139291 | -1000000
5 | 18 | 5 | 4 | 24.1224 | 0 | 69.9783 | 0 | 9.0299 | 0 | 5.9064 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13505.3 | 0 | 13505.3 | 185512 | -1650.06 | 37 | 44 | 185512 | -1001650.06
5 | 18 | 6 | 4 | 38.4605 | 0 | 140.608 | 0 | 22.2514 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 226.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36649.2 | 0 | 36649.2 | 330498 | -47570.5 | 36 | 43 | 330498 | -1047570.5
5 | 18 | 7 | 4 | 39.0438 | 0 | 168.222 | 0 | 32.4457 | 0 | 6.332 | 19.0475 | 0 | 0 | 0 | 0 | 265.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40207 | 0 | 40207 | 461896 | -134721 | 38 | 46 | 461896 | -1134721
5 | 18 | 8 | 4 | 39.6631 | 0 | 173.795 | 0 | 34.6523 | 0 | 6.332 | 19.1296 | 0 | 0 | 0 | 0 | 273.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50895.7 | 0 | 50895.7 | 487314 | -94984.1 | 40 | 50 | 487314 | -1094984.1
5 | 18 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 37.4139 | 0 | 6.332 | 19.2485 | 0 | 0 | 0 | 0 | 275.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79380.8 | 0 | 79380.8 | 517789 | -70737.8 | 41 | 53 | 517789 | -1070737.8
5 | 18 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 31.705 | 0 | 6.332 | 19.5574 | 0 | 0 | 0 | 0 | 261.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81161 | 0 | 81161 | 503264 | -34844.2 | 43 | 56 | 503264 | -1034844.2
5 | 18 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 33.1609 | 0 | 6.332 | 19.8102 | 0 | 0 | 0 | 0 | 249.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81161.1 | 0 | 81161.1 | 507728 | -14323.1 | 44 | 60 | 507728 | -1014323.1
5 | 18 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 39.6766 | 0 | 6.332 | 20.0619 | 0 | 0 | 0 | 0 | 256.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81160.7 | 0 | 81160.7 | 577172 | -11937.5 | 45 | 63 | 577172 | -1011937.5
5 | 18 | 13 | 4 | 41.246 | 0 | 165.698 | 0 | 35.7172 | 0 | 25.335 | 21.1246 | 0 | 0 | 0 | 0 | 289.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81160.7 | 0 | 81160.7 | 653702 | -10251.3 | 46 | 64 | 653702 | -1010251.3
5 | 18 | 14 | 4 | 40.6559 | 0 | 172.702 | 0 | 40.8119 | 0 | 25.335 | 21.2752 | 0 | 0 | 0 | 0 | 300.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79380.2 | 0 | 79380.2 | 730312 | -9749.13 | 47 | 66 | 730312 | -1009749.13
5 | 18 | 15 | 4 | 40.5417 | 0 | 173.986 | 0 | 43.3517 | 0 | 25.335 | 21.5913 | 0 | 0 | 0 | 0 | 304.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72258.2 | 0 | 72258.2 | 778784 | -11246.7 | 48 | 67 | 778784 | -1011246.7
5 | 18 | 16 | 4 | 40.2951 | 0 | 169.782 | 0 | 40.7634 | 0 | 25.335 | 21.4388 | 0 | 0 | 0 | 0 | 297.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59795.5 | 0 | 59795.5 | 757175 | -11358.7 | 48 | 66 | 757175 | -1011358.7
5 | 18 | 17 | 4 | 35.4821 | 0 | 152.497 | 0 | 36.5637 | 0 | 25.335 | 20.9232 | 0 | 0 | 0 | 0 | 270.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45552.8 | 0 | 45552.8 | 681088 | -9289.03 | 48 | 66 | 681088 | -1009289.03
5 | 18 | 18 | 4 | 24.5964 | 0 | 93.4203 | 0 | 24.588 | 0 | 25.335 | 19.5735 | 0 | 0 | 0 | 0 | 187.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27750 | 0 | 27750 | 462153 | -8642.33 | 47 | 65 | 462153 | -1008642.33
5 | 18 | 19 | 4 | 19.3308 | 0 | 62.7906 | 0 | 9.315 | 0 | 8.2993 | 8.818 | 0 | 0 | 0 | 1.2 | 109.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19739.7 | 0 | 19739.7 | 190847 | 0 | 46 | 62 | 190847 | -1000000
5 | 18 | 20 | 4 | 18.6382 | 0 | 54.6418 | 0 | 7.8974 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4 | 99.4745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18851.3 | 0 | 18851.3 | 170845 | 0 | 44 | 59 | 170845 | -1000000
5 | 18 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7857 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11720.1 | 0 | 11720.1 | 157278 | 0 | 42 | 56 | 157278 | -1000000
5 | 18 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2816 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11434.5 | 0 | 11434.5 | 146286 | 0 | 41 | 51 | 146286 | -1000000
5 | 18 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0448 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.43 | 0 | 9938.43 | 141203 | 0 | 40 | 47 | 141203 | -1000000
5 | 18 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9555 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.44 | 0 | 9939.44 | 139302 | 0 | 37 | 42 | 139302 | -1000000
5 | 19 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9043 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.62 | 0 | 9940.62 | 138194 | 0 | 37 | 40 | 138194 | -1000000
5 | 19 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.0091 | 0 | 5.8977 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.7148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.03 | 0 | 9942.03 | 137185 | -9051.15 | 36 | 39 | 137185 | -1009051.15
5 | 19 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8094 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 79.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9943.65 | 0 | 9943.65 | 136118 | 0 | 34 | 37 | 136118 | -1000000
5 | 19 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.2228 | 0 | 5.9017 | 12.9754 | 0 | 0 | 0 | 3.2 | 89.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11049.1 | 0 | 11049.1 | 138723 | -15599.7 | 35 | 38 | 138723 | -1015599.7
5 | 19 | 5 | 5 | 24.0255 | 0 | 69.9783 | 0 | 8.9949 | 0 | 5.906 | 12.9754 | 0 | 0 | 0 | 1.6 | 123.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13507.7 | 0 | 13507.7 | 184741 | -4001.63 | 36 | 38 | 184741 | -1004001.63
5 | 19 | 6 | 5 | 38.8807 | 0 | 140.608 | 0 | 22.7381 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 227.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36652 | 0 | 36652 | 329854 | -101146 | 36 | 39 | 329854 | -1101146
5 | 19 | 7 | 5 | 39.0842 | 0 | 168.222 | 0 | 31.6604 | 0 | 7.5863 | 19.0363 | 0 | 0 | 0 | 0 | 265.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40210.5 | 0 | 40210.5 | 458824 | -167745 | 41 | 45 | 458824 | -1167745
5 | 19 | 8 | 5 | 39.7862 | 0 | 173.795 | 0 | 36.7405 | 0 | 6.332 | 19.0834 | 0 | 0 | 0 | 0 | 275.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50897.4 | 0 | 50897.4 | 487836 | -91377.2 | 44 | 52 | 487836 | -1091377.2
5 | 19 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 38.0399 | 0 | 6.332 | 19.1491 | 0 | 0 | 0 | 0 | 276.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79382.2 | 0 | 79382.2 | 530466 | -43203.1 | 47 | 58 | 530466 | -1043203.1
5 | 19 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 37.2111 | 0 | 6.332 | 19.6439 | 0 | 0 | 0 | 0 | 267.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81162.6 | 0 | 81162.6 | 549437 | -18020.9 | 48 | 62 | 549437 | -1018020.9
5 | 19 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 39.4466 | 0 | 6.332 | 19.9172 | 0 | 0 | 0 | 0 | 256.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81162.9 | 0 | 81162.9 | 560995 | -11294.4 | 49 | 65 | 560995 | -1011294.4
5 | 19 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 45.473 | 0 | 6.332 | 20.1715 | 0 | 0 | 0 | 0 | 261.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81162.3 | 0 | 81162.3 | 652880 | -10353.8 | 49 | 69 | 652880 | -1010353.8
5 | 19 | 13 | 5 | 41.2671 | 0 | 165.698 | 0 | 42.5836 | 0 | 25.335 | 21.4317 | 0 | 0 | 0 | 0 | 296.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81161.5 | 0 | 81161.5 | 750132 | -8771.37 | 50 | 71 | 750132 | -1008771.37
5 | 19 | 14 | 5 | 40.6713 | 0 | 172.702 | 0 | 48.4187 | 0 | 25.335 | 21.5554 | 0 | 0 | 0 | 0 | 308.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79380.9 | 0 | 79380.9 | 841890 | -8450.01 | 51 | 73 | 841890 | -1008450.01
5 | 19 | 15 | 5 | 40.5643 | 0 | 173.986 | 0 | 52.9605 | 0 | 25.335 | 21.9296 | 0 | 0 | 0 | 0 | 314.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72259 | 0 | 72259 | 909499 | -8075.48 | 52 | 75 | 909499 | -1008075.48
5 | 19 | 16 | 5 | 40.3045 | 0 | 169.782 | 0 | 50.2501 | 0 | 25.335 | 22.1363 | 0 | 0 | 0 | 0 | 307.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59796.6 | 0 | 59796.6 | 896442 | -8872.15 | 52 | 74 | 896442 | -1008872.15
5 | 19 | 17 | 5 | 35.4829 | 0 | 152.497 | 0 | 48.7406 | 0 | 25.335 | 21.2617 | 0 | 0 | 0 | 0 | 283.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45553.9 | 0 | 45553.9 | 844849 | -15541.8 | 52 | 74 | 844849 | -1015541.8
5 | 19 | 18 | 5 | 24.6058 | 0 | 93.4203 | 0 | 32.5194 | 0 | 25.335 | 19.497 | 0 | 0 | 0 | 0 | 195.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27750.7 | 0 | 27750.7 | 611847 | -22043.8 | 52 | 73 | 611847 | -1022043.8
5 | 19 | 19 | 5 | 19.3569 | 0 | 62.7906 | 0 | 8.7835 | 0 | 5.4904 | 8.818 | 0 | 0 | 0 | 1.2 | 106.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19740 | 0 | 19740 | 192149 | 0 | 53 | 68 | 192149 | -1000000
5 | 19 | 20 | 5 | 18.4653 | 0 | 54.6418 | 0 | 6.9838 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4 | 98.3886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18851.5 | 0 | 18851.5 | 171682 | 0 | 52 | 62 | 171682 | -1000000
5 | 19 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.308 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11719.4 | 0 | 11719.4 | 158048 | 0 | 51 | 57 | 158048 | -1000000
5 | 19 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.297 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11433.3 | 0 | 11433.3 | 146616 | 0 | 49 | 54 | 146616 | -1000000
5 | 19 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.0648 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.81 | 0 | 9936.81 | 141642 | 0 | 47 | 52 | 141642 | -1000000
5 | 19 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.9754 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.54 | 0 | 9937.54 | 139735 | 0 | 45 | 49 | 139735 | -1000000
5 | 20 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9262 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.39 | 0 | 9938.39 | 138675 | 0 | 44 | 47 | 138675 | -1000000
5 | 20 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8725 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.05 | 0 | 9940.05 | 137497 | 0 | 42 | 45 | 137497 | -1000000
5 | 20 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8325 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9941.49 | 0 | 9941.49 | 136626 | 0 | 41 | 43 | 136626 | -1000000
5 | 20 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.5336 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 3.2 | 80.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9943.09 | 0 | 9943.09 | 135793 | -7919.97 | 42 | 44 | 135793 | -1007919.97
5 | 20 | 5 | 6 | 6.3039 | 0 | 42.7453 | 0 | 6.7498 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 1.6 | 71.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9944.72 | 0 | 9944.72 | 134813 | 0 | 42 | 44 | 134813 | -1000000
5 | 20 | 6 | 6 | 5.0514 | 0 | 42.7453 | 0 | 6.7218 | 0 | 5.9 | 12.8287 | 0 | 0 | 0 | 0 | 73.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.48 | 0 | 9946.48 | 134207 | -1774.62 | 44 | 45 | 134207 | -1001774.62
5 | 20 | 7 | 6 | 4.6071 | 0 | 42.7453 | 0 | 13.9637 | 0 | 5.9469 | 18.8896 | 0 | 0 | 0 | 0 | 86.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9948.27 | 0 | 9948.27 | 183825 | -119847 | 47 | 51 | 183825 | -1119847
5 | 20 | 8 | 6 | 4.9421 | 0 | 42.7453 | 0 | 16.718 | 0 | 6.0136 | 18.8896 | 0 | 0 | 0 | 0 | 89.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9949.54 | 0 | 9949.54 | 204389 | -107883 | 50 | 58 | 204389 | -1107883
5 | 20 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 17.0318 | 0 | 6.0702 | 18.8896 | 0 | 0 | 0 | 0 | 90.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9954.5 | 0 | 9954.5 | 203438 | -50195.1 | 52 | 64 | 203438 | -1050195.1
5 | 20 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 19.8018 | 0 | 6.2667 | 18.8896 | 0 | 0 | 0 | 0 | 93.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9955.8 | 0 | 9955.8 | 244755 | -45022.3 | 53 | 68 | 244755 | -1045022.3
5 | 20 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 23.4667 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 96.9024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.57 | 0 | 9956.57 | 296258 | -35827.3 | 54 | 73 | 296258 | -1035827.3
5 | 20 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 26.2903 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 99.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.8 | 0 | 9956.8 | 343947 | -29548 | 54 | 77 | 343947 | -1029548
5 | 20 | 13 | 6 | 5.4726 | 0 | 42.7453 | 0 | 26.9728 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 100.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.78 | 0 | 9956.78 | 367895 | -26225 | 54 | 78 | 367895 | -1026225
5 | 20 | 14 | 6 | 5.4748 | 0 | 42.7453 | 0 | 10.8938 | 0 | 10.4229 | 12.8287 | 0 | 0 | 0 | 0 | 82.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.66 | 0 | 9956.66 | 177444 | 0 | 55 | 78 | 177444 | -1000000
5 | 20 | 15 | 6 | 5.4752 | 0 | 42.7453 | 0 | 10.7479 | 0 | 10.239 | 12.8287 | 0 | 0 | 0 | 0 | 82.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9956.45 | 0 | 9956.45 | 178326 | 0 | 55 | 79 | 178326 | -1000000
5 | 20 | 16 | 6 | 5.4744 | 0 | 42.7453 | 0 | 7.9749 | 0 | 7.4442 | 8.818 | 0 | 0 | 0 | 0 | 72.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9952.42 | 0 | 9952.42 | 130326 | 0 | 55 | 79 | 130326 | -1000000
5 | 20 | 17 | 6 | 5.4748 | 0 | 42.7453 | 0 | 7.8385 | 0 | 7.3783 | 8.818 | 0 | 0 | 0 | 0 | 72.2549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9949.46 | 0 | 9949.46 | 130163 | 0 | 55 | 78 | 130163 | -1000000
5 | 20 | 18 | 6 | 5.4763 | 0 | 42.7453 | 0 | 7.7756 | 0 | 7.3578 | 8.818 | 0 | 0 | 0 | 0 | 72.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.57 | 0 | 9947.57 | 130095 | 0 | 55 | 78 | 130095 | -1000000
5 | 20 | 19 | 6 | 7.0074 | 0 | 42.7453 | 0 | 6.5038 | 0 | 6.5511 | 8.818 | 0 | 0 | 0 | 1.2 | 72.8255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9945.78 | 0 | 9945.78 | 130050 | 0 | 54 | 72 | 130050 | -1000000
5 | 20 | 20 | 6 | 8.6741 | 0 | 42.7453 | 0 | 5.1344 | 0 | 5.5019 | 8.818 | 0 | 0 | 0 | 4 | 74.8737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9944.52 | 0 | 9944.52 | 129545 | 0 | 52 | 66 | 129545 | -1000000
5 | 20 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 4.9539 | 0 | 5.5098 | 8.818 | 0 | 0 | 0 | 7.2 | 78.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9943.45 | 0 | 9943.45 | 129205 | 0 | 50 | 60 | 129205 | -1000000
5 | 20 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4765 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 6.4 | 78.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.86 | 0 | 9942.86 | 128844 | 0 | 49 | 57 | 128844 | -1000000
5 | 20 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4609 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 5.6 | 77.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9942.83 | 0 | 9942.83 | 128502 | 0 | 48 | 54 | 128502 | -1000000
5 | 20 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.4385 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712.68 | 0 | 3712.68 | 128010 | 0 | 47 | 51 | 128010 | -1000000
5 | 21 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4157 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 73.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3713.33 | 0 | 3713.33 | 127511 | 0 | 46 | 50 | 127511 | -1000000
5 | 21 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3964 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 4.8 | 73.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714.35 | 0 | 3714.35 | 127090 | 0 | 45 | 48 | 127090 | -1000000
5 | 21 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3763 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 4.8 | 73.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715.53 | 0 | 3715.53 | 126648 | 0 | 44 | 47 | 126648 | -1000000
5 | 21 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4254 | 0 | 5.9027 | 12.8287 | 0 | 0 | 0 | 3.2 | 76.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3716.81 | 0 | 3716.81 | 127749 | -5572.18 | 45 | 48 | 127749 | -1005572.18
5 | 21 | 5 | 7 | 5.0441 | 0 | 42.7453 | 0 | 6.353 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 1.6 | 70.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3718.15 | 0 | 3718.15 | 126119 | 0 | 47 | 49 | 126119 | -1000000
5 | 21 | 6 | 7 | 4.042 | 0 | 42.7453 | 0 | 6.3318 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 0 | 67.4227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719.54 | 0 | 3719.54 | 125676 | 0 | 48 | 50 | 125676 | -1000000
5 | 21 | 7 | 7 | 3.6892 | 0 | 42.7453 | 0 | 6.3253 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 0 | 67.0634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.98 | 0 | 3720.98 | 125538 | 0 | 51 | 56 | 125538 | -1000000
5 | 21 | 8 | 7 | 3.7973 | 0 | 42.7453 | 0 | 6.737 | 0 | 5.8996 | 12.8287 | 0 | 0 | 0 | 0 | 72.0078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3721.92 | 0 | 3721.92 | 128206 | -5499.55 | 54 | 61 | 128206 | -1005499.55
5 | 21 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.1525 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 0 | 69.3421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3721.59 | 0 | 3721.59 | 125087 | 0 | 55 | 67 | 125087 | -1000000
5 | 21 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.8 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 0 | 68.9882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.72 | 0 | 3720.72 | 125162 | 0 | 56 | 71 | 125162 | -1000000
5 | 21 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.4536 | 0 | 5.5117 | 12.8287 | 0 | 0 | 0 | 0 | 74.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719.47 | 0 | 3719.47 | 155043 | 0 | 57 | 75 | 155043 | -1000000
5 | 21 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.8562 | 0 | 5.4977 | 12.8287 | 0 | 0 | 0 | 0 | 74.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3717.72 | 0 | 3717.72 | 165171 | 0 | 57 | 79 | 165171 | -1000000
5 | 21 | 13 | 7 | 4.147 | 0 | 42.7453 | 0 | 9.2482 | 0 | 5.5064 | 12.8287 | 0 | 0 | 0 | 0 | 74.4755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715.94 | 0 | 3715.94 | 173010 | 0 | 57 | 80 | 173010 | -1000000
5 | 21 | 14 | 7 | 4.1481 | 0 | 42.7453 | 0 | 9.5782 | 0 | 5.5151 | 12.8287 | 0 | 0 | 0 | 0 | 74.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3714.43 | 0 | 3714.43 | 179621 | 0 | 57 | 81 | 179621 | -1000000
5 | 21 | 15 | 7 | 4.1485 | 0 | 42.7453 | 0 | 9.6547 | 0 | 5.5172 | 12.8287 | 0 | 0 | 0 | 0 | 74.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3712.88 | 0 | 3712.88 | 181074 | 0 | 57 | 82 | 181074 | -1000000
5 | 21 | 16 | 7 | 4.1485 | 0 | 42.7453 | 0 | 6.9381 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3711.1 | 0 | 3711.1 | 125542 | 0 | 57 | 81 | 125542 | -1000000
5 | 21 | 17 | 7 | 4.149 | 0 | 42.7453 | 0 | 8.9306 | 0 | 5.4992 | 10.866 | 0 | 0 | 0 | 0 | 72.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.37 | 0 | 3709.37 | 167193 | 0 | 56 | 80 | 167193 | -1000000
5 | 21 | 18 | 7 | 4.1497 | 0 | 42.7453 | 0 | 6.9351 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707.74 | 0 | 3707.74 | 125716 | 0 | 56 | 79 | 125716 | -1000000
5 | 21 | 19 | 7 | 5.2089 | 0 | 42.7453 | 0 | 6.898 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 1.2 | 70.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.23 | 0 | 3706.23 | 125662 | 0 | 55 | 76 | 125662 | -1000000
5 | 21 | 20 | 7 | 6.4981 | 0 | 42.7453 | 0 | 5.9498 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 4 | 73.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3704.96 | 0 | 3704.96 | 125659 | 0 | 54 | 72 | 125659 | -1000000
5 | 21 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.841 | 0 | 5.4879 | 8.818 | 0 | 0 | 0 | 7.2 | 76.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.86 | 0 | 3703.86 | 125569 | 0 | 53 | 69 | 125569 | -1000000
5 | 21 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3412 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 6.4 | 76.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.07 | 0 | 3703.07 | 125524 | 0 | 53 | 68 | 125524 | -1000000
5 | 21 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0012 | 0 | 5.4871 | 8.818 | 0 | 0 | 0 | 5.6 | 75.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702.63 | 0 | 3702.63 | 125459 | 0 | 53 | 66 | 125459 | -1000000
5 | 21 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.2397 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9933 | 0 | 9933 | 125644 | 0 | 53 | 65 | 125644 | -1000000
5 | 22 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5025 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.88 | 0 | 9932.88 | 125624 | 0 | 54 | 65 | 125624 | -1000000
5 | 22 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2013 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.05 | 0 | 9932.05 | 125555 | 0 | 55 | 64 | 125555 | -1000000
5 | 22 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.45 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9931.72 | 0 | 9931.72 | 125263 | 0 | 55 | 64 | 125263 | -1000000
5 | 22 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.3281 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 3.2 | 80.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11035.1 | 0 | 11035.1 | 129078 | 0 | 55 | 63 | 129078 | -1000000
5 | 22 | 5 | 1 | 24.005 | 0 | 69.9783 | 0 | 10.7545 | 0 | 5.5265 | 12.8287 | 0 | 0 | 0 | 1.6 | 124.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13491.6 | 0 | 13491.6 | 234253 | 0 | 55 | 61 | 234253 | -1000000
5 | 22 | 6 | 1 | 38.1683 | 0 | 140.608 | 0 | 44.475 | 0 | 6.332 | 20.053 | 0 | 0 | 0 | 0 | 249.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36633.9 | 0 | 36633.9 | 682764 | -13828.9 | 55 | 60 | 682764 | -1013828.9
5 | 22 | 7 | 1 | 39.062 | 0 | 168.222 | 0 | 52.2037 | 0 | 6.332 | 20.7971 | 0 | 0 | 0 | 0 | 286.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40190.4 | 0 | 40190.4 | 765140 | -18263.7 | 57 | 63 | 765140 | -1018263.7
5 | 22 | 8 | 1 | 39.6631 | 0 | 173.795 | 0 | 54.2302 | 0 | 6.332 | 21.0758 | 0 | 0 | 0 | 0 | 295.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50886.7 | 0 | 50886.7 | 819267 | -12062.5 | 58 | 66 | 819267 | -1012062.5
5 | 22 | 9 | 1 | 40.6683 | 0 | 172.186 | 0 | 44.2459 | 0 | 6.332 | 21.7232 | 0 | 0 | 0 | 0 | 285.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79372.9 | 0 | 79372.9 | 876198 | -9974.98 | 59 | 69 | 876198 | -1009974.98
5 | 22 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 47.4877 | 0 | 6.332 | 22.0354 | 0 | 0 | 0 | 0 | 280.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81154.5 | 0 | 81154.5 | 922824 | -7431.8 | 60 | 72 | 922824 | -1007431.8
5 | 22 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 47.1182 | 0 | 6.332 | 22.4585 | 0 | 0 | 0 | 0 | 266.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81154.7 | 0 | 81154.7 | 908572 | -6414.36 | 61 | 74 | 908572 | -1006414.36
5 | 22 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 59.2961 | 0 | 6.332 | 21.8794 | 0 | 0 | 0 | 0 | 277.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81155.1 | 0 | 81155.1 | 998331 | -16625.8 | 62 | 77 | 998331 | -1016625.8
5 | 22 | 13 | 1 | 41.2512 | 0 | 165.698 | 0 | 57.3945 | 0 | 6.332 | 23.3144 | 0 | 0 | 0 | 0 | 293.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.1 | 0 | 81156.1 | 1110880 | -5110 | 63 | 78 | 1110880 | -1005110
5 | 22 | 14 | 1 | 40.6655 | 0 | 172.702 | 0 | 65.2878 | 0 | 6.332 | 23.2432 | 0 | 0 | 0 | 0 | 308.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79376.1 | 0 | 79376.1 | 1157860 | -5474.9 | 63 | 80 | 1157860 | -1005474.9
5 | 22 | 15 | 1 | 40.547 | 0 | 173.986 | 0 | 70.5464 | 0 | 6.332 | 23.1912 | 0 | 0 | 0 | 0 | 314.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72255.2 | 0 | 72255.2 | 1251740 | -5969.75 | 64 | 81 | 1251740 | -1005969.75
5 | 22 | 16 | 1 | 40.2788 | 0 | 169.782 | 0 | 69.1704 | 0 | 6.332 | 22.6112 | 0 | 0 | 0 | 0 | 308.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59792.9 | 0 | 59792.9 | 1227380 | -19166.5 | 63 | 79 | 1227380 | -1019166.5
5 | 22 | 17 | 1 | 35.4745 | 0 | 152.497 | 0 | 61.182 | 0 | 6.332 | 22.0451 | 0 | 0 | 0 | 0 | 277.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45550.5 | 0 | 45550.5 | 1112680 | -24687.5 | 62 | 78 | 1112680 | -1024687.5
5 | 22 | 18 | 1 | 24.8117 | 0 | 93.4203 | 0 | 38.1997 | 0 | 6.332 | 20.6972 | 0 | 0 | 0 | 0 | 183.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27747.7 | 0 | 27747.7 | 739668 | -14557.1 | 62 | 76 | 739668 | -1014557.1
5 | 22 | 19 | 1 | 19.0402 | 0 | 62.7906 | 0 | 10.4321 | 0 | 5.5429 | 8.818 | 0 | 0 | 0 | 1.2 | 107.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19736.6 | 0 | 19736.6 | 187469 | 0 | 61 | 75 | 187469 | -1000000
5 | 22 | 20 | 1 | 18.5174 | 0 | 54.6418 | 0 | 8.666 | 0 | 5.4931 | 8.818 | 0 | 0 | 0 | 4 | 100.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18847.3 | 0 | 18847.3 | 167536 | 0 | 60 | 74 | 167536 | -1000000
5 | 22 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.9609 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11713.9 | 0 | 11713.9 | 154374 | 0 | 59 | 73 | 154374 | -1000000
5 | 22 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.0758 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11426.5 | 0 | 11426.5 | 143768 | 0 | 59 | 71 | 143768 | -1000000
5 | 22 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.0614 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.86 | 0 | 9928.86 | 138813 | 0 | 58 | 70 | 138813 | -1000000
5 | 22 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6515 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.19 | 0 | 9928.19 | 137617 | 0 | 58 | 68 | 137617 | -1000000
5 | 23 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.1547 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.67 | 0 | 9927.67 | 136935 | 0 | 59 | 68 | 136935 | -1000000
5 | 23 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.1257 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.25 | 0 | 9927.25 | 136330 | 0 | 60 | 68 | 136330 | -1000000
5 | 23 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.0916 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9926.9 | 0 | 9926.9 | 135615 | 0 | 60 | 68 | 135615 | -1000000
5 | 23 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.95 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 3.2 | 81.0916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11030.3 | 0 | 11030.3 | 139170 | 0 | 61 | 67 | 139170 | -1000000
5 | 23 | 5 | 2 | 24.0726 | 0 | 69.9783 | 0 | 12.9164 | 0 | 5.6347 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13486.6 | 0 | 13486.6 | 261274 | 0 | 61 | 67 | 261274 | -1000000
5 | 23 | 6 | 2 | 39.6723 | 0 | 140.608 | 0 | 57.2747 | 0 | 6.332 | 21.3722 | 0 | 0 | 0 | 0 | 265.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36628.7 | 0 | 36628.7 | 922362 | -7408.75 | 61 | 66 | 922362 | -1007408.75
5 | 23 | 7 | 2 | 39.2206 | 0 | 168.222 | 0 | 48.4197 | 0 | 6.332 | 21.6801 | 0 | 0 | 0 | 0 | 283.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40185 | 0 | 40185 | 982053 | -9199.28 | 62 | 67 | 982053 | -1009199.28
5 | 23 | 8 | 2 | 39.6745 | 0 | 173.795 | 0 | 50.8408 | 0 | 6.332 | 22.1412 | 0 | 0 | 0 | 0 | 292.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50883.9 | 0 | 50883.9 | 1023990 | -9464.12 | 63 | 68 | 1023990 | -1009464.12
5 | 23 | 9 | 2 | 41.7554 | 0 | 172.186 | 0 | 52.5922 | 0 | 6.332 | 22.0718 | 0 | 0 | 0 | 0 | 294.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79370.9 | 0 | 79370.9 | 1052070 | -10873 | 64 | 69 | 1052070 | -1010873
5 | 23 | 10 | 2 | 41.8014 | 0 | 163.102 | 0 | 51.4752 | 0 | 6.332 | 22.178 | 0 | 0 | 0 | 0 | 284.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152.2 | 0 | 81152.2 | 1047060 | -9979.73 | 64 | 68 | 1047060 | -1009979.73
5 | 23 | 11 | 2 | 40.9621 | 0 | 149.692 | 0 | 47.9774 | 0 | 6.332 | 22.2146 | 0 | 0 | 0 | 0 | 267.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152 | 0 | 81152 | 970732 | -7273.79 | 65 | 68 | 970732 | -1007273.79
5 | 23 | 12 | 2 | 39.8961 | 0 | 150.207 | 0 | 46.7235 | 0 | 7.4597 | 21.9958 | 0 | 0 | 0 | 0 | 266.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152.3 | 0 | 81152.3 | 958118 | -7134.34 | 65 | 67 | 958118 | -1007134.34
5 | 23 | 13 | 2 | 41.5934 | 0 | 165.698 | 0 | 55.7357 | 0 | 25.335 | 22.5303 | 0 | 0 | 0 | 0 | 310.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152.8 | 0 | 81152.8 | 1100510 | -10491.9 | 66 | 68 | 1100510 | -1010491.9
5 | 23 | 14 | 2 | 40.8681 | 0 | 172.702 | 0 | 60.6292 | 0 | 25.335 | 22.924 | 0 | 0 | 0 | 0 | 322.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79372.7 | 0 | 79372.7 | 1133690 | -13147.1 | 66 | 69 | 1133690 | -1013147.1
5 | 23 | 15 | 2 | 40.7979 | 0 | 173.986 | 0 | 66.4662 | 0 | 25.335 | 23.2525 | 0 | 0 | 0 | 0 | 329.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72251.1 | 0 | 72251.1 | 1207060 | -14137.6 | 67 | 70 | 1207060 | -1014137.6
5 | 23 | 16 | 2 | 40.3041 | 0 | 169.782 | 0 | 63.0777 | 0 | 25.335 | 22.9554 | 0 | 0 | 0 | 0 | 321.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59788.8 | 0 | 59788.8 | 1188300 | -13711.9 | 66 | 70 | 1188300 | -1013711.9
5 | 23 | 17 | 2 | 35.4939 | 0 | 152.497 | 0 | 56.0499 | 0 | 6.332 | 22.5181 | 0 | 0 | 0 | 0 | 272.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45546.4 | 0 | 45546.4 | 1098910 | -10217.9 | 66 | 71 | 1098910 | -1010217.9
5 | 23 | 18 | 2 | 24.7578 | 0 | 93.4203 | 0 | 37.2469 | 0 | 6.332 | 20.4469 | 0 | 0 | 0 | 0 | 182.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27744.1 | 0 | 27744.1 | 752170 | -6207.46 | 66 | 71 | 752170 | -1006207.46
5 | 23 | 19 | 2 | 19.7599 | 0 | 62.7906 | 0 | 10.0628 | 0 | 5.5213 | 8.818 | 0 | 0 | 0 | 1.2 | 108.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19733.7 | 0 | 19733.7 | 191705 | 0 | 66 | 70 | 191705 | -1000000
5 | 23 | 20 | 2 | 18.507 | 0 | 54.6418 | 0 | 8.5973 | 0 | 5.4883 | 8.818 | 0 | 0 | 0 | 4 | 100.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18845.5 | 0 | 18845.5 | 171402 | 0 | 65 | 69 | 171402 | -1000000
5 | 23 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.9069 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11712.2 | 0 | 11712.2 | 158096 | 0 | 65 | 68 | 158096 | -1000000
5 | 23 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.0319 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11425.5 | 0 | 11425.5 | 147110 | 0 | 65 | 66 | 147110 | -1000000
5 | 23 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.014 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.17 | 0 | 9928.17 | 142050 | 0 | 64 | 65 | 142050 | -1000000
5 | 23 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.5971 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.96 | 0 | 9927.96 | 140395 | 0 | 63 | 63 | 140395 | -1000000
5 | 24 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0777 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.84 | 0 | 9927.84 | 139531 | 0 | 63 | 63 | 139531 | -1000000
5 | 24 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.039 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.8 | 0 | 9927.8 | 138699 | 0 | 63 | 63 | 138699 | -1000000
5 | 24 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0027 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.82 | 0 | 9927.82 | 137919 | 0 | 63 | 63 | 137919 | -1000000
5 | 24 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.8418 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 3.2 | 80.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11031.6 | 0 | 11031.6 | 140929 | 0 | 62 | 62 | 140929 | -1000000
5 | 24 | 5 | 3 | 24.2268 | 0 | 69.9783 | 0 | 12.083 | 0 | 5.577 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13488.3 | 0 | 13488.3 | 250641 | 0 | 61 | 62 | 250641 | -1000000
5 | 24 | 6 | 3 | 45.1599 | 0 | 140.608 | 0 | 47.2479 | 0 | 6.332 | 20.9437 | 0 | 0 | 0 | 0 | 260.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36630.8 | 0 | 36630.8 | 732941 | -8909.87 | 60 | 61 | 732941 | -1008909.87
5 | 24 | 7 | 3 | 39.2243 | 0 | 168.222 | 0 | 37.2327 | 0 | 6.332 | 20.5614 | 0 | 0 | 0 | 0 | 271.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40187.5 | 0 | 40187.5 | 798860 | -15311.5 | 59 | 60 | 798860 | -1015311.5
5 | 24 | 8 | 3 | 40.1702 | 0 | 173.795 | 0 | 36.8424 | 0 | 6.332 | 20.6173 | 0 | 0 | 0 | 0 | 277.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50884.5 | 0 | 50884.5 | 783631 | -18014.6 | 58 | 60 | 783631 | -1018014.6
5 | 24 | 9 | 3 | 41.2841 | 0 | 172.186 | 0 | 36.0666 | 0 | 6.332 | 20.6991 | 0 | 0 | 0 | 0 | 276.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79370.8 | 0 | 79370.8 | 767208 | -19449.7 | 57 | 59 | 767208 | -1019449.7
5 | 24 | 10 | 3 | 41.803 | 0 | 163.102 | 0 | 39.2034 | 0 | 6.332 | 20.5169 | 0 | 0 | 0 | 0 | 270.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81151.7 | 0 | 81151.7 | 751756 | -18247.8 | 57 | 59 | 751756 | -1018247.8
5 | 24 | 11 | 3 | 40.9369 | 0 | 149.692 | 0 | 35.7694 | 0 | 6.332 | 20.5215 | 0 | 0 | 0 | 0 | 253.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152.1 | 0 | 81152.1 | 695306 | -15391.6 | 57 | 60 | 695306 | -1015391.6
5 | 24 | 12 | 3 | 39.8388 | 0 | 150.207 | 0 | 33.9624 | 0 | 6.332 | 20.5541 | 0 | 0 | 0 | 0 | 250.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81152.5 | 0 | 81152.5 | 664329 | -14006.7 | 56 | 60 | 664329 | -1014006.7
5 | 24 | 13 | 3 | 41.5864 | 0 | 165.698 | 0 | 37.0991 | 0 | 6.4234 | 20.8635 | 0 | 0 | 0 | 0 | 271.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81153.3 | 0 | 81153.3 | 743032 | -17481 | 56 | 60 | 743032 | -1017481
5 | 24 | 14 | 3 | 40.8315 | 0 | 172.702 | 0 | 37.9051 | 0 | 25.335 | 21.2351 | 0 | 0 | 0 | 0 | 298.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79373.3 | 0 | 79373.3 | 773297 | -20163.5 | 56 | 59 | 773297 | -1020163.5
5 | 24 | 15 | 3 | 40.7216 | 0 | 173.986 | 0 | 37.9028 | 0 | 25.335 | 21.505 | 0 | 0 | 0 | 0 | 299.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72251.7 | 0 | 72251.7 | 778145 | -21223.2 | 55 | 59 | 778145 | -1021223.2
5 | 24 | 16 | 3 | 41.0318 | 0 | 169.782 | 0 | 37.2549 | 0 | 25.335 | 20.8103 | 0 | 0 | 0 | 0 | 294.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59789.3 | 0 | 59789.3 | 755394 | -21673.2 | 55 | 59 | 755394 | -1021673.2
5 | 24 | 17 | 3 | 36.1629 | 0 | 152.497 | 0 | 33.4114 | 0 | 6.332 | 20.1993 | 0 | 0 | 0 | 0 | 248.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45547.1 | 0 | 45547.1 | 647278 | -20075.2 | 55 | 58 | 647278 | -1020075.2
5 | 24 | 18 | 3 | 25.2323 | 0 | 93.4203 | 0 | 24.2447 | 0 | 6.332 | 19.1334 | 0 | 0 | 0 | 0 | 168.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27744.7 | 0 | 27744.7 | 421035 | -18387.3 | 55 | 58 | 421035 | -1018387.3
5 | 24 | 19 | 3 | 19.5363 | 0 | 62.7906 | 0 | 9.4794 | 0 | 5.4952 | 8.818 | 0 | 0 | 0 | 1.2 | 107.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19734.6 | 0 | 19734.6 | 190744 | 0 | 54 | 57 | 190744 | -1000000
5 | 24 | 20 | 3 | 18.6269 | 0 | 54.6418 | 0 | 8.4213 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4 | 99.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18846.5 | 0 | 18846.5 | 171088 | 0 | 54 | 55 | 171088 | -1000000
5 | 24 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.7927 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11715 | 0 | 11715 | 157429 | 0 | 53 | 54 | 157429 | -1000000
5 | 24 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2835 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11429.6 | 0 | 11429.6 | 146326 | 0 | 53 | 54 | 146326 | -1000000
5 | 24 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.057 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9933.51 | 0 | 9933.51 | 141472 | 0 | 54 | 55 | 141472 | -1000000
5 | 24 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.9787 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9934.47 | 0 | 9934.47 | 139812 | 0 | 54 | 55 | 139812 | -1000000
5 | 25 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9332 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9935.33 | 0 | 9935.33 | 138829 | 0 | 54 | 55 | 138829 | -1000000
5 | 25 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8926 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.16 | 0 | 9936.16 | 137941 | 0 | 54 | 55 | 137941 | -1000000
5 | 25 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8559 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.86 | 0 | 9936.86 | 137138 | 0 | 54 | 55 | 137138 | -1000000
5 | 25 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.9887 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.3 | 0 | 11041.3 | 140109 | 0 | 54 | 55 | 140109 | -1000000
5 | 25 | 5 | 4 | 24.2177 | 0 | 69.9783 | 0 | 9.0883 | 0 | 5.4891 | 8.818 | 0 | 0 | 0 | 1.6 | 119.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13498.5 | 0 | 13498.5 | 186798 | 0 | 54 | 55 | 186798 | -1000000
5 | 25 | 6 | 4 | 45.4536 | 0 | 140.608 | 0 | 32.379 | 0 | 6.332 | 19.3495 | 0 | 0 | 0 | 0 | 244.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36641.6 | 0 | 36641.6 | 410002 | -32850.3 | 54 | 55 | 410002 | -1032850.3
5 | 25 | 7 | 4 | 39.3695 | 0 | 168.222 | 0 | 25.7207 | 0 | 6.332 | 19.3007 | 0 | 0 | 0 | 0 | 258.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40198.6 | 0 | 40198.6 | 549602 | -21176.2 | 54 | 56 | 549602 | -1021176.2
5 | 25 | 8 | 4 | 39.7703 | 0 | 173.795 | 0 | 39.3587 | 0 | 6.332 | 19.3259 | 0 | 0 | 0 | 0 | 278.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50890.3 | 0 | 50890.3 | 597754 | -26135.4 | 54 | 58 | 597754 | -1026135.4
5 | 25 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 38.6623 | 0 | 6.332 | 19.7361 | 0 | 0 | 0 | 0 | 277.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79375.5 | 0 | 79375.5 | 635679 | -21847.3 | 54 | 59 | 635679 | -1021847.3
5 | 25 | 10 | 4 | 41.3843 | 0 | 163.102 | 0 | 37.9597 | 0 | 6.332 | 19.8175 | 0 | 0 | 0 | 0 | 268.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.3 | 0 | 81156.3 | 632312 | -19600.2 | 54 | 59 | 632312 | -1019600.2
5 | 25 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 34.8776 | 0 | 6.332 | 19.8188 | 0 | 0 | 0 | 0 | 251.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.2 | 0 | 81156.2 | 602307 | -16732.3 | 55 | 59 | 602307 | -1016732.3
5 | 25 | 12 | 4 | 39.8212 | 0 | 150.207 | 0 | 33.8179 | 0 | 6.332 | 19.8213 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.3 | 0 | 81156.3 | 592435 | -15228.8 | 55 | 59 | 592435 | -1015228.8
5 | 25 | 13 | 4 | 41.6816 | 0 | 165.698 | 0 | 37.7165 | 0 | 25.335 | 20.0849 | 0 | 0 | 0 | 0 | 290.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.8 | 0 | 81156.8 | 691487 | -18386.4 | 56 | 60 | 691487 | -1018386.4
5 | 25 | 14 | 4 | 40.882 | 0 | 172.702 | 0 | 39.303 | 0 | 25.335 | 20.5873 | 0 | 0 | 0 | 0 | 298.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79376.6 | 0 | 79376.6 | 736633 | -20194.8 | 56 | 61 | 736633 | -1020194.8
5 | 25 | 15 | 4 | 40.835 | 0 | 173.986 | 0 | 42.7157 | 0 | 25.335 | 20.9338 | 0 | 0 | 0 | 0 | 303.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72254.9 | 0 | 72254.9 | 797307 | -20235.3 | 57 | 62 | 797307 | -1020235.3
5 | 25 | 16 | 4 | 41.2085 | 0 | 169.782 | 0 | 42.6763 | 0 | 25.335 | 20.5417 | 0 | 0 | 0 | 0 | 299.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59792.2 | 0 | 59792.2 | 813775 | -20162.5 | 58 | 62 | 813775 | -1020162.5
5 | 25 | 17 | 4 | 36.1369 | 0 | 152.497 | 0 | 37.868 | 0 | 25.335 | 20.1356 | 0 | 0 | 0 | 0 | 271.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45549.7 | 0 | 45549.7 | 719285 | -16832.5 | 58 | 63 | 719285 | -1016832.5
5 | 25 | 18 | 4 | 25.084 | 0 | 93.4203 | 0 | 27.5694 | 0 | 6.332 | 19.1831 | 0 | 0 | 0 | 0 | 171.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27747.3 | 0 | 27747.3 | 492964 | -13635.4 | 59 | 63 | 492964 | -1013635.4
5 | 25 | 19 | 4 | 21.0022 | 0 | 62.7906 | 0 | 9.3905 | 0 | 5.4955 | 8.818 | 0 | 0 | 0 | 1.2 | 108.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19737 | 0 | 19737 | 191052 | 0 | 58 | 62 | 191052 | -1000000
5 | 25 | 20 | 4 | 18.6452 | 0 | 54.6418 | 0 | 7.9179 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4 | 99.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18848.8 | 0 | 18848.8 | 171297 | 0 | 58 | 60 | 171297 | -1000000
5 | 25 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.8032 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11717.2 | 0 | 11717.2 | 157659 | 0 | 57 | 59 | 157659 | -1000000
5 | 25 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2972 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11431.5 | 0 | 11431.5 | 146627 | 0 | 57 | 58 | 146627 | -1000000
5 | 25 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0606 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9935.18 | 0 | 9935.18 | 141547 | 0 | 56 | 56 | 141547 | -1000000
5 | 25 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9801 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9935.75 | 0 | 9935.75 | 139841 | 0 | 55 | 55 | 139841 | -1000000
5 | 26 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9376 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.12 | 0 | 9936.12 | 138925 | 0 | 55 | 55 | 138925 | -1000000
5 | 26 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9034 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.79 | 0 | 9936.79 | 138180 | 0 | 56 | 56 | 138180 | -1000000
5 | 26 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8636 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.42 | 0 | 9937.42 | 137308 | 0 | 56 | 56 | 137308 | -1000000
5 | 26 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9972 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11041.8 | 0 | 11041.8 | 140294 | 0 | 56 | 56 | 140294 | -1000000
5 | 26 | 5 | 5 | 24.12 | 0 | 69.9783 | 0 | 9.1068 | 0 | 5.4893 | 8.818 | 0 | 0 | 0 | 1.6 | 119.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13499 | 0 | 13499 | 187206 | 0 | 57 | 57 | 187206 | -1000000
5 | 26 | 6 | 5 | 39.1999 | 0 | 140.608 | 0 | 37.1391 | 0 | 6.332 | 19.3667 | 0 | 0 | 0 | 0 | 242.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36642 | 0 | 36642 | 462464 | -30151.7 | 57 | 57 | 462464 | -1030151.7
5 | 26 | 7 | 5 | 39.1084 | 0 | 168.222 | 0 | 30.7605 | 0 | 6.332 | 19.3595 | 0 | 0 | 0 | 0 | 263.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40199.1 | 0 | 40199.1 | 658159 | -17965.8 | 58 | 59 | 658159 | -1017965.8
5 | 26 | 8 | 5 | 39.7927 | 0 | 173.795 | 0 | 34.2756 | 0 | 6.332 | 19.4197 | 0 | 0 | 0 | 0 | 273.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50891 | 0 | 50891 | 720996 | -20797.1 | 59 | 61 | 720996 | -1020797.1
5 | 26 | 9 | 5 | 41.1394 | 0 | 172.186 | 0 | 37.1316 | 0 | 6.332 | 19.8179 | 0 | 0 | 0 | 0 | 276.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79376.2 | 0 | 79376.2 | 766450 | -18630.6 | 59 | 63 | 766450 | -1018630.6
5 | 26 | 10 | 5 | 41.6992 | 0 | 163.102 | 0 | 37.3555 | 0 | 6.332 | 19.978 | 0 | 0 | 0 | 0 | 268.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.8 | 0 | 81156.8 | 771620 | -16409.2 | 59 | 64 | 771620 | -1016409.2
5 | 26 | 11 | 5 | 40.7528 | 0 | 149.692 | 0 | 37.0797 | 0 | 10.3177 | 20.2901 | 0 | 0 | 0 | 0 | 258.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.7 | 0 | 81156.7 | 750971 | -12176.3 | 60 | 66 | 750971 | -1012176.3
5 | 26 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 41.5693 | 0 | 25.335 | 20.8865 | 0 | 0 | 0 | 0 | 277.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81156.9 | 0 | 81156.9 | 785488 | -10789.7 | 60 | 67 | 785488 | -1010789.7
5 | 26 | 13 | 5 | 41.2369 | 0 | 165.698 | 0 | 50.1035 | 0 | 25.335 | 21.7693 | 0 | 0 | 0 | 0 | 304.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81157.3 | 0 | 81157.3 | 890122 | -12887.1 | 60 | 69 | 890122 | -1012887.1
5 | 26 | 14 | 5 | 40.6483 | 0 | 172.702 | 0 | 54.4362 | 0 | 25.335 | 22.3137 | 0 | 0 | 0 | 0 | 315.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79377 | 0 | 79377 | 962499 | -15697.4 | 61 | 70 | 962499 | -1015697.4
5 | 26 | 15 | 5 | 40.532 | 0 | 173.986 | 0 | 59.6792 | 0 | 25.335 | 22.6291 | 0 | 0 | 0 | 0 | 322.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72255.1 | 0 | 72255.1 | 1037880 | -16541.4 | 61 | 72 | 1037880 | -1016541.4
5 | 26 | 16 | 5 | 40.2847 | 0 | 169.782 | 0 | 59.0999 | 0 | 25.335 | 22.6141 | 0 | 0 | 0 | 0 | 317.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59792.3 | 0 | 59792.3 | 1052340 | -15930.4 | 62 | 72 | 1052340 | -1015930.4
5 | 26 | 17 | 5 | 35.4752 | 0 | 152.497 | 0 | 52.9836 | 0 | 25.335 | 21.9145 | 0 | 0 | 0 | 0 | 288.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45549.7 | 0 | 45549.7 | 965929 | -12544.7 | 62 | 71 | 965929 | -1012544.7
5 | 26 | 18 | 5 | 24.7965 | 0 | 93.4203 | 0 | 34.0024 | 0 | 25.335 | 19.8778 | 0 | 0 | 0 | 0 | 197.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27747.2 | 0 | 27747.2 | 645797 | -8392.52 | 62 | 71 | 645797 | -1008392.52
5 | 26 | 19 | 5 | 19.3556 | 0 | 62.7906 | 0 | 9.3446 | 0 | 5.5005 | 8.818 | 0 | 0 | 0 | 1.2 | 107.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19736.9 | 0 | 19736.9 | 192108 | 0 | 61 | 68 | 192108 | -1000000
5 | 26 | 20 | 5 | 18.5011 | 0 | 54.6418 | 0 | 7.6007 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4 | 99.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18848.5 | 0 | 18848.5 | 172041 | 0 | 60 | 64 | 172041 | -1000000
5 | 26 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.1103 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 91.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11715.8 | 0 | 11715.8 | 158520 | 0 | 59 | 61 | 158520 | -1000000
5 | 26 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.3726 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11429.6 | 0 | 11429.6 | 147430 | 0 | 59 | 61 | 147430 | -1000000
5 | 26 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1396 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.78 | 0 | 9932.78 | 142458 | 0 | 59 | 61 | 142458 | -1000000
5 | 26 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0598 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9933.22 | 0 | 9933.22 | 140775 | 0 | 60 | 61 | 140775 | -1000000
5 | 27 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7095 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9933.6 | 0 | 9933.6 | 139542 | 0 | 59 | 60 | 139542 | -1000000
5 | 27 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9202 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9934.59 | 0 | 9934.59 | 138544 | 0 | 58 | 59 | 138544 | -1000000
5 | 27 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8776 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9935.15 | 0 | 9935.15 | 137613 | 0 | 57 | 58 | 137613 | -1000000
5 | 27 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8505 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 3.2 | 73.4765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9935.78 | 0 | 9935.78 | 137025 | 0 | 58 | 58 | 137025 | -1000000
5 | 27 | 5 | 6 | 6.3052 | 0 | 42.7453 | 0 | 6.8126 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9936.38 | 0 | 9936.38 | 136191 | 0 | 58 | 59 | 136191 | -1000000
5 | 27 | 6 | 6 | 5.5336 | 0 | 42.7453 | 0 | 6.7811 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 0 | 69.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.03 | 0 | 9937.03 | 135503 | 0 | 58 | 59 | 135503 | -1000000
5 | 27 | 7 | 6 | 4.6442 | 0 | 42.7453 | 0 | 17.1624 | 0 | 6.0568 | 18.8896 | 0 | 0 | 0 | 0 | 89.4982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.65 | 0 | 9937.65 | 223812 | -21411.1 | 59 | 61 | 223812 | -1021411.1
5 | 27 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 18.8729 | 0 | 6.1793 | 18.8896 | 0 | 0 | 0 | 0 | 91.6182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.07 | 0 | 9938.07 | 254903 | -17055.5 | 60 | 63 | 254903 | -1017055.5
5 | 27 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 20.824 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 94.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9947.94 | 0 | 9947.94 | 293268 | -20853.4 | 61 | 65 | 293268 | -1020853.4
5 | 27 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 23.7748 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 97.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9949.18 | 0 | 9949.18 | 330951 | -19076.6 | 62 | 67 | 330951 | -1019076.6
5 | 27 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 27.0294 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 100.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9950.15 | 0 | 9950.15 | 377808 | -18793.3 | 63 | 70 | 377808 | -1018793.3
5 | 27 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 27.927 | 0 | 6.332 | 18.9225 | 0 | 0 | 0 | 0 | 101.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9950.63 | 0 | 9950.63 | 412580 | -18563.7 | 64 | 72 | 412580 | -1018563.7
5 | 27 | 13 | 6 | 5.4704 | 0 | 42.7453 | 0 | 27.4885 | 0 | 6.332 | 18.9966 | 0 | 0 | 0 | 0 | 101.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.09 | 0 | 9951.09 | 430042 | -18694.8 | 64 | 73 | 430042 | -1018694.8
5 | 27 | 14 | 6 | 5.4713 | 0 | 42.7453 | 0 | 8.6036 | 0 | 7.8898 | 8.818 | 0 | 0 | 0 | 0 | 73.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.52 | 0 | 9951.52 | 131652 | 0 | 65 | 74 | 131652 | -1000000
5 | 27 | 15 | 6 | 5.4725 | 0 | 42.7453 | 0 | 8.3604 | 0 | 7.724 | 8.818 | 0 | 0 | 0 | 0 | 73.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9951.96 | 0 | 9951.96 | 131334 | 0 | 65 | 75 | 131334 | -1000000
5 | 27 | 16 | 6 | 5.4719 | 0 | 42.7453 | 0 | 7.9189 | 0 | 7.4233 | 8.818 | 0 | 0 | 0 | 0 | 72.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9946.67 | 0 | 9946.67 | 130974 | 0 | 64 | 75 | 130974 | -1000000
5 | 27 | 17 | 6 | 5.475 | 0 | 42.7453 | 0 | 7.4547 | 0 | 7.0991 | 8.818 | 0 | 0 | 0 | 0 | 71.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9943.83 | 0 | 9943.83 | 130843 | 0 | 64 | 74 | 130843 | -1000000
5 | 27 | 18 | 6 | 6.0104 | 0 | 42.7453 | 0 | 7.4571 | 0 | 7.2268 | 8.818 | 0 | 0 | 0 | 0 | 72.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9941.74 | 0 | 9941.74 | 130623 | 0 | 64 | 74 | 130623 | -1000000
5 | 27 | 19 | 6 | 6.8967 | 0 | 42.7453 | 0 | 6.1436 | 0 | 5.4835 | 8.818 | 0 | 0 | 0 | 1.2 | 71.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9939.95 | 0 | 9939.95 | 130371 | 0 | 63 | 71 | 130371 | -1000000
5 | 27 | 20 | 6 | 8.5891 | 0 | 42.7453 | 0 | 6.0217 | 0 | 5.486 | 8.818 | 0 | 0 | 0 | 4 | 75.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9938.74 | 0 | 9938.74 | 130055 | 0 | 62 | 68 | 130055 | -1000000
5 | 27 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.8978 | 0 | 5.4889 | 8.818 | 0 | 0 | 0 | 7.2 | 78.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.83 | 0 | 9937.83 | 129577 | 0 | 60 | 65 | 129577 | -1000000
5 | 27 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.383 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.28 | 0 | 9937.28 | 129444 | 0 | 60 | 64 | 129444 | -1000000
5 | 27 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3351 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 5.6 | 77.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9937.03 | 0 | 9937.03 | 129161 | 0 | 60 | 63 | 129161 | -1000000
5 | 27 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.2843 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.49 | 0 | 3706.49 | 128799 | 0 | 60 | 62 | 128799 | -1000000
5 | 28 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2371 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 4.8 | 73.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.57 | 0 | 3706.57 | 128501 | 0 | 60 | 61 | 128501 | -1000000
5 | 28 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.1892 | 0 | 5.4873 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.9 | 0 | 3706.9 | 128171 | 0 | 60 | 60 | 128171 | -1000000
5 | 28 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4251 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707.25 | 0 | 3707.25 | 127717 | 0 | 59 | 59 | 127717 | -1000000
5 | 28 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.413 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 3.2 | 71.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707.67 | 0 | 3707.67 | 127455 | 0 | 59 | 59 | 127455 | -1000000
5 | 28 | 5 | 7 | 5.0311 | 0 | 42.7453 | 0 | 6.3938 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 1.6 | 70.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708.14 | 0 | 3708.14 | 127032 | 0 | 58 | 59 | 127032 | -1000000
5 | 28 | 6 | 7 | 4.0475 | 0 | 42.7453 | 0 | 6.3845 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 0 | 67.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708.69 | 0 | 3708.69 | 126832 | 0 | 58 | 59 | 126832 | -1000000
5 | 28 | 7 | 7 | 3.6715 | 0 | 42.7453 | 0 | 7.266 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 0 | 67.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.25 | 0 | 3709.25 | 126758 | 0 | 60 | 63 | 126758 | -1000000
5 | 28 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 7.3864 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.71 | 0 | 3709.71 | 126730 | 0 | 62 | 66 | 126730 | -1000000
5 | 28 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.8277 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 0 | 69.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.71 | 0 | 3709.71 | 126687 | 0 | 64 | 70 | 126687 | -1000000
5 | 28 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.0519 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.2378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3709.33 | 0 | 3709.33 | 126609 | 0 | 65 | 71 | 126609 | -1000000
5 | 28 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.0871 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.2729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708.04 | 0 | 3708.04 | 126464 | 0 | 66 | 72 | 126464 | -1000000
5 | 28 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.7399 | 0 | 5.5167 | 12.8287 | 0 | 0 | 0 | 0 | 74.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.83 | 0 | 3706.83 | 180450 | 0 | 67 | 73 | 180450 | -1000000
5 | 28 | 13 | 7 | 4.513 | 0 | 42.7453 | 0 | 6.8853 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 0 | 68.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3705.31 | 0 | 3705.31 | 126202 | 0 | 67 | 73 | 126202 | -1000000
5 | 28 | 14 | 7 | 4.1864 | 0 | 42.7453 | 0 | 6.5244 | 0 | 5.9635 | 8.818 | 0 | 0 | 0 | 0 | 68.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.79 | 0 | 3703.79 | 126184 | 0 | 67 | 72 | 126184 | -1000000
5 | 28 | 15 | 7 | 4.36 | 0 | 42.7453 | 0 | 7.0207 | 0 | 6.9191 | 8.818 | 0 | 0 | 0 | 0 | 69.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3702.55 | 0 | 3702.55 | 126174 | 0 | 67 | 72 | 126174 | -1000000
5 | 28 | 16 | 7 | 4.1466 | 0 | 42.7453 | 0 | 7.0948 | 0 | 6.9363 | 8.818 | 0 | 0 | 0 | 0 | 69.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3701.73 | 0 | 3701.73 | 126146 | 0 | 67 | 72 | 126146 | -1000000
5 | 28 | 17 | 7 | 4.4539 | 0 | 42.7453 | 0 | 6.7054 | 0 | 6.6933 | 8.818 | 0 | 0 | 0 | 0 | 69.4159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3700.63 | 0 | 3700.63 | 126128 | 0 | 67 | 71 | 126128 | -1000000
5 | 28 | 18 | 7 | 4.9371 | 0 | 42.7453 | 0 | 6.7999 | 0 | 6.8215 | 8.818 | 0 | 0 | 0 | 0 | 70.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3700.01 | 0 | 3700.01 | 125962 | 0 | 66 | 71 | 125962 | -1000000
5 | 28 | 19 | 7 | 5.5057 | 0 | 42.7453 | 0 | 6.4349 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 1.2 | 70.1851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.95 | 0 | 3698.95 | 125925 | 0 | 66 | 70 | 125925 | -1000000
5 | 28 | 20 | 7 | 6.4808 | 0 | 42.7453 | 0 | 6.0942 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 4 | 73.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.45 | 0 | 3698.45 | 125966 | 0 | 67 | 68 | 125966 | -1000000
5 | 28 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3187 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.96 | 0 | 3697.96 | 125812 | 0 | 66 | 67 | 125812 | -1000000
5 | 28 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.1916 | 0 | 5.4965 | 12.8287 | 0 | 0 | 0 | 6.4 | 83.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.69 | 0 | 3697.69 | 181653 | 0 | 66 | 67 | 181653 | -1000000
5 | 28 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3161 | 0 | 5.4835 | 8.818 | 0 | 0 | 0 | 5.6 | 75.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.57 | 0 | 3697.57 | 125582 | 0 | 66 | 66 | 125582 | -1000000
5 | 28 | 24 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5336 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.59 | 0 | 3697.59 | 125506 | 0 | 66 | 66 | 125506 | -1000000
5 | 29 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.5297 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 73.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.7 | 0 | 3697.7 | 125425 | 0 | 66 | 66 | 125425 | -1000000
5 | 29 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.2205 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 4.8 | 73.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.7 | 0 | 3697.7 | 125227 | 0 | 65 | 65 | 125227 | -1000000
5 | 29 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.4755 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.79 | 0 | 3697.79 | 125045 | 0 | 64 | 65 | 125045 | -1000000
5 | 29 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.4749 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 3.2 | 71.8259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.87 | 0 | 3697.87 | 125035 | 0 | 65 | 65 | 125035 | -1000000
5 | 29 | 5 | 8 | 5.0594 | 0 | 42.7453 | 0 | 6.7767 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 1.6 | 70.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.01 | 0 | 3698.01 | 125045 | 0 | 66 | 66 | 125045 | -1000000
5 | 29 | 6 | 8 | 4.683 | 0 | 42.7453 | 0 | 8.4156 | 0 | 5.4844 | 12.8287 | 0 | 0 | 0 | 0 | 74.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.16 | 0 | 3698.16 | 166064 | 0 | 66 | 66 | 166064 | -1000000
5 | 29 | 7 | 8 | 4.1796 | 0 | 42.7453 | 0 | 6.8365 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 0 | 68.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.29 | 0 | 3698.29 | 124804 | 0 | 66 | 67 | 124804 | -1000000
5 | 29 | 8 | 8 | 4.1485 | 0 | 42.7453 | 0 | 6.8398 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 0 | 68.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.34 | 0 | 3698.34 | 124738 | 0 | 66 | 68 | 124738 | -1000000
5 | 29 | 9 | 8 | 4.667 | 0 | 42.7453 | 0 | 6.8775 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 0 | 68.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.38 | 0 | 3698.38 | 124695 | 0 | 66 | 69 | 124695 | -1000000
5 | 29 | 10 | 8 | 4.4187 | 0 | 42.7453 | 0 | 6.6055 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 0 | 68.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.14 | 0 | 3698.14 | 124645 | 0 | 66 | 69 | 124645 | -1000000
5 | 29 | 11 | 8 | 4.3225 | 0 | 42.7453 | 0 | 6.9146 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 0 | 68.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.72 | 0 | 3697.72 | 124627 | 0 | 66 | 70 | 124627 | -1000000
5 | 29 | 12 | 8 | 4.3315 | 0 | 42.7453 | 0 | 9.2031 | 0 | 5.4997 | 12.8287 | 0 | 0 | 0 | 0 | 74.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3697.09 | 0 | 3697.09 | 178524 | 0 | 65 | 70 | 178524 | -1000000
5 | 29 | 13 | 8 | 4.1454 | 0 | 42.7453 | 0 | 7.3163 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 0 | 68.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696.24 | 0 | 3696.24 | 124643 | 0 | 66 | 72 | 124643 | -1000000
5 | 29 | 14 | 8 | 4.144 | 0 | 42.7453 | 0 | 7.6885 | 0 | 6.362 | 8.818 | 0 | 0 | 0 | 0 | 69.7578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3695.25 | 0 | 3695.25 | 124699 | 0 | 67 | 75 | 124699 | -1000000
5 | 29 | 15 | 8 | 4.1448 | 0 | 42.7453 | 0 | 10.3033 | 0 | 10.4255 | 12.8287 | 0 | 0 | 0 | 0 | 80.4475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3694.39 | 0 | 3694.39 | 188620 | 0 | 67 | 77 | 188620 | -1000000
5 | 29 | 16 | 8 | 4.1462 | 0 | 42.7453 | 0 | 7.2079 | 0 | 7.0956 | 8.818 | 0 | 0 | 0 | 0 | 70.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693.16 | 0 | 3693.16 | 124769 | 0 | 67 | 77 | 124769 | -1000000
5 | 29 | 17 | 8 | 4.2992 | 0 | 42.7453 | 0 | 7.092 | 0 | 7.0427 | 8.818 | 0 | 0 | 0 | 0 | 69.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691.7 | 0 | 3691.7 | 124858 | 0 | 67 | 77 | 124858 | -1000000
5 | 29 | 18 | 8 | 4.3065 | 0 | 42.7453 | 0 | 6.9143 | 0 | 6.9995 | 8.818 | 0 | 0 | 0 | 0 | 69.7836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3690.4 | 0 | 3690.4 | 124939 | 0 | 67 | 77 | 124939 | -1000000
5 | 29 | 19 | 8 | 5.301 | 0 | 42.7453 | 0 | 6.5255 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 1.2 | 70.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3689.11 | 0 | 3689.11 | 124595 | 0 | 64 | 74 | 124595 | -1000000
5 | 29 | 20 | 8 | 6.5254 | 0 | 42.7453 | 0 | 8.8332 | 0 | 5.4927 | 12.8287 | 0 | 0 | 0 | 4 | 80.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3688.11 | 0 | 3688.11 | 193577 | 0 | 62 | 70 | 193577 | -1000000
5 | 29 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.7716 | 0 | 5.4898 | 8.818 | 0 | 0 | 0 | 7.2 | 76.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.23 | 0 | 3687.23 | 124365 | 0 | 59 | 67 | 124365 | -1000000
5 | 29 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.2186 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 6.4 | 76.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3686.76 | 0 | 3686.76 | 124451 | 0 | 58 | 66 | 124451 | -1000000
5 | 29 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.887 | 0 | 5.4896 | 8.818 | 0 | 0 | 0 | 5.6 | 75.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3686.69 | 0 | 3686.69 | 124437 | 0 | 57 | 64 | 124437 | -1000000
5 | 29 | 24 | 8 | 10.424 | 0 | 42.3304 | 0 | 6.1243 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 4.8 | 77.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9917.29 | 0 | 9917.29 | 124629 | 0 | 56 | 63 | 124629 | -1000000
5 | 30 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.5673 | 0 | 5.4786 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9917.47 | 0 | 9917.47 | 163733 | 0 | 55 | 61 | 163733 | -1000000
5 | 30 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.0464 | 0 | 5.4892 | 8.818 | 0 | 0 | 0 | 4.8 | 77.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9916.93 | 0 | 9916.93 | 124395 | 0 | 54 | 59 | 124395 | -1000000
5 | 30 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.2639 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9916.93 | 0 | 9916.93 | 124193 | 0 | 52 | 57 | 124193 | -1000000
5 | 30 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.4413 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 3.2 | 80.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.8 | 0 | 11020.8 | 128144 | 0 | 53 | 56 | 128144 | -1000000
5 | 30 | 5 | 2 | 23.7612 | 0 | 69.9783 | 0 | 11.2114 | 0 | 5.539 | 12.8287 | 0 | 0 | 0 | 1.6 | 124.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13477.7 | 0 | 13477.7 | 234280 | 0 | 53 | 56 | 234280 | -1000000
5 | 30 | 6 | 2 | 37.4414 | 0 | 140.608 | 0 | 47.2163 | 0 | 6.332 | 20.1279 | 0 | 0 | 0 | 0 | 251.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36620.5 | 0 | 36620.5 | 701074 | -16270.3 | 53 | 55 | 701074 | -1016270.3
5 | 30 | 7 | 2 | 38.8858 | 0 | 168.222 | 0 | 49.4226 | 0 | 6.332 | 20.5637 | 0 | 0 | 0 | 0 | 283.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40177.2 | 0 | 40177.2 | 758786 | -28090.6 | 55 | 58 | 758786 | -1028090.6
5 | 30 | 8 | 2 | 39.6708 | 0 | 173.795 | 0 | 53.6544 | 0 | 6.332 | 20.5435 | 0 | 0 | 0 | 0 | 293.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50877.8 | 0 | 50877.8 | 806514 | -18353.8 | 56 | 62 | 806514 | -1018353.8
5 | 30 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 42.2502 | 0 | 6.332 | 20.9461 | 0 | 0 | 0 | 0 | 282.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79365.3 | 0 | 79365.3 | 856840 | -11969.5 | 57 | 65 | 856840 | -1011969.5
5 | 30 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 42.5765 | 0 | 6.332 | 21.4614 | 0 | 0 | 0 | 0 | 274.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81148.5 | 0 | 81148.5 | 858047 | -9173.84 | 57 | 67 | 858047 | -1009173.84
5 | 30 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 40.2244 | 0 | 6.332 | 22.0604 | 0 | 0 | 0 | 0 | 259.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81150 | 0 | 81150 | 810487 | -7192.65 | 58 | 68 | 810487 | -1007192.65
5 | 30 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 41.3146 | 0 | 6.332 | 22.1482 | 0 | 0 | 0 | 0 | 259.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81150.3 | 0 | 81150.3 | 817558 | -7414.22 | 57 | 70 | 817558 | -1007414.22
5 | 30 | 13 | 2 | 41.2459 | 0 | 165.698 | 0 | 45.2772 | 0 | 6.332 | 23.016 | 0 | 0 | 0 | 0 | 281.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81150 | 0 | 81150 | 897218 | -6825.3 | 57 | 71 | 897218 | -1006825.3
5 | 30 | 14 | 2 | 40.6773 | 0 | 172.702 | 0 | 49.5829 | 0 | 6.332 | 22.8947 | 0 | 0 | 0 | 0 | 292.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79369.9 | 0 | 79369.9 | 975288 | -7477.99 | 58 | 72 | 975288 | -1007477.99
5 | 30 | 15 | 2 | 40.5585 | 0 | 173.986 | 0 | 54.2928 | 0 | 6.332 | 23.1034 | 0 | 0 | 0 | 0 | 298.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72249.1 | 0 | 72249.1 | 985731 | -8273.66 | 57 | 73 | 985731 | -1008273.66
5 | 30 | 16 | 2 | 40.3026 | 0 | 169.782 | 0 | 53.314 | 0 | 6.332 | 22.7987 | 0 | 0 | 0 | 0 | 292.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59787 | 0 | 59787 | 985057 | -14021 | 57 | 72 | 985057 | -1014021
5 | 30 | 17 | 2 | 35.4834 | 0 | 152.497 | 0 | 44.761 | 0 | 6.332 | 22.5081 | 0 | 0 | 0 | 0 | 261.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45544.6 | 0 | 45544.6 | 860208 | -13428.2 | 56 | 71 | 860208 | -1013428.2
5 | 30 | 18 | 2 | 24.5888 | 0 | 93.4203 | 0 | 31.9694 | 0 | 6.332 | 20.0641 | 0 | 0 | 0 | 0 | 176.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27741.8 | 0 | 27741.8 | 628551 | -21142.1 | 55 | 70 | 628551 | -1021142.1
5 | 30 | 19 | 2 | 19.29 | 0 | 62.7906 | 0 | 8.7082 | 0 | 5.4879 | 8.818 | 0 | 0 | 0 | 1.2 | 106.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19730.8 | 0 | 19730.8 | 186675 | 0 | 55 | 66 | 186675 | -1000000
5 | 30 | 20 | 2 | 17.9684 | 0 | 54.6418 | 0 | 6.9768 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4 | 97.8849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18842.7 | 0 | 18842.7 | 166734 | 0 | 54 | 61 | 166734 | -1000000
5 | 30 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.3465 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11709.2 | 0 | 11709.2 | 153281 | 0 | 52 | 57 | 153281 | -1000000
5 | 30 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.1086 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11422.7 | 0 | 11422.7 | 142503 | 0 | 52 | 56 | 142503 | -1000000
5 | 30 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.884 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9925.83 | 0 | 9925.83 | 137688 | 0 | 51 | 54 | 137688 | -1000000
5 | 30 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8192 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9926.4 | 0 | 9926.4 | 136326 | 0 | 51 | 53 | 136326 | -1000000
5 | 31 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7773 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.02 | 0 | 9927.02 | 135416 | 0 | 50 | 51 | 135416 | -1000000
5 | 31 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7383 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9927.78 | 0 | 9927.78 | 134565 | 0 | 49 | 50 | 134565 | -1000000
5 | 31 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6998 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.54 | 0 | 9928.54 | 133721 | 0 | 47 | 48 | 133721 | -1000000
5 | 31 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.8431 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 3.2 | 80.9866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11033.1 | 0 | 11033.1 | 136926 | 0 | 48 | 48 | 136926 | -1000000
5 | 31 | 5 | 3 | 23.8639 | 0 | 69.9783 | 0 | 12.2696 | 0 | 5.9376 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13490.8 | 0 | 13490.8 | 198233 | -4397.37 | 48 | 48 | 198233 | -1004397.37
5 | 31 | 6 | 3 | 37.6644 | 0 | 140.608 | 0 | 24.5649 | 0 | 6.332 | 19.435 | 0 | 0 | 0 | 0 | 228.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36634.3 | 0 | 36634.3 | 371310 | -23793.9 | 48 | 48 | 371310 | -1023793.9
5 | 31 | 7 | 3 | 38.9296 | 0 | 168.222 | 0 | 31.7206 | 0 | 6.332 | 19.3736 | 0 | 0 | 0 | 0 | 264.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40192.1 | 0 | 40192.1 | 505144 | -37141.8 | 51 | 53 | 505144 | -1037141.8
5 | 31 | 8 | 3 | 39.6631 | 0 | 173.795 | 0 | 40.3674 | 0 | 6.332 | 19.6716 | 0 | 0 | 0 | 0 | 279.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50886.1 | 0 | 50886.1 | 630455 | -21486.1 | 54 | 59 | 630455 | -1021486.1
5 | 31 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 48.1074 | 0 | 6.332 | 20.0257 | 0 | 0 | 0 | 0 | 287.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79371.8 | 0 | 79371.8 | 739685 | -14236 | 56 | 64 | 739685 | -1014236
5 | 31 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 49.7075 | 0 | 6.332 | 20.6744 | 0 | 0 | 0 | 0 | 280.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81153.6 | 0 | 81153.6 | 786974 | -10650.5 | 57 | 67 | 786974 | -1010650.5
5 | 31 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 41.1809 | 0 | 25.335 | 21.4625 | 0 | 0 | 0 | 0 | 278.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81154.9 | 0 | 81154.9 | 743363 | -7863.19 | 57 | 69 | 743363 | -1007863.19
5 | 31 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 46.4318 | 0 | 25.335 | 21.649 | 0 | 0 | 0 | 0 | 283.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81154.8 | 0 | 81154.8 | 797704 | -8134.46 | 57 | 72 | 797704 | -1008134.46
5 | 31 | 13 | 3 | 41.2426 | 0 | 165.698 | 0 | 53.0659 | 0 | 25.335 | 22.7029 | 0 | 0 | 0 | 0 | 308.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81155 | 0 | 81155 | 903932 | -6842.38 | 58 | 74 | 903932 | -1006842.38
5 | 31 | 14 | 3 | 40.6558 | 0 | 172.702 | 0 | 58.2561 | 0 | 25.335 | 22.4461 | 0 | 0 | 0 | 0 | 319.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79374.2 | 0 | 79374.2 | 994577 | -10070.9 | 59 | 75 | 994577 | -1010070.9
5 | 31 | 15 | 3 | 40.5452 | 0 | 173.986 | 0 | 63.0096 | 0 | 25.335 | 22.8026 | 0 | 0 | 0 | 0 | 325.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72253.2 | 0 | 72253.2 | 1082440 | -11046.9 | 60 | 77 | 1082440 | -1011046.9
5 | 31 | 16 | 3 | 40.2873 | 0 | 169.782 | 0 | 63.1329 | 0 | 25.335 | 22.7335 | 0 | 0 | 0 | 0 | 321.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59791 | 0 | 59791 | 1087960 | -15194.8 | 60 | 77 | 1087960 | -1015194.8
5 | 31 | 17 | 3 | 35.47 | 0 | 152.497 | 0 | 59.0847 | 0 | 25.335 | 22.3339 | 0 | 0 | 0 | 0 | 294.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45548.5 | 0 | 45548.5 | 1036130 | -18342 | 61 | 76 | 1036130 | -1018342
5 | 31 | 18 | 3 | 24.5884 | 0 | 93.4203 | 0 | 41.7574 | 0 | 25.335 | 20.2894 | 0 | 0 | 0 | 0 | 205.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27745.7 | 0 | 27745.7 | 739863 | -21500 | 61 | 76 | 739863 | -1021500
5 | 31 | 19 | 3 | 18.598 | 0 | 62.7906 | 0 | 9.9521 | 0 | 5.9626 | 8.818 | 0 | 0 | 0 | 1.2 | 107.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19734.6 | 0 | 19734.6 | 191576 | 0 | 61 | 73 | 191576 | -1000000
5 | 31 | 20 | 3 | 18.3004 | 0 | 54.6418 | 0 | 8.0986 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 4 | 99.3418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18846 | 0 | 18846 | 171261 | 0 | 60 | 70 | 171261 | -1000000
5 | 31 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.6285 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 91.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11712.5 | 0 | 11712.5 | 157877 | 0 | 59 | 68 | 157877 | -1000000
5 | 31 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.9532 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 6.4 | 84.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11425.6 | 0 | 11425.6 | 146912 | 0 | 59 | 69 | 146912 | -1000000
5 | 31 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.7594 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 5.6 | 80.5157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.21 | 0 | 9928.21 | 142036 | 0 | 59 | 70 | 142036 | -1000000
5 | 31 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.7372 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9928.01 | 0 | 9928.01 | 140692 | 0 | 60 | 71 | 140692 | -1000000
6 | 1 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.752 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.46 | 0 | 9103.46 | 140059 | 0 | 60 | 72 | 140059 | -1000000
6 | 1 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.7701 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.11 | 0 | 9103.11 | 139475 | 0 | 61 | 73 | 139475 | -1000000
6 | 1 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.4562 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.57 | 0 | 9102.57 | 138704 | 0 | 61 | 73 | 138704 | -1000000
6 | 1 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.2999 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 3.2 | 81.4412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10103.4 | 0 | 10103.4 | 142106 | 0 | 61 | 72 | 142106 | -1000000
6 | 1 | 5 | 4 | 23.7528 | 0 | 69.9783 | 0 | 13.3877 | 0 | 5.6801 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12331.9 | 0 | 12331.9 | 270442 | 0 | 61 | 71 | 270442 | -1000000
6 | 1 | 6 | 4 | 38.167 | 0 | 140.608 | 0 | 57.3732 | 0 | 6.332 | 21.9026 | 0 | 0 | 0 | 0 | 264.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33330.4 | 0 | 33330.4 | 1068770 | -5023.01 | 63 | 73 | 1068770 | -1005023.01
6 | 1 | 7 | 4 | 39.039 | 0 | 168.222 | 0 | 67.1805 | 0 | 6.332 | 21.8972 | 0 | 0 | 0 | 0 | 302.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36556.6 | 0 | 36556.6 | 1210630 | -10663.2 | 65 | 74 | 1210630 | -1010663.2
6 | 1 | 8 | 4 | 39.7897 | 0 | 173.795 | 0 | 51.3838 | 0 | 6.3461 | 21.3831 | 0 | 0 | 0 | 0 | 292.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46268.2 | 0 | 46268.2 | 1026730 | -14405.3 | 60 | 68 | 1026730 | -1014405.3
6 | 1 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 50.0398 | 0 | 25.335 | 21.4869 | 0 | 0 | 0 | 0 | 309.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72118.3 | 0 | 72118.3 | 968154 | -15913.6 | 58 | 68 | 968154 | -1015913.6
6 | 1 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 53.442 | 0 | 25.335 | 21.6079 | 0 | 0 | 0 | 0 | 304.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735 | 0 | 73735 | 953837 | -14353.8 | 58 | 69 | 953837 | -1014353.8
6 | 1 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 45.7529 | 0 | 25.335 | 22.2886 | 0 | 0 | 0 | 0 | 283.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.7 | 0 | 73735.7 | 839037 | -11765.4 | 57 | 68 | 839037 | -1011765.4
6 | 1 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 50.6666 | 0 | 25.335 | 22.2892 | 0 | 0 | 0 | 0 | 288.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.7 | 0 | 73735.7 | 888225 | -16274.5 | 58 | 70 | 888225 | -1016274.5
6 | 1 | 13 | 4 | 41.2377 | 0 | 165.698 | 0 | 54.8227 | 0 | 25.335 | 22.7872 | 0 | 0 | 0 | 0 | 309.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.1 | 0 | 73735.1 | 966331 | -13872 | 58 | 71 | 966331 | -1013872
6 | 1 | 14 | 4 | 40.6401 | 0 | 172.702 | 0 | 51.7754 | 0 | 25.335 | 22.455 | 0 | 0 | 0 | 0 | 312.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72120 | 0 | 72120 | 946928 | -17777.6 | 56 | 68 | 946928 | -1017777.6
6 | 1 | 15 | 4 | 40.5526 | 0 | 173.986 | 0 | 53.779 | 0 | 25.335 | 22.4742 | 0 | 0 | 0 | 0 | 316.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65658.5 | 0 | 65658.5 | 973293 | -19181 | 56 | 68 | 973293 | -1019181
6 | 1 | 16 | 4 | 40.2827 | 0 | 169.782 | 0 | 52.0595 | 0 | 25.335 | 22.5619 | 0 | 0 | 0 | 0 | 310.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54350.3 | 0 | 54350.3 | 947712 | -19248.8 | 56 | 68 | 947712 | -1019248.8
6 | 1 | 17 | 4 | 35.474 | 0 | 152.497 | 0 | 41.2716 | 0 | 25.335 | 21.9748 | 0 | 0 | 0 | 0 | 276.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.8 | 0 | 41426.8 | 790423 | -16865 | 54 | 65 | 790423 | -1016865
6 | 1 | 18 | 4 | 24.5854 | 0 | 93.4203 | 0 | 29.3677 | 0 | 25.335 | 19.9601 | 0 | 0 | 0 | 0 | 192.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.6 | 0 | 25272.6 | 556197 | -16549.9 | 54 | 65 | 556197 | -1016549.9
6 | 1 | 19 | 4 | 19.015 | 0 | 62.7906 | 0 | 9.5112 | 0 | 8.726 | 8.818 | 0 | 0 | 0 | 1.2 | 110.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.6 | 0 | 18003.6 | 192744 | 0 | 53 | 63 | 192744 | -1000000
6 | 1 | 20 | 4 | 18.06 | 0 | 54.6418 | 0 | 7.7229 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4 | 98.7214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197.8 | 0 | 17197.8 | 172638 | 0 | 51 | 60 | 172638 | -1000000
6 | 1 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.8778 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10724.3 | 0 | 10724.3 | 159298 | 0 | 50 | 57 | 159298 | -1000000
6 | 1 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.3599 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10464.5 | 0 | 10464.5 | 147995 | 0 | 49 | 56 | 147995 | -1000000
6 | 1 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.1227 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.28 | 0 | 9106.28 | 142907 | 0 | 47 | 55 | 142907 | -1000000
6 | 1 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.0554 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.84 | 0 | 9106.84 | 141495 | 0 | 47 | 54 | 141495 | -1000000
6 | 2 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0033 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.44 | 0 | 9107.44 | 140360 | 0 | 46 | 52 | 140360 | -1000000
6 | 2 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9569 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.13 | 0 | 9108.13 | 139347 | 0 | 45 | 50 | 139347 | -1000000
6 | 2 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9181 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.81 | 0 | 9108.81 | 138500 | 0 | 45 | 48 | 138500 | -1000000
6 | 2 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.0267 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10111.1 | 0 | 10111.1 | 140931 | 0 | 43 | 47 | 140931 | -1000000
6 | 2 | 5 | 5 | 23.6985 | 0 | 69.9783 | 0 | 12.4496 | 0 | 5.9417 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12341.2 | 0 | 12341.2 | 201102 | -3857.95 | 42 | 45 | 201102 | -1003857.95
6 | 2 | 6 | 5 | 37.6794 | 0 | 140.608 | 0 | 22.8137 | 0 | 6.332 | 19.2672 | 0 | 0 | 0 | 0 | 226.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33341.4 | 0 | 33341.4 | 369258 | -22740.1 | 42 | 48 | 369258 | -1022740.1
6 | 2 | 7 | 5 | 38.9746 | 0 | 168.222 | 0 | 30.6447 | 0 | 6.332 | 19.3241 | 0 | 0 | 0 | 0 | 263.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36569.3 | 0 | 36569.3 | 489113 | -50233.8 | 44 | 51 | 489113 | -1050233.8
6 | 2 | 8 | 5 | 39.6631 | 0 | 173.795 | 0 | 31.6141 | 0 | 25.335 | 19.317 | 0 | 0 | 0 | 0 | 289.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46272.9 | 0 | 46272.9 | 566402 | -47214.1 | 45 | 54 | 566402 | -1047214.1
6 | 2 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 31.2902 | 0 | 25.335 | 19.4995 | 0 | 0 | 0 | 0 | 288.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.9 | 0 | 72119.9 | 589742 | -30339.3 | 46 | 56 | 589742 | -1030339.3
6 | 2 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 33.0009 | 0 | 25.335 | 19.9129 | 0 | 0 | 0 | 0 | 282.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73737.3 | 0 | 73737.3 | 612302 | -22263.7 | 47 | 59 | 612302 | -1022263.7
6 | 2 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 33.3911 | 0 | 25.335 | 20.4791 | 0 | 0 | 0 | 0 | 269.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73738.1 | 0 | 73738.1 | 616899 | -15793.9 | 48 | 62 | 616899 | -1015793.9
6 | 2 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 35.443 | 0 | 25.335 | 21.1404 | 0 | 0 | 0 | 0 | 271.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73738 | 0 | 73738 | 644230 | -13204.6 | 49 | 64 | 644230 | -1013204.6
6 | 2 | 13 | 5 | 41.2523 | 0 | 165.698 | 0 | 41.7376 | 0 | 25.335 | 21.7967 | 0 | 0 | 0 | 0 | 295.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73737.5 | 0 | 73737.5 | 750876 | -15542 | 50 | 66 | 750876 | -1015542
6 | 2 | 14 | 5 | 40.6577 | 0 | 172.702 | 0 | 48.6172 | 0 | 25.335 | 21.84 | 0 | 0 | 0 | 0 | 309.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72121.5 | 0 | 72121.5 | 851673 | -17645.2 | 52 | 69 | 851673 | -1017645.2
6 | 2 | 15 | 5 | 40.5488 | 0 | 173.986 | 0 | 49.3138 | 0 | 25.335 | 22.0743 | 0 | 0 | 0 | 0 | 311.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65659.5 | 0 | 65659.5 | 879539 | -18676.6 | 52 | 69 | 879539 | -1018676.6
6 | 2 | 16 | 5 | 40.2921 | 0 | 169.782 | 0 | 49.6185 | 0 | 25.335 | 22.3281 | 0 | 0 | 0 | 0 | 307.355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54351.6 | 0 | 54351.6 | 884234 | -17701.2 | 52 | 70 | 884234 | -1017701.2
6 | 2 | 17 | 5 | 35.4728 | 0 | 152.497 | 0 | 45.0443 | 0 | 25.335 | 21.6292 | 0 | 0 | 0 | 0 | 279.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41428 | 0 | 41428 | 816628 | -17448.5 | 53 | 70 | 816628 | -1017448.5
6 | 2 | 18 | 5 | 24.5878 | 0 | 93.4203 | 0 | 30.2212 | 0 | 25.335 | 19.7789 | 0 | 0 | 0 | 0 | 193.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25273.7 | 0 | 25273.7 | 569140 | -16713.8 | 52 | 68 | 569140 | -1016713.8
6 | 2 | 19 | 5 | 18.6422 | 0 | 62.7906 | 0 | 9.834 | 0 | 9.1463 | 8.818 | 0 | 0 | 0 | 1.2 | 110.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18005.2 | 0 | 18005.2 | 192826 | 0 | 52 | 66 | 192826 | -1000000
6 | 2 | 20 | 5 | 17.9948 | 0 | 54.6418 | 0 | 7.5509 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4 | 98.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17199.4 | 0 | 17199.4 | 172745 | 0 | 51 | 62 | 172745 | -1000000
6 | 2 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.6608 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10726.2 | 0 | 10726.2 | 159278 | 0 | 51 | 61 | 159278 | -1000000
6 | 2 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.104 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10466.3 | 0 | 10466.3 | 148008 | 0 | 49 | 55 | 148008 | -1000000
6 | 2 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1279 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.11 | 0 | 9108.11 | 143023 | 0 | 49 | 54 | 143023 | -1000000
6 | 2 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0308 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.59 | 0 | 9108.59 | 140946 | 0 | 48 | 55 | 140946 | -1000000
6 | 3 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9844 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9109.24 | 0 | 9109.24 | 139949 | 0 | 47 | 55 | 139949 | -1000000
6 | 3 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9414 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9110.66 | 0 | 9110.66 | 139009 | 0 | 46 | 54 | 139009 | -1000000
6 | 3 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9059 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.69 | 0 | 9111.69 | 138235 | 0 | 46 | 53 | 138235 | -1000000
6 | 3 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8647 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 3.2 | 73.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9112.67 | 0 | 9112.67 | 137330 | 0 | 46 | 52 | 137330 | -1000000
6 | 3 | 5 | 6 | 6.2586 | 0 | 42.7453 | 0 | 6.8266 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9113.65 | 0 | 9113.65 | 136497 | 0 | 46 | 51 | 136497 | -1000000
6 | 3 | 6 | 6 | 4.8502 | 0 | 42.7453 | 0 | 6.7869 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 0 | 68.6817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9114.69 | 0 | 9114.69 | 135628 | 0 | 46 | 53 | 135628 | -1000000
6 | 3 | 7 | 6 | 4.5902 | 0 | 42.7453 | 0 | 15.9456 | 0 | 5.9893 | 18.8896 | 0 | 0 | 0 | 0 | 88.1599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9115.76 | 0 | 9115.76 | 196228 | -38496.5 | 50 | 57 | 196228 | -1038496.5
6 | 3 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 15.9042 | 0 | 6.022 | 18.8896 | 0 | 0 | 0 | 0 | 88.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9116.68 | 0 | 9116.68 | 217278 | -40283.2 | 52 | 61 | 217278 | -1040283.2
6 | 3 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 19.0173 | 0 | 6.2319 | 18.8896 | 0 | 0 | 0 | 0 | 92.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9124.7 | 0 | 9124.7 | 246489 | -29145.6 | 54 | 66 | 246489 | -1029145.6
6 | 3 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 20.5985 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 94.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9125.85 | 0 | 9125.85 | 283426 | -23706 | 56 | 69 | 283426 | -1023706
6 | 3 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 21.7063 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 95.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9126.73 | 0 | 9126.73 | 318160 | -20050.5 | 57 | 72 | 318160 | -1020050.5
6 | 3 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 22.0983 | 0 | 6.332 | 18.9287 | 0 | 0 | 0 | 0 | 95.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.15 | 0 | 9127.15 | 349322 | -19117.9 | 58 | 74 | 349322 | -1019117.9
6 | 3 | 13 | 6 | 5.4706 | 0 | 42.7453 | 0 | 22.6023 | 0 | 25.335 | 19.0658 | 0 | 0 | 0 | 0 | 115.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.41 | 0 | 9127.41 | 383894 | -18614 | 59 | 76 | 383894 | -1018614
6 | 3 | 14 | 6 | 5.4729 | 0 | 42.7453 | 0 | 11.3288 | 0 | 11.0539 | 12.8287 | 0 | 0 | 0 | 0 | 83.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.73 | 0 | 9127.73 | 185341 | 0 | 60 | 79 | 185341 | -1000000
6 | 3 | 15 | 6 | 5.4731 | 0 | 42.7453 | 0 | 11.2417 | 0 | 10.9557 | 12.8287 | 0 | 0 | 0 | 0 | 83.2444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9128.04 | 0 | 9128.04 | 187744 | 0 | 60 | 79 | 187744 | -1000000
6 | 3 | 16 | 6 | 5.4724 | 0 | 42.7453 | 0 | 8.0181 | 0 | 7.4948 | 8.818 | 0 | 0 | 0 | 0 | 72.5486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9122.77 | 0 | 9122.77 | 131629 | 0 | 61 | 80 | 131629 | -1000000
6 | 3 | 17 | 6 | 5.4732 | 0 | 42.7453 | 0 | 7.8946 | 0 | 7.4269 | 8.818 | 0 | 0 | 0 | 0 | 72.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9119.48 | 0 | 9119.48 | 131405 | 0 | 61 | 80 | 131405 | -1000000
6 | 3 | 18 | 6 | 5.4748 | 0 | 42.7453 | 0 | 7.8646 | 0 | 7.415 | 8.818 | 0 | 0 | 0 | 0 | 72.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9117.12 | 0 | 9117.12 | 131295 | 0 | 61 | 79 | 131295 | -1000000
6 | 3 | 19 | 6 | 6.6996 | 0 | 42.7453 | 0 | 7.6955 | 0 | 7.3571 | 8.818 | 0 | 0 | 0 | 1.2 | 74.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9115.02 | 0 | 9115.02 | 130996 | 0 | 60 | 76 | 130996 | -1000000
6 | 3 | 20 | 6 | 8.4524 | 0 | 42.7453 | 0 | 6.2011 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 4 | 75.6995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9113.4 | 0 | 9113.4 | 130796 | 0 | 59 | 72 | 130796 | -1000000
6 | 3 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.6992 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 7.2 | 79.7393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9112.01 | 0 | 9112.01 | 130576 | 0 | 59 | 71 | 130576 | -1000000
6 | 3 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3428 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 6.4 | 78.5857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.05 | 0 | 9111.05 | 130402 | 0 | 59 | 69 | 130402 | -1000000
6 | 3 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.873 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 5.6 | 78.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9110.47 | 0 | 9110.47 | 130213 | 0 | 60 | 69 | 130213 | -1000000
6 | 3 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.5473 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.51 | 0 | 3456.51 | 129835 | 0 | 60 | 68 | 129835 | -1000000
6 | 4 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.1941 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 73.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.2 | 0 | 3456.2 | 129541 | 0 | 60 | 66 | 129541 | -1000000
6 | 4 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.7081 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.12 | 0 | 3456.12 | 129200 | 0 | 60 | 66 | 129200 | -1000000
6 | 4 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6948 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 73.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.03 | 0 | 3456.03 | 128918 | 0 | 60 | 66 | 128918 | -1000000
6 | 4 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6818 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 3.2 | 72.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.04 | 0 | 3456.04 | 128643 | 0 | 60 | 66 | 128643 | -1000000
6 | 4 | 5 | 7 | 5.009 | 0 | 42.7453 | 0 | 6.3705 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 1.6 | 70.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.06 | 0 | 3456.06 | 128423 | 0 | 60 | 65 | 128423 | -1000000
6 | 4 | 6 | 7 | 3.956 | 0 | 42.7453 | 0 | 8.1135 | 0 | 7.4413 | 8.818 | 0 | 0 | 0 | 0 | 71.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.09 | 0 | 3456.09 | 128356 | 0 | 62 | 68 | 128356 | -1000000
6 | 4 | 7 | 7 | 3.668 | 0 | 42.7453 | 0 | 7.3647 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.06 | 0 | 3456.06 | 128330 | 0 | 64 | 70 | 128330 | -1000000
6 | 4 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 7.1262 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 67.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.03 | 0 | 3456.03 | 128135 | 0 | 65 | 71 | 128135 | -1000000
6 | 4 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.1404 | 0 | 5.4881 | 8.818 | 0 | 0 | 0 | 0 | 69.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455.4 | 0 | 3455.4 | 128162 | 0 | 68 | 77 | 128162 | -1000000
6 | 4 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.5313 | 0 | 10.8231 | 12.8287 | 0 | 0 | 0 | 0 | 81.0723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453.76 | 0 | 3453.76 | 194347 | 0 | 71 | 82 | 194347 | -1000000
6 | 4 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.0962 | 0 | 11.2797 | 12.8287 | 0 | 0 | 0 | 0 | 82.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452 | 0 | 3452 | 195901 | 0 | 71 | 84 | 195901 | -1000000
6 | 4 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.8769 | 0 | 12.1665 | 12.8287 | 0 | 0 | 0 | 0 | 83.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3450.08 | 0 | 3450.08 | 203369 | 0 | 69 | 79 | 203369 | -1000000
6 | 4 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.9106 | 0 | 8.9641 | 12.8287 | 0 | 0 | 0 | 0 | 78.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447.66 | 0 | 3447.66 | 207115 | 0 | 68 | 69 | 207115 | -1000000
6 | 4 | 14 | 7 | 4.7041 | 0 | 42.7453 | 0 | 6.8725 | 0 | 6.534 | 8.818 | 0 | 0 | 0 | 0 | 69.6738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446.35 | 0 | 3446.35 | 127234 | 0 | 65 | 67 | 127234 | -1000000
6 | 4 | 15 | 7 | 4.8997 | 0 | 42.7453 | 0 | 6.6877 | 0 | 6.4114 | 8.818 | 0 | 0 | 0 | 0 | 69.5621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.26 | 0 | 3444.26 | 126869 | 0 | 62 | 65 | 126869 | -1000000
6 | 4 | 16 | 7 | 4.5717 | 0 | 42.7453 | 0 | 7.2509 | 0 | 6.7045 | 8.818 | 0 | 0 | 0 | 0 | 70.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443.36 | 0 | 3443.36 | 126681 | 0 | 59 | 65 | 126681 | -1000000
6 | 4 | 17 | 7 | 4.6682 | 0 | 42.7453 | 0 | 7.5263 | 0 | 6.9139 | 8.818 | 0 | 0 | 0 | 0 | 70.6716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443.1 | 0 | 3443.1 | 126898 | 0 | 60 | 66 | 126898 | -1000000
6 | 4 | 18 | 7 | 5.1177 | 0 | 42.7453 | 0 | 7.1718 | 0 | 6.7247 | 8.818 | 0 | 0 | 0 | 0 | 70.5775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.99 | 0 | 3442.99 | 126718 | 0 | 60 | 66 | 126718 | -1000000
6 | 4 | 19 | 7 | 5.7477 | 0 | 42.7453 | 0 | 6.792 | 0 | 6.6435 | 8.818 | 0 | 0 | 0 | 1.2 | 71.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.63 | 0 | 3442.63 | 126609 | 0 | 60 | 66 | 126609 | -1000000
6 | 4 | 20 | 7 | 6.529 | 0 | 42.7453 | 0 | 6.2734 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 4 | 73.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.33 | 0 | 3442.33 | 126354 | 0 | 59 | 65 | 126354 | -1000000
6 | 4 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2298 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.21 | 0 | 3442.21 | 126164 | 0 | 58 | 64 | 126164 | -1000000
6 | 4 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4887 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 6.4 | 76.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.1 | 0 | 3442.1 | 126097 | 0 | 58 | 64 | 126097 | -1000000
6 | 4 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.196 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 5.6 | 75.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.14 | 0 | 3442.14 | 126172 | 0 | 59 | 63 | 126172 | -1000000
6 | 4 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 5.5853 | 0 | 5.4965 | 8.818 | 0 | 0 | 0 | 4.8 | 77.8792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.81 | 0 | 9095.81 | 126187 | 0 | 58 | 60 | 126187 | -1000000
6 | 5 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3505 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.96 | 0 | 9095.96 | 126091 | 0 | 58 | 60 | 126091 | -1000000
6 | 5 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3416 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.31 | 0 | 9095.31 | 125895 | 0 | 57 | 58 | 125895 | -1000000
6 | 5 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.5848 | 0 | 5.4786 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.27 | 0 | 9095.27 | 153568 | 0 | 56 | 58 | 153568 | -1000000
6 | 5 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.5094 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 3.2 | 80.6556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10096.8 | 0 | 10096.8 | 129163 | 0 | 55 | 57 | 129163 | -1000000
6 | 5 | 5 | 1 | 24.0034 | 0 | 69.9783 | 0 | 10.8071 | 0 | 5.5263 | 12.8287 | 0 | 0 | 0 | 1.6 | 124.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12326.2 | 0 | 12326.2 | 225258 | 0 | 54 | 56 | 225258 | -1000000
6 | 5 | 6 | 1 | 43.3143 | 0 | 140.608 | 0 | 42.8153 | 0 | 6.332 | 20.3619 | 0 | 0 | 0 | 0 | 253.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33325.7 | 0 | 33325.7 | 675674 | -13951.3 | 54 | 56 | 675674 | -1013951.3
6 | 5 | 7 | 1 | 39.2576 | 0 | 168.222 | 0 | 41.107 | 0 | 6.332 | 20.3168 | 0 | 0 | 0 | 0 | 275.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36552.9 | 0 | 36552.9 | 657389 | -25218.2 | 53 | 56 | 657389 | -1025218.2
6 | 5 | 8 | 1 | 39.9207 | 0 | 173.795 | 0 | 29.7551 | 0 | 6.332 | 20.5146 | 0 | 0 | 0 | 0 | 270.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46262.8 | 0 | 46262.8 | 633070 | -19150.6 | 52 | 56 | 633070 | -1019150.6
6 | 5 | 9 | 1 | 40.9278 | 0 | 172.186 | 0 | 32.3855 | 0 | 6.332 | 20.7928 | 0 | 0 | 0 | 0 | 272.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72111.6 | 0 | 72111.6 | 604866 | -17207.8 | 49 | 56 | 604866 | -1017207.8
6 | 5 | 10 | 1 | 41.6312 | 0 | 163.102 | 0 | 31.7895 | 0 | 6.332 | 20.8878 | 0 | 0 | 0 | 0 | 263.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73727.9 | 0 | 73727.9 | 617540 | -14278.5 | 50 | 59 | 617540 | -1014278.5
6 | 5 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 32.8294 | 0 | 6.332 | 21.3226 | 0 | 0 | 0 | 0 | 250.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73728.4 | 0 | 73728.4 | 629079 | -10404.7 | 52 | 62 | 629079 | -1010404.7
6 | 5 | 12 | 1 | 39.8253 | 0 | 150.207 | 0 | 32.4661 | 0 | 6.332 | 21.4804 | 0 | 0 | 0 | 0 | 250.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73728.9 | 0 | 73728.9 | 634305 | -8578.75 | 53 | 63 | 634305 | -1008578.75
6 | 5 | 13 | 1 | 41.3965 | 0 | 165.698 | 0 | 36.8484 | 0 | 6.332 | 21.9009 | 0 | 0 | 0 | 0 | 272.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729.8 | 0 | 73729.8 | 714062 | -12188.4 | 53 | 63 | 714062 | -1012188.4
6 | 5 | 14 | 1 | 40.9403 | 0 | 172.702 | 0 | 40.0796 | 0 | 8.1114 | 22.0791 | 0 | 0 | 0 | 0 | 283.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72114.7 | 0 | 72114.7 | 767627 | -14106.6 | 54 | 64 | 767627 | -1014106.6
6 | 5 | 15 | 1 | 40.8409 | 0 | 173.986 | 0 | 45.3354 | 0 | 25.335 | 22.4482 | 0 | 0 | 0 | 0 | 307.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65652.9 | 0 | 65652.9 | 851778 | -14596.4 | 56 | 66 | 851778 | -1014596.4
6 | 5 | 16 | 1 | 40.7584 | 0 | 169.782 | 0 | 46.7215 | 0 | 25.335 | 22.2107 | 0 | 0 | 0 | 0 | 304.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54344.9 | 0 | 54344.9 | 878274 | -13984 | 57 | 67 | 878274 | -1013984
6 | 5 | 17 | 1 | 36.125 | 0 | 152.497 | 0 | 39.8132 | 0 | 25.335 | 21.7243 | 0 | 0 | 0 | 0 | 275.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41421.8 | 0 | 41421.8 | 778900 | -11562.2 | 57 | 66 | 778900 | -1011562.2
6 | 5 | 18 | 1 | 25.0795 | 0 | 93.4203 | 0 | 25.6346 | 0 | 25.335 | 19.7666 | 0 | 0 | 0 | 0 | 189.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25268.3 | 0 | 25268.3 | 518007 | -8802.88 | 57 | 65 | 518007 | -1008802.88
6 | 5 | 19 | 1 | 20.4029 | 0 | 62.7906 | 0 | 9.3057 | 0 | 5.4958 | 8.818 | 0 | 0 | 0 | 1.2 | 108.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000 | 0 | 18000 | 186543 | 0 | 56 | 64 | 186543 | -1000000
6 | 5 | 20 | 1 | 18.3362 | 0 | 54.6418 | 0 | 8.4106 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 4 | 99.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17194.4 | 0 | 17194.4 | 166944 | 0 | 56 | 64 | 166944 | -1000000
6 | 5 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.8009 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10720.8 | 0 | 10720.8 | 153991 | 0 | 57 | 64 | 153991 | -1000000
6 | 5 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.9965 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10460.7 | 0 | 10460.7 | 143232 | 0 | 58 | 63 | 143232 | -1000000
6 | 5 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.0274 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.2 | 0 | 9102.2 | 138381 | 0 | 58 | 63 | 138381 | -1000000
6 | 5 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.9687 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.09 | 0 | 9102.09 | 137178 | 0 | 59 | 63 | 137178 | -1000000
6 | 6 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.9233 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.98 | 0 | 9101.98 | 136204 | 0 | 58 | 63 | 136204 | -1000000
6 | 6 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8956 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 78.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.84 | 0 | 9101.84 | 135613 | 0 | 58 | 63 | 135613 | -1000000
6 | 6 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8672 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.69 | 0 | 9101.69 | 135003 | 0 | 58 | 63 | 135003 | -1000000
6 | 6 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.722 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 3.2 | 80.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10103.2 | 0 | 10103.2 | 138340 | 0 | 58 | 62 | 138340 | -1000000
6 | 6 | 5 | 2 | 23.9992 | 0 | 69.9783 | 0 | 11.8414 | 0 | 5.5669 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12332.1 | 0 | 12332.1 | 245361 | 0 | 58 | 62 | 245361 | -1000000
6 | 6 | 6 | 2 | 41.7801 | 0 | 140.608 | 0 | 44.3857 | 0 | 6.332 | 20.9326 | 0 | 0 | 0 | 0 | 254.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33331.4 | 0 | 33331.4 | 697551 | -9629.25 | 58 | 62 | 697551 | -1009629.25
6 | 6 | 7 | 2 | 39.3613 | 0 | 168.222 | 0 | 39.291 | 0 | 25.335 | 20.6777 | 0 | 0 | 0 | 0 | 292.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36558.3 | 0 | 36558.3 | 798481 | -14302 | 58 | 63 | 798481 | -1014302
6 | 6 | 8 | 2 | 39.8834 | 0 | 173.795 | 0 | 44.1648 | 0 | 25.335 | 21.1588 | 0 | 0 | 0 | 0 | 304.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46266.6 | 0 | 46266.6 | 827114 | -16544.6 | 58 | 63 | 827114 | -1016544.6
6 | 6 | 9 | 2 | 40.9987 | 0 | 172.186 | 0 | 46.6123 | 0 | 25.335 | 21.4881 | 0 | 0 | 0 | 0 | 306.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72114.6 | 0 | 72114.6 | 869439 | -17327.9 | 59 | 63 | 869439 | -1017327.9
6 | 6 | 10 | 2 | 41.5337 | 0 | 163.102 | 0 | 50.4708 | 0 | 25.335 | 21.6225 | 0 | 0 | 0 | 0 | 302.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.8 | 0 | 73730.8 | 903139 | -14669.6 | 60 | 66 | 903139 | -1014669.6
6 | 6 | 11 | 2 | 40.8754 | 0 | 149.692 | 0 | 47.6363 | 0 | 25.335 | 21.8076 | 0 | 0 | 0 | 0 | 285.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.2 | 0 | 73731.2 | 854669 | -11343.7 | 61 | 67 | 854669 | -1011343.7
6 | 6 | 12 | 2 | 39.7838 | 0 | 150.207 | 0 | 50.8736 | 0 | 25.335 | 22.1984 | 0 | 0 | 0 | 0 | 288.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.5 | 0 | 73731.5 | 902779 | -10044 | 62 | 68 | 902779 | -1010044
6 | 6 | 13 | 2 | 41.4038 | 0 | 165.698 | 0 | 60.0325 | 0 | 25.335 | 22.4352 | 0 | 0 | 0 | 0 | 314.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.2 | 0 | 73732.2 | 1040430 | -12930.3 | 63 | 70 | 1040430 | -1012930.3
6 | 6 | 14 | 2 | 40.7518 | 0 | 172.702 | 0 | 64.3592 | 0 | 25.335 | 22.986 | 0 | 0 | 0 | 0 | 326.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72117.2 | 0 | 72117.2 | 1108150 | -15570.2 | 64 | 71 | 1108150 | -1015570.2
6 | 6 | 15 | 2 | 40.6906 | 0 | 173.986 | 0 | 66.9836 | 0 | 25.335 | 23.267 | 0 | 0 | 0 | 0 | 330.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65655.7 | 0 | 65655.7 | 1147970 | -16637.1 | 64 | 72 | 1147970 | -1016637.1
6 | 6 | 16 | 2 | 41.6071 | 0 | 169.782 | 0 | 64.9626 | 0 | 25.335 | 22.7611 | 0 | 0 | 0 | 0 | 324.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54347.4 | 0 | 54347.4 | 1132430 | -16063.6 | 64 | 72 | 1132430 | -1016063.6
6 | 6 | 17 | 2 | 36.312 | 0 | 152.497 | 0 | 57.8267 | 0 | 25.335 | 22.3096 | 0 | 0 | 0 | 0 | 294.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41424.2 | 0 | 41424.2 | 1034160 | -13012.4 | 64 | 71 | 1034160 | -1013012.4
6 | 6 | 18 | 2 | 26.1655 | 0 | 93.4203 | 0 | 39.3071 | 0 | 25.335 | 20.0538 | 0 | 0 | 0 | 0 | 204.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25270.1 | 0 | 25270.1 | 705028 | -9053.5 | 64 | 71 | 705028 | -1009053.5
6 | 6 | 19 | 2 | 21.8068 | 0 | 62.7906 | 0 | 10.9097 | 0 | 10.3808 | 8.818 | 0 | 0 | 0 | 1.2 | 115.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18001.8 | 0 | 18001.8 | 191786 | 0 | 64 | 70 | 191786 | -1000000
6 | 6 | 20 | 2 | 18.3284 | 0 | 54.6418 | 0 | 8.8124 | 0 | 8.316 | 8.818 | 0 | 0 | 0 | 4 | 102.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196 | 0 | 17196 | 171692 | 0 | 64 | 69 | 171692 | -1000000
6 | 6 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.9069 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10721.8 | 0 | 10721.8 | 158090 | 0 | 63 | 68 | 158090 | -1000000
6 | 6 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.6544 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.8824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10461.4 | 0 | 10461.4 | 147233 | 0 | 63 | 68 | 147233 | -1000000
6 | 6 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1081 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.52 | 0 | 9102.52 | 142360 | 0 | 63 | 67 | 142360 | -1000000
6 | 6 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.2984 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.27 | 0 | 9102.27 | 140810 | 0 | 63 | 67 | 140810 | -1000000
6 | 7 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9524 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 79.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.01 | 0 | 9102.01 | 139979 | 0 | 63 | 66 | 139979 | -1000000
6 | 7 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.175 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.8 | 0 | 9101.8 | 139080 | 0 | 63 | 66 | 139080 | -1000000
6 | 7 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1402 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.56 | 0 | 9101.56 | 138346 | 0 | 63 | 66 | 138346 | -1000000
6 | 7 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.2907 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 3.2 | 81.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10102.8 | 0 | 10102.8 | 141600 | 0 | 63 | 66 | 141600 | -1000000
6 | 7 | 5 | 3 | 23.8909 | 0 | 69.9783 | 0 | 12.8055 | 0 | 5.6249 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12331.8 | 0 | 12331.8 | 260415 | 0 | 63 | 66 | 260415 | -1000000
6 | 7 | 6 | 3 | 42.5778 | 0 | 140.608 | 0 | 50.5914 | 0 | 6.332 | 21.6756 | 0 | 0 | 0 | 0 | 261.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33330.8 | 0 | 33330.8 | 966745 | -6869.52 | 64 | 67 | 966745 | -1006869.52
6 | 7 | 7 | 3 | 39.5961 | 0 | 168.222 | 0 | 57.3906 | 0 | 25.335 | 21.4989 | 0 | 0 | 0 | 0 | 312.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36557.4 | 0 | 36557.4 | 1057560 | -16782.2 | 64 | 67 | 1057560 | -1016782.2
6 | 7 | 8 | 3 | 39.8955 | 0 | 173.795 | 0 | 60.5597 | 0 | 25.335 | 21.9392 | 0 | 0 | 0 | 0 | 321.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46266.5 | 0 | 46266.5 | 1087030 | -17695.2 | 65 | 68 | 1087030 | -1017695.2
6 | 7 | 9 | 3 | 41.0523 | 0 | 172.186 | 0 | 70.4458 | 0 | 25.335 | 22.7908 | 0 | 0 | 0 | 0 | 331.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115 | 0 | 72115 | 1192760 | -17357.3 | 67 | 73 | 1192760 | -1017357.3
6 | 7 | 10 | 3 | 41.2226 | 0 | 163.102 | 0 | 74.966 | 0 | 25.335 | 22.4969 | 0 | 0 | 0 | 0 | 327.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731 | 0 | 73731 | 1264440 | -14375 | 68 | 76 | 1264440 | -1014375
6 | 7 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 69.7929 | 0 | 25.335 | 22.9077 | 0 | 0 | 0 | 0 | 308.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.2 | 0 | 73731.2 | 1183110 | -10207 | 68 | 79 | 1183110 | -1010207
6 | 7 | 12 | 3 | 39.7747 | 0 | 150.207 | 0 | 71.961 | 0 | 25.335 | 23.2689 | 0 | 0 | 0 | 0 | 310.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.6 | 0 | 73732.6 | 1215050 | -9199.56 | 68 | 80 | 1215050 | -1009199.56
6 | 7 | 13 | 3 | 41.2386 | 0 | 165.698 | 0 | 82.6602 | 0 | 25.335 | 23.8501 | 0 | 0 | 0 | 0 | 338.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.1 | 0 | 73734.1 | 1386090 | -12222.7 | 69 | 81 | 1386090 | -1012222.7
6 | 7 | 14 | 3 | 40.6251 | 0 | 172.702 | 0 | 80.4656 | 0 | 25.335 | 23.4862 | 0 | 0 | 0 | 0 | 342.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72118.5 | 0 | 72118.5 | 1341370 | -16440.7 | 67 | 80 | 1341370 | -1016440.7
6 | 7 | 15 | 3 | 40.5369 | 0 | 173.986 | 0 | 85.2738 | 0 | 25.335 | 23.5204 | 0 | 0 | 0 | 0 | 348.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.1 | 0 | 65657.1 | 1422150 | -17862.6 | 68 | 81 | 1422150 | -1017862.6
6 | 7 | 16 | 3 | 40.2744 | 0 | 169.782 | 0 | 85.5761 | 0 | 25.335 | 23.4061 | 0 | 0 | 0 | 0 | 344.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349 | 0 | 54349 | 1444980 | -20956 | 68 | 81 | 1444980 | -1020956
6 | 7 | 17 | 3 | 35.4648 | 0 | 152.497 | 0 | 79.932 | 0 | 25.335 | 23.0194 | 0 | 0 | 0 | 0 | 316.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41425.8 | 0 | 41425.8 | 1366140 | -23924.2 | 68 | 81 | 1366140 | -1023924.2
6 | 7 | 18 | 3 | 24.6438 | 0 | 93.4203 | 0 | 53.7347 | 0 | 25.335 | 21.3646 | 0 | 0 | 0 | 0 | 218.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.1 | 0 | 25272.1 | 932529 | -18869.4 | 67 | 79 | 932529 | -1018869.4
6 | 7 | 19 | 3 | 18.0457 | 0 | 62.7906 | 0 | 11.9065 | 0 | 12.3672 | 8.818 | 0 | 0 | 0 | 1.2 | 115.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.1 | 0 | 18003.1 | 194114 | 0 | 66 | 76 | 194114 | -1000000
6 | 7 | 20 | 3 | 18.0672 | 0 | 54.6418 | 0 | 9.1874 | 0 | 8.6892 | 8.818 | 0 | 0 | 0 | 4 | 103.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196.2 | 0 | 17196.2 | 174009 | 0 | 66 | 73 | 174009 | -1000000
6 | 7 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 8.2334 | 0 | 7.7477 | 8.818 | 0 | 0 | 0 | 7.2 | 94.7193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10721.2 | 0 | 10721.2 | 159667 | 0 | 62 | 71 | 159667 | -1000000
6 | 7 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2386 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10460 | 0 | 10460 | 148877 | 0 | 60 | 69 | 148877 | -1000000
6 | 7 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.6057 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 5.6 | 79.3627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.69 | 0 | 9100.69 | 143794 | 0 | 58 | 66 | 143794 | -1000000
6 | 7 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 5.5494 | 0 | 5.4972 | 8.818 | 0 | 0 | 0 | 4.8 | 77.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.17 | 0 | 9100.17 | 142216 | 0 | 56 | 60 | 142216 | -1000000
6 | 8 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0496 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.84 | 0 | 9099.84 | 141378 | 0 | 57 | 60 | 141378 | -1000000
6 | 8 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0011 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.71 | 0 | 9099.71 | 140313 | 0 | 56 | 58 | 140313 | -1000000
6 | 8 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9568 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.83 | 0 | 9099.83 | 139345 | 0 | 55 | 57 | 139345 | -1000000
6 | 8 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0895 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10101.6 | 0 | 10101.6 | 142314 | 0 | 55 | 57 | 142314 | -1000000
6 | 8 | 5 | 4 | 23.5484 | 0 | 69.9783 | 0 | 11.6742 | 0 | 5.5553 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12331 | 0 | 12331 | 244350 | 0 | 54 | 57 | 244350 | -1000000
6 | 8 | 6 | 4 | 38.1559 | 0 | 140.608 | 0 | 36.8347 | 0 | 7.4158 | 20.804 | 0 | 0 | 0 | 0 | 243.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33330.1 | 0 | 33330.1 | 715508 | -8652.37 | 56 | 61 | 715508 | -1008652.37
6 | 8 | 7 | 4 | 39.0476 | 0 | 168.222 | 0 | 44.825 | 0 | 25.335 | 20.496 | 0 | 0 | 0 | 0 | 297.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36557.5 | 0 | 36557.5 | 824280 | -23121.1 | 56 | 63 | 824280 | -1023121.1
6 | 8 | 8 | 4 | 39.7452 | 0 | 173.795 | 0 | 50.5302 | 0 | 25.335 | 20.6664 | 0 | 0 | 0 | 0 | 310.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46267.1 | 0 | 46267.1 | 891001 | -21311.1 | 57 | 67 | 891001 | -1021311.1
6 | 8 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 52.0036 | 0 | 25.335 | 20.9186 | 0 | 0 | 0 | 0 | 311.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72117.1 | 0 | 72117.1 | 912336 | -21004.2 | 57 | 69 | 912336 | -1021004.2
6 | 8 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 53.3295 | 0 | 25.335 | 21.1848 | 0 | 0 | 0 | 0 | 304.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.5 | 0 | 73734.5 | 921017 | -17380.2 | 57 | 71 | 921017 | -1017380.2
6 | 8 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 49.2966 | 0 | 25.335 | 22.0153 | 0 | 0 | 0 | 0 | 287.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.4 | 0 | 73735.4 | 849688 | -13502.5 | 57 | 72 | 849688 | -1013502.5
6 | 8 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 55.9087 | 0 | 25.335 | 22.6102 | 0 | 0 | 0 | 0 | 293.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.6 | 0 | 73735.6 | 928268 | -14625.3 | 59 | 75 | 928268 | -1014625.3
6 | 8 | 13 | 4 | 41.2719 | 0 | 165.698 | 0 | 60.3378 | 0 | 25.335 | 23.0461 | 0 | 0 | 0 | 0 | 315.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.2 | 0 | 73735.2 | 1013500 | -14814 | 59 | 77 | 1013500 | -1014814
6 | 8 | 14 | 4 | 40.6512 | 0 | 172.702 | 0 | 63.987 | 0 | 25.335 | 22.7363 | 0 | 0 | 0 | 0 | 325.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.5 | 0 | 72119.5 | 1072430 | -18347.6 | 59 | 77 | 1072430 | -1018347.6
6 | 8 | 15 | 4 | 40.5357 | 0 | 173.986 | 0 | 66.382 | 0 | 25.335 | 22.922 | 0 | 0 | 0 | 0 | 329.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.9 | 0 | 65657.9 | 1115940 | -19903.8 | 59 | 78 | 1115940 | -1019903.8
6 | 8 | 16 | 4 | 40.2851 | 0 | 169.782 | 0 | 65.2375 | 0 | 25.335 | 23.1764 | 0 | 0 | 0 | 0 | 323.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54350 | 0 | 54350 | 1109580 | -18849.5 | 59 | 79 | 1109580 | -1018849.5
6 | 8 | 17 | 4 | 35.4755 | 0 | 152.497 | 0 | 59.8516 | 0 | 25.335 | 22.9209 | 0 | 0 | 0 | 0 | 296.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.6 | 0 | 41426.6 | 1031650 | -20184.3 | 59 | 79 | 1031650 | -1020184.3
6 | 8 | 18 | 4 | 24.7991 | 0 | 93.4203 | 0 | 39.5251 | 0 | 25.335 | 21.2582 | 0 | 0 | 0 | 0 | 204.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.7 | 0 | 25272.7 | 689118 | -11081.8 | 59 | 75 | 689118 | -1011081.8
6 | 8 | 19 | 4 | 18.2391 | 0 | 62.7906 | 0 | 10.5964 | 0 | 10.0963 | 8.818 | 0 | 0 | 0 | 1.2 | 111.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.6 | 0 | 18003.6 | 194409 | 0 | 59 | 72 | 194409 | -1000000
6 | 8 | 20 | 4 | 17.9679 | 0 | 54.6418 | 0 | 8.1128 | 0 | 7.4174 | 8.818 | 0 | 0 | 0 | 4 | 100.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197 | 0 | 17197 | 174313 | 0 | 59 | 67 | 174313 | -1000000
6 | 8 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7221 | 0 | 7.1017 | 8.818 | 0 | 0 | 0 | 7.2 | 93.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10722.4 | 0 | 10722.4 | 160444 | 0 | 57 | 64 | 160444 | -1000000
6 | 8 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.1885 | 0 | 6.7874 | 8.818 | 0 | 0 | 0 | 6.4 | 84.7245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10461.6 | 0 | 10461.6 | 149305 | 0 | 56 | 62 | 149305 | -1000000
6 | 8 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.8773 | 0 | 6.5694 | 8.818 | 0 | 0 | 0 | 5.6 | 80.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.66 | 0 | 9102.66 | 144402 | 0 | 56 | 60 | 144402 | -1000000
6 | 8 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.3216 | 0 | 6.8186 | 8.818 | 0 | 0 | 0 | 4.8 | 80.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.18 | 0 | 9102.18 | 142670 | 0 | 56 | 60 | 142670 | -1000000
6 | 9 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2637 | 0 | 6.7844 | 8.818 | 0 | 0 | 0 | 4.8 | 80.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.83 | 0 | 9101.83 | 141447 | 0 | 54 | 57 | 141447 | -1000000
6 | 9 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2283 | 0 | 6.7638 | 8.818 | 0 | 0 | 0 | 4.8 | 80.7894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.58 | 0 | 9101.58 | 140702 | 0 | 55 | 57 | 140702 | -1000000
6 | 9 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.1744 | 0 | 6.7328 | 8.818 | 0 | 0 | 0 | 4.8 | 80.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.82 | 0 | 9101.82 | 139549 | 0 | 54 | 57 | 139549 | -1000000
6 | 9 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.307 | 0 | 6.8099 | 8.818 | 0 | 0 | 0 | 3.2 | 82.7794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10103.7 | 0 | 10103.7 | 142436 | 0 | 53 | 56 | 142436 | -1000000
6 | 9 | 5 | 5 | 23.7951 | 0 | 69.9783 | 0 | 11.9325 | 0 | 11.5047 | 12.8287 | 0 | 0 | 0 | 1.6 | 131.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12332.7 | 0 | 12332.7 | 242392 | 0 | 53 | 56 | 242392 | -1000000
6 | 9 | 6 | 5 | 37.1827 | 0 | 140.608 | 0 | 32.0941 | 0 | 6.332 | 20.1724 | 0 | 0 | 0 | 0 | 236.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33332.4 | 0 | 33332.4 | 591411 | -10022.1 | 53 | 58 | 591411 | -1010022.1
6 | 9 | 7 | 5 | 38.912 | 0 | 168.222 | 0 | 40.1136 | 0 | 25.335 | 20.5902 | 0 | 0 | 0 | 0 | 293.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36559.7 | 0 | 36559.7 | 729687 | -24817.2 | 54 | 62 | 729687 | -1024817.2
6 | 9 | 8 | 5 | 39.6631 | 0 | 173.795 | 0 | 44.4934 | 0 | 25.335 | 20.5769 | 0 | 0 | 0 | 0 | 303.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46268 | 0 | 46268 | 788337 | -22895.9 | 54 | 66 | 788337 | -1022895.9
6 | 9 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 50.8192 | 0 | 25.335 | 21.0233 | 0 | 0 | 0 | 0 | 309.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116.4 | 0 | 72116.4 | 877569 | -21401 | 56 | 70 | 877569 | -1021401
6 | 9 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 55.4371 | 0 | 25.335 | 21.3911 | 0 | 0 | 0 | 0 | 306.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.5 | 0 | 73734.5 | 931629 | -17399.3 | 57 | 74 | 931629 | -1017399.3
6 | 9 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 52.9473 | 0 | 25.335 | 22.3742 | 0 | 0 | 0 | 0 | 291.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.5 | 0 | 73735.5 | 895463 | -12743.6 | 57 | 76 | 895463 | -1012743.6
6 | 9 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 56.6433 | 0 | 25.335 | 22.6329 | 0 | 0 | 0 | 0 | 294.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73736 | 0 | 73736 | 959884 | -17059.2 | 59 | 78 | 959884 | -1017059.2
6 | 9 | 13 | 5 | 41.2389 | 0 | 165.698 | 0 | 62.0842 | 0 | 25.335 | 23.1946 | 0 | 0 | 0 | 0 | 317.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.9 | 0 | 73735.9 | 1046620 | -14414.3 | 59 | 79 | 1046620 | -1014414.3
6 | 9 | 14 | 5 | 40.6443 | 0 | 172.702 | 0 | 69.224 | 0 | 25.335 | 22.8725 | 0 | 0 | 0 | 0 | 330.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72120.1 | 0 | 72120.1 | 1161520 | -18028.9 | 61 | 81 | 1161520 | -1018028.9
6 | 9 | 15 | 5 | 40.536 | 0 | 173.986 | 0 | 69.6954 | 0 | 25.335 | 23.0318 | 0 | 0 | 0 | 0 | 332.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65658.7 | 0 | 65658.7 | 1170840 | -19817.2 | 60 | 81 | 1170840 | -1019817.2
6 | 9 | 16 | 5 | 40.2781 | 0 | 169.782 | 0 | 69.119 | 0 | 25.335 | 23.0273 | 0 | 0 | 0 | 0 | 327.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54350.7 | 0 | 54350.7 | 1177030 | -24129.1 | 60 | 82 | 1177030 | -1024129.1
6 | 9 | 17 | 5 | 35.4665 | 0 | 152.497 | 0 | 64.7261 | 0 | 25.335 | 22.8222 | 0 | 0 | 0 | 0 | 300.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41427.3 | 0 | 41427.3 | 1116760 | -23836.4 | 61 | 81 | 1116760 | -1023836.4
6 | 9 | 18 | 5 | 24.5943 | 0 | 93.4203 | 0 | 45.359 | 0 | 25.335 | 21.2477 | 0 | 0 | 0 | 0 | 209.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25273.4 | 0 | 25273.4 | 792963 | -22377.1 | 61 | 80 | 792963 | -1022377.1
6 | 9 | 19 | 5 | 18.106 | 0 | 62.7906 | 0 | 11.8077 | 0 | 12.2161 | 8.818 | 0 | 0 | 0 | 1.2 | 114.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18004.3 | 0 | 18004.3 | 194962 | 0 | 61 | 76 | 194962 | -1000000
6 | 9 | 20 | 5 | 17.8928 | 0 | 54.6418 | 0 | 9.182 | 0 | 8.702 | 8.818 | 0 | 0 | 0 | 4 | 103.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197.3 | 0 | 17197.3 | 174434 | 0 | 60 | 73 | 174434 | -1000000
6 | 9 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.2335 | 0 | 7.7821 | 8.818 | 0 | 0 | 0 | 7.2 | 94.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10722.6 | 0 | 10722.6 | 160923 | 0 | 59 | 71 | 160923 | -1000000
6 | 9 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.5948 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 6.4 | 83.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10461.3 | 0 | 10461.3 | 149752 | 0 | 58 | 70 | 149752 | -1000000
6 | 9 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.6312 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 5.6 | 80.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.08 | 0 | 9102.08 | 144999 | 0 | 59 | 70 | 144999 | -1000000
6 | 9 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.2222 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 75.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.46 | 0 | 9101.46 | 143070 | 0 | 59 | 69 | 143070 | -1000000
6 | 10 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.13 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.94 | 0 | 9100.94 | 142026 | 0 | 59 | 68 | 142026 | -1000000
6 | 10 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.3604 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.16 | 0 | 9101.16 | 141243 | 0 | 60 | 68 | 141243 | -1000000
6 | 10 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.315 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.04 | 0 | 9101.04 | 140288 | 0 | 60 | 68 | 140288 | -1000000
6 | 10 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2757 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 3.2 | 73.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101 | 0 | 9101 | 139467 | 0 | 60 | 68 | 139467 | -1000000
6 | 10 | 5 | 6 | 6.2691 | 0 | 42.7453 | 0 | 7.5564 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 1.6 | 72.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.91 | 0 | 9100.91 | 138823 | 0 | 61 | 69 | 138823 | -1000000
6 | 10 | 6 | 6 | 5.4419 | 0 | 42.7453 | 0 | 7.6883 | 0 | 7.0426 | 8.818 | 0 | 0 | 0 | 0 | 71.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.79 | 0 | 9100.79 | 138241 | 0 | 62 | 68 | 138241 | -1000000
6 | 10 | 7 | 6 | 4.6922 | 0 | 42.7453 | 0 | 23.6967 | 0 | 25.335 | 19.1015 | 0 | 0 | 0 | 0 | 115.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.67 | 0 | 9100.67 | 457676 | -3709.22 | 62 | 65 | 457676 | -1003709.22
6 | 10 | 8 | 6 | 5.3567 | 0 | 42.7453 | 0 | 21.6388 | 0 | 25.335 | 19.062 | 0 | 0 | 0 | 0 | 114.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.4 | 0 | 9100.4 | 402894 | -6146.91 | 63 | 64 | 402894 | -1006146.91
6 | 10 | 9 | 6 | 6.4483 | 0 | 42.7453 | 0 | 20.332 | 0 | 25.335 | 18.9592 | 0 | 0 | 0 | 0 | 113.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9116.36 | 0 | 9116.36 | 371448 | -11428.6 | 63 | 64 | 371448 | -1011428.6
6 | 10 | 10 | 6 | 5.7979 | 0 | 42.7453 | 0 | 23.9211 | 0 | 25.335 | 18.9627 | 0 | 0 | 0 | 0 | 116.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9118.35 | 0 | 9118.35 | 414396 | -13130.8 | 65 | 67 | 414396 | -1013130.8
6 | 10 | 11 | 6 | 5.6776 | 0 | 42.7453 | 0 | 25.6946 | 0 | 25.335 | 18.9875 | 0 | 0 | 0 | 0 | 118.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9120.2 | 0 | 9120.2 | 445951 | -13848 | 66 | 69 | 445951 | -1013848
6 | 10 | 12 | 6 | 5.63 | 0 | 42.7453 | 0 | 30.0439 | 0 | 25.335 | 19.0369 | 0 | 0 | 0 | 0 | 122.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9121.38 | 0 | 9121.38 | 504179 | -14299.6 | 68 | 72 | 504179 | -1014299.6
6 | 10 | 13 | 6 | 5.5527 | 0 | 42.7453 | 0 | 31.7613 | 0 | 25.335 | 19.0911 | 0 | 0 | 0 | 0 | 124.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9122.18 | 0 | 9122.18 | 538973 | -14516.3 | 69 | 73 | 538973 | -1014516.3
6 | 10 | 14 | 6 | 5.6207 | 0 | 42.7453 | 0 | 9.0699 | 0 | 8.1712 | 8.818 | 0 | 0 | 0 | 0 | 74.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9122.87 | 0 | 9122.87 | 133668 | 0 | 70 | 74 | 133668 | -1000000
6 | 10 | 15 | 6 | 5.611 | 0 | 42.7453 | 0 | 8.6842 | 0 | 7.8951 | 8.818 | 0 | 0 | 0 | 0 | 73.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9123.47 | 0 | 9123.47 | 133438 | 0 | 71 | 75 | 133438 | -1000000
6 | 10 | 16 | 6 | 5.768 | 0 | 42.7453 | 0 | 8.2341 | 0 | 7.5844 | 8.818 | 0 | 0 | 0 | 0 | 73.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9117.07 | 0 | 9117.07 | 133360 | 0 | 73 | 78 | 133360 | -1000000
6 | 10 | 17 | 6 | 5.4718 | 0 | 42.7453 | 0 | 8.0769 | 0 | 7.5296 | 8.818 | 0 | 0 | 0 | 0 | 72.6417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9113.97 | 0 | 9113.97 | 133186 | 0 | 74 | 80 | 133186 | -1000000
6 | 10 | 18 | 6 | 5.5428 | 0 | 42.7453 | 0 | 7.9726 | 0 | 7.482 | 8.818 | 0 | 0 | 0 | 0 | 72.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.39 | 0 | 9111.39 | 132604 | 0 | 71 | 78 | 132604 | -1000000
6 | 10 | 19 | 6 | 6.6576 | 0 | 42.7453 | 0 | 7.9235 | 0 | 7.4607 | 8.818 | 0 | 0 | 0 | 1.2 | 74.8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9109.54 | 0 | 9109.54 | 132372 | 0 | 71 | 77 | 132372 | -1000000
6 | 10 | 20 | 6 | 8.4764 | 0 | 42.7453 | 0 | 7.8881 | 0 | 7.4444 | 8.818 | 0 | 0 | 0 | 4 | 79.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.68 | 0 | 9107.68 | 132162 | 0 | 71 | 75 | 132162 | -1000000
6 | 10 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.5943 | 0 | 7.3516 | 8.818 | 0 | 0 | 0 | 7.2 | 82.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.26 | 0 | 9106.26 | 131939 | 0 | 71 | 75 | 131939 | -1000000
6 | 10 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.8623 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 79.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9105.14 | 0 | 9105.14 | 131399 | 0 | 68 | 74 | 131399 | -1000000
6 | 10 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.1823 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 77.6235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.34 | 0 | 9104.34 | 131167 | 0 | 68 | 71 | 131167 | -1000000
6 | 10 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.6768 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3450.09 | 0 | 3450.09 | 130929 | 0 | 69 | 70 | 130929 | -1000000
6 | 11 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.9246 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449.38 | 0 | 3449.38 | 130440 | 0 | 67 | 70 | 130440 | -1000000
6 | 11 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6007 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449.04 | 0 | 3449.04 | 130155 | 0 | 67 | 69 | 130155 | -1000000
6 | 11 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5448 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.73 | 0 | 3448.73 | 129782 | 0 | 66 | 68 | 129782 | -1000000
6 | 11 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.1905 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 3.2 | 71.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.49 | 0 | 3448.49 | 129464 | 0 | 65 | 66 | 129464 | -1000000
6 | 11 | 5 | 7 | 5.0189 | 0 | 42.7453 | 0 | 7.0161 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 1.6 | 70.6773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.28 | 0 | 3448.28 | 129272 | 0 | 66 | 67 | 129272 | -1000000
6 | 11 | 6 | 7 | 4.0498 | 0 | 42.7453 | 0 | 6.7382 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 0 | 67.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.18 | 0 | 3448.18 | 129030 | 0 | 66 | 67 | 129030 | -1000000
6 | 11 | 7 | 7 | 3.888 | 0 | 42.7453 | 0 | 7.3487 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 0 | 68.2787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.15 | 0 | 3448.15 | 128891 | 0 | 67 | 69 | 128891 | -1000000
6 | 11 | 8 | 7 | 4.0625 | 0 | 42.7453 | 0 | 7.1105 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447.79 | 0 | 3447.79 | 128679 | 0 | 67 | 70 | 128679 | -1000000
6 | 11 | 9 | 7 | 4.6413 | 0 | 42.7453 | 0 | 7.4597 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 0 | 69.1435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447.31 | 0 | 3447.31 | 128470 | 0 | 67 | 72 | 128470 | -1000000
6 | 11 | 10 | 7 | 4.3013 | 0 | 42.7453 | 0 | 9.3108 | 0 | 5.502 | 12.8287 | 0 | 0 | 0 | 0 | 74.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446.91 | 0 | 3446.91 | 192148 | 0 | 67 | 70 | 192148 | -1000000
6 | 11 | 11 | 7 | 4.3072 | 0 | 42.7453 | 0 | 7.1795 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446.09 | 0 | 3446.09 | 128169 | 0 | 68 | 71 | 128169 | -1000000
6 | 11 | 12 | 7 | 4.2564 | 0 | 42.7453 | 0 | 7.4903 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 0 | 68.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445.25 | 0 | 3445.25 | 128180 | 0 | 69 | 73 | 128180 | -1000000
6 | 11 | 13 | 7 | 4.3195 | 0 | 42.7453 | 0 | 3.892 | 0 | 5.5381 | 8.818 | 0 | 0 | 0 | 0 | 65.3129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.07 | 0 | 3444.07 | 127055 | 0 | 60 | 63 | 127055 | -1000000
6 | 11 | 14 | 7 | 4.2748 | 0 | 42.7453 | 0 | 5.9231 | 0 | 5.4905 | 8.818 | 0 | 0 | 0 | 0 | 67.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443.06 | 0 | 3443.06 | 127290 | 0 | 59 | 61 | 127290 | -1000000
6 | 11 | 15 | 7 | 4.3532 | 0 | 42.7453 | 0 | 6.1281 | 0 | 5.4881 | 8.818 | 0 | 0 | 0 | 0 | 67.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.79 | 0 | 3441.79 | 126831 | 0 | 56 | 59 | 126831 | -1000000
6 | 11 | 16 | 7 | 4.7071 | 0 | 42.7453 | 0 | 8.4268 | 0 | 5.4819 | 12.8287 | 0 | 0 | 0 | 0 | 74.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.3 | 0 | 3441.3 | 172295 | 0 | 55 | 57 | 172295 | -1000000
6 | 11 | 17 | 7 | 4.8919 | 0 | 42.7453 | 0 | 6.4028 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 0 | 68.3428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441 | 0 | 3441 | 126473 | 0 | 54 | 56 | 126473 | -1000000
6 | 11 | 18 | 7 | 5.1695 | 0 | 42.7453 | 0 | 6.3636 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 0 | 68.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.03 | 0 | 3441.03 | 126377 | 0 | 54 | 56 | 126377 | -1000000
6 | 11 | 19 | 7 | 5.8488 | 0 | 42.7453 | 0 | 6.3564 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 1.2 | 70.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.61 | 0 | 3441.61 | 126218 | 0 | 54 | 55 | 126218 | -1000000
6 | 11 | 20 | 7 | 6.5232 | 0 | 42.7453 | 0 | 6.3408 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4 | 73.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.2 | 0 | 3442.2 | 125875 | 0 | 53 | 54 | 125875 | -1000000
6 | 11 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3238 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.97 | 0 | 3442.97 | 125501 | 0 | 51 | 52 | 125501 | -1000000
6 | 11 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3189 | 0 | 5.4857 | 8.818 | 0 | 0 | 0 | 6.4 | 76.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3443.81 | 0 | 3443.81 | 125399 | 0 | 51 | 52 | 125399 | -1000000
6 | 11 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3063 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 5.6 | 75.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.79 | 0 | 3444.79 | 125119 | 0 | 50 | 51 | 125119 | -1000000
6 | 11 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 8.4867 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.44 | 0 | 9099.44 | 132542 | -2425.76 | 50 | 51 | 132542 | -1002425.76
6 | 12 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3061 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.57 | 0 | 9100.57 | 124995 | 0 | 49 | 50 | 124995 | -1000000
6 | 12 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2967 | 0 | 5.486 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.9 | 0 | 9100.9 | 124914 | 0 | 49 | 50 | 124914 | -1000000
6 | 12 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2893 | 0 | 5.486 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.75 | 0 | 9101.75 | 124750 | 0 | 49 | 51 | 124750 | -1000000
6 | 12 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 8.4348 | 0 | 5.8974 | 12.9754 | 0 | 0 | 0 | 3.2 | 87.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10104 | 0 | 10104 | 128316 | -6248.71 | 49 | 51 | 128316 | -1006248.71
6 | 12 | 5 | 1 | 23.7639 | 0 | 69.9783 | 0 | 8.5746 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 1.6 | 118.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12334.1 | 0 | 12334.1 | 175561 | 0 | 50 | 51 | 175561 | -1000000
6 | 12 | 6 | 1 | 41.7801 | 0 | 140.608 | 0 | 31.618 | 0 | 6.332 | 19.6508 | 0 | 0 | 0 | 0 | 239.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33334.1 | 0 | 33334.1 | 409534 | -36437.7 | 50 | 52 | 409534 | -1036437.7
6 | 12 | 7 | 1 | 39.1865 | 0 | 168.222 | 0 | 23.1643 | 0 | 6.332 | 19.5625 | 0 | 0 | 0 | 0 | 256.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36561.9 | 0 | 36561.9 | 493833 | -23020.7 | 50 | 52 | 493833 | -1023020.7
6 | 12 | 8 | 1 | 39.8394 | 0 | 173.795 | 0 | 34.0334 | 0 | 6.332 | 19.5309 | 0 | 0 | 0 | 0 | 273.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46266.6 | 0 | 46266.6 | 545191 | -33450.2 | 51 | 53 | 545191 | -1033450.2
6 | 12 | 9 | 1 | 41.0121 | 0 | 172.186 | 0 | 33.4481 | 0 | 6.332 | 19.7957 | 0 | 0 | 0 | 0 | 272.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72114.4 | 0 | 72114.4 | 585891 | -22020 | 52 | 55 | 585891 | -1022020
6 | 12 | 10 | 1 | 41.5067 | 0 | 163.102 | 0 | 34.6242 | 0 | 6.332 | 20.0109 | 0 | 0 | 0 | 0 | 265.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.7 | 0 | 73730.7 | 606233 | -19779.4 | 53 | 57 | 606233 | -1019779.4
6 | 12 | 11 | 1 | 40.8631 | 0 | 149.692 | 0 | 33.3041 | 0 | 6.332 | 20.1442 | 0 | 0 | 0 | 0 | 250.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731 | 0 | 73731 | 615161 | -13521.3 | 55 | 60 | 615161 | -1013521.3
6 | 12 | 12 | 1 | 39.7574 | 0 | 150.207 | 0 | 36.7083 | 0 | 6.332 | 20.6994 | 0 | 0 | 0 | 0 | 253.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.4 | 0 | 73731.4 | 677939 | -10739.1 | 57 | 63 | 677939 | -1010739.1
6 | 12 | 13 | 1 | 41.2345 | 0 | 165.698 | 0 | 46.9588 | 0 | 6.332 | 21.6164 | 0 | 0 | 0 | 0 | 281.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732 | 0 | 73732 | 845708 | -12146.2 | 59 | 66 | 845708 | -1012146.2
6 | 12 | 14 | 1 | 40.6656 | 0 | 172.702 | 0 | 53.8206 | 0 | 6.857 | 22.2318 | 0 | 0 | 0 | 0 | 296.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116.9 | 0 | 72116.9 | 947057 | -13706.7 | 60 | 69 | 947057 | -1013706.7
6 | 12 | 15 | 1 | 40.5535 | 0 | 173.986 | 0 | 62.4695 | 0 | 11.5408 | 22.6531 | 0 | 0 | 0 | 0 | 311.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65654.8 | 0 | 65654.8 | 1076800 | -13905.2 | 62 | 72 | 1076800 | -1013905.2
6 | 12 | 16 | 1 | 40.2945 | 0 | 169.782 | 0 | 66.3744 | 0 | 25.335 | 22.8589 | 0 | 0 | 0 | 0 | 324.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54346.6 | 0 | 54346.6 | 1151270 | -12827.9 | 64 | 74 | 1151270 | -1012827.9
6 | 12 | 17 | 1 | 35.4689 | 0 | 152.497 | 0 | 62.0459 | 0 | 6.6124 | 21.9799 | 0 | 0 | 0 | 0 | 278.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41423.3 | 0 | 41423.3 | 1102200 | -18726.3 | 64 | 74 | 1102200 | -1018726.3
6 | 12 | 18 | 1 | 24.5831 | 0 | 93.4203 | 0 | 43.8377 | 0 | 6.332 | 20.0546 | 0 | 0 | 0 | 0 | 188.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25269.6 | 0 | 25269.6 | 795474 | -22222.8 | 64 | 75 | 795474 | -1022222.8
6 | 12 | 19 | 1 | 18.5353 | 0 | 62.7906 | 0 | 9.4605 | 0 | 5.5079 | 8.818 | 0 | 0 | 0 | 1.2 | 106.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18001.2 | 0 | 18001.2 | 187355 | 0 | 64 | 72 | 187355 | -1000000
6 | 12 | 20 | 1 | 17.5439 | 0 | 54.6418 | 0 | 8.1678 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 4 | 98.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17195.4 | 0 | 17195.4 | 167080 | 0 | 62 | 70 | 167080 | -1000000
6 | 12 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 6.545 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 7.2 | 90.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10721.5 | 0 | 10721.5 | 154387 | 0 | 62 | 65 | 154387 | -1000000
6 | 12 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.7404 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 6.4 | 82.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10461 | 0 | 10461 | 143325 | 0 | 61 | 63 | 143325 | -1000000
6 | 12 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.747 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 5.6 | 79.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.24 | 0 | 9102.24 | 138748 | 0 | 61 | 62 | 138748 | -1000000
6 | 12 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6401 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.19 | 0 | 9102.19 | 137255 | 0 | 60 | 61 | 137255 | -1000000
6 | 13 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5608 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.09 | 0 | 9102.09 | 136293 | 0 | 58 | 59 | 136293 | -1000000
6 | 13 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7766 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.39 | 0 | 9102.39 | 135403 | 0 | 56 | 59 | 135403 | -1000000
6 | 13 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7453 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.26 | 0 | 9102.26 | 134720 | 0 | 54 | 57 | 134720 | -1000000
6 | 13 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.8876 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 3.2 | 81.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10103.9 | 0 | 10103.9 | 137900 | 0 | 53 | 55 | 137900 | -1000000
6 | 13 | 5 | 2 | 23.4119 | 0 | 69.9783 | 0 | 11.2127 | 0 | 5.539 | 12.8287 | 0 | 0 | 0 | 1.6 | 124.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12333.5 | 0 | 12333.5 | 234143 | 0 | 53 | 55 | 234143 | -1000000
6 | 13 | 6 | 2 | 38.0182 | 0 | 140.608 | 0 | 38.3796 | 0 | 6.332 | 20.4639 | 0 | 0 | 0 | 0 | 243.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33333.1 | 0 | 33333.1 | 597306 | -11574.2 | 55 | 58 | 597306 | -1011574.2
6 | 13 | 7 | 2 | 39.0476 | 0 | 168.222 | 0 | 37.5354 | 0 | 6.332 | 20.2999 | 0 | 0 | 0 | 0 | 271.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36560.5 | 0 | 36560.5 | 771354 | -17319.3 | 56 | 63 | 771354 | -1017319.3
6 | 13 | 8 | 2 | 39.7651 | 0 | 173.795 | 0 | 43.5641 | 0 | 6.332 | 20.4532 | 0 | 0 | 0 | 0 | 283.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46267.9 | 0 | 46267.9 | 857171 | -16631.3 | 57 | 68 | 857171 | -1016631.3
6 | 13 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 49.9032 | 0 | 6.332 | 20.9145 | 0 | 0 | 0 | 0 | 289.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72117.4 | 0 | 72117.4 | 883706 | -16226.3 | 57 | 69 | 883706 | -1016226.3
6 | 13 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 47.5858 | 0 | 25.335 | 21.1864 | 0 | 0 | 0 | 0 | 298.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.1 | 0 | 73735.1 | 854364 | -14017.1 | 56 | 70 | 854364 | -1014017.1
6 | 13 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 48.4152 | 0 | 25.335 | 22.0164 | 0 | 0 | 0 | 0 | 286.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.6 | 0 | 73735.6 | 839563 | -9657.41 | 58 | 73 | 839563 | -1009657.41
6 | 13 | 12 | 2 | 39.9727 | 0 | 150.207 | 0 | 43.7874 | 0 | 25.335 | 22.1477 | 0 | 0 | 0 | 0 | 281.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.4 | 0 | 73735.4 | 789004 | -9751.15 | 57 | 71 | 789004 | -1009751.15
6 | 13 | 13 | 2 | 41.7205 | 0 | 165.698 | 0 | 52.0843 | 0 | 25.335 | 22.7194 | 0 | 0 | 0 | 0 | 307.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735.2 | 0 | 73735.2 | 908497 | -12717.6 | 58 | 72 | 908497 | -1012717.6
6 | 13 | 14 | 2 | 40.7386 | 0 | 172.702 | 0 | 51.4438 | 0 | 25.335 | 23.0542 | 0 | 0 | 0 | 0 | 313.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72118.5 | 0 | 72118.5 | 923691 | -16567.1 | 57 | 70 | 923691 | -1016567.1
6 | 13 | 15 | 2 | 40.5155 | 0 | 173.986 | 0 | 57.6515 | 0 | 25.335 | 23.2502 | 0 | 0 | 0 | 0 | 320.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65656.4 | 0 | 65656.4 | 997145 | -17397.2 | 58 | 72 | 997145 | -1017397.2
6 | 13 | 16 | 2 | 40.4996 | 0 | 169.782 | 0 | 50.0579 | 0 | 25.335 | 23.0128 | 0 | 0 | 0 | 0 | 308.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54348.6 | 0 | 54348.6 | 897403 | -17218.7 | 55 | 71 | 897403 | -1017218.7
6 | 13 | 17 | 2 | 35.4797 | 0 | 152.497 | 0 | 46.8073 | 0 | 25.335 | 22.3407 | 0 | 0 | 0 | 0 | 282.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41425.5 | 0 | 41425.5 | 844481 | -13792.8 | 56 | 71 | 844481 | -1013792.8
6 | 13 | 18 | 2 | 24.587 | 0 | 93.4203 | 0 | 33.7985 | 0 | 25.335 | 20.2286 | 0 | 0 | 0 | 0 | 197.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25271.1 | 0 | 25271.1 | 613345 | -13850.8 | 55 | 71 | 613345 | -1013850.8
6 | 13 | 19 | 2 | 18.4435 | 0 | 62.7906 | 0 | 10.1875 | 0 | 9.6085 | 8.818 | 0 | 0 | 0 | 1.2 | 111.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18002.8 | 0 | 18002.8 | 191737 | 0 | 55 | 69 | 191737 | -1000000
6 | 13 | 20 | 2 | 17.4205 | 0 | 54.6418 | 0 | 6.4443 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4 | 96.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197 | 0 | 17197 | 171986 | 0 | 55 | 61 | 171986 | -1000000
6 | 13 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.5655 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10723 | 0 | 10723 | 158066 | 0 | 54 | 58 | 158066 | -1000000
6 | 13 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.3163 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10462.8 | 0 | 10462.8 | 147044 | 0 | 54 | 57 | 147044 | -1000000
6 | 13 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.0825 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 5.6 | 79.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.2 | 0 | 9104.2 | 142028 | 0 | 53 | 56 | 142028 | -1000000
6 | 13 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.006 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.24 | 0 | 9104.24 | 140411 | 0 | 52 | 55 | 140411 | -1000000
6 | 14 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9651 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.86 | 0 | 9104.86 | 139528 | 0 | 52 | 54 | 139528 | -1000000
6 | 14 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9182 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9105.39 | 0 | 9105.39 | 138500 | 0 | 51 | 53 | 138500 | -1000000
6 | 14 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8827 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.03 | 0 | 9106.03 | 137725 | 0 | 51 | 53 | 137725 | -1000000
6 | 14 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.0129 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10108.2 | 0 | 10108.2 | 140638 | 0 | 51 | 53 | 140638 | -1000000
6 | 14 | 5 | 3 | 23.9317 | 0 | 69.9783 | 0 | 10.6332 | 0 | 5.5213 | 12.8287 | 0 | 0 | 0 | 1.6 | 124.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12338.1 | 0 | 12338.1 | 221190 | 0 | 52 | 54 | 221190 | -1000000
6 | 14 | 6 | 3 | 42.0931 | 0 | 140.608 | 0 | 29.8586 | 0 | 6.332 | 19.6228 | 0 | 0 | 0 | 0 | 238.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33338 | 0 | 33338 | 467321 | -16298.6 | 53 | 55 | 467321 | -1016298.6
6 | 14 | 7 | 3 | 39.2961 | 0 | 168.222 | 0 | 37.054 | 0 | 6.332 | 19.5246 | 0 | 0 | 0 | 0 | 270.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36565.5 | 0 | 36565.5 | 604639 | -29747.2 | 54 | 56 | 604639 | -1029747.2
6 | 14 | 8 | 3 | 39.8479 | 0 | 173.795 | 0 | 36.4557 | 0 | 6.332 | 19.7935 | 0 | 0 | 0 | 0 | 276.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46270.8 | 0 | 46270.8 | 650937 | -25013 | 54 | 58 | 650937 | -1025013
6 | 14 | 9 | 3 | 41.0768 | 0 | 172.186 | 0 | 38.8831 | 0 | 25.335 | 20.1746 | 0 | 0 | 0 | 0 | 297.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72118.1 | 0 | 72118.1 | 728004 | -22747.9 | 56 | 61 | 728004 | -1022747.9
6 | 14 | 10 | 3 | 41.4521 | 0 | 163.102 | 0 | 41.8619 | 0 | 25.335 | 20.3585 | 0 | 0 | 0 | 0 | 292.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.2 | 0 | 73734.2 | 782573 | -19609 | 58 | 62 | 782573 | -1019609
6 | 14 | 11 | 3 | 40.9277 | 0 | 149.692 | 0 | 42.3823 | 0 | 25.335 | 20.5648 | 0 | 0 | 0 | 0 | 278.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.3 | 0 | 73734.3 | 773026 | -15264.1 | 60 | 64 | 773026 | -1015264.1
6 | 14 | 12 | 3 | 39.8332 | 0 | 150.207 | 0 | 47.8235 | 0 | 25.335 | 20.9328 | 0 | 0 | 0 | 0 | 284.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.6 | 0 | 73734.6 | 846151 | -12834.8 | 62 | 67 | 846151 | -1012834.8
6 | 14 | 13 | 3 | 41.2393 | 0 | 165.698 | 0 | 59.2922 | 0 | 25.335 | 22.0637 | 0 | 0 | 0 | 0 | 313.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73735 | 0 | 73735 | 1030780 | -14801.1 | 64 | 70 | 1030780 | -1014801.1
6 | 14 | 14 | 3 | 40.6288 | 0 | 172.702 | 0 | 66.8456 | 0 | 25.335 | 22.6005 | 0 | 0 | 0 | 0 | 328.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.8 | 0 | 72119.8 | 1140470 | -17435.5 | 65 | 73 | 1140470 | -1017435.5
6 | 14 | 15 | 3 | 40.5377 | 0 | 173.986 | 0 | 71.4775 | 0 | 25.335 | 22.9535 | 0 | 0 | 0 | 0 | 334.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.6 | 0 | 65657.6 | 1207250 | -18081 | 65 | 76 | 1207250 | -1018081
6 | 14 | 16 | 3 | 40.2858 | 0 | 169.782 | 0 | 67.2077 | 0 | 25.335 | 23.1284 | 0 | 0 | 0 | 0 | 325.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349.4 | 0 | 54349.4 | 1168000 | -17498.3 | 64 | 74 | 1168000 | -1017498.3
6 | 14 | 17 | 3 | 35.4654 | 0 | 152.497 | 0 | 59.5885 | 0 | 25.335 | 22.5002 | 0 | 0 | 0 | 0 | 295.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.1 | 0 | 41426.1 | 1057810 | -13806 | 63 | 73 | 1057810 | -1013806
6 | 14 | 18 | 3 | 24.6315 | 0 | 93.4203 | 0 | 42.5517 | 0 | 25.335 | 20.4816 | 0 | 0 | 0 | 0 | 206.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.2 | 0 | 25272.2 | 750497 | -10228.2 | 64 | 74 | 750497 | -1010228.2
6 | 14 | 19 | 3 | 18.1256 | 0 | 62.7906 | 0 | 10.599 | 0 | 10.3284 | 8.818 | 0 | 0 | 0 | 1.2 | 111.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.7 | 0 | 18003.7 | 193007 | 0 | 63 | 72 | 193007 | -1000000
6 | 14 | 20 | 3 | 17.6278 | 0 | 54.6418 | 0 | 8.138 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 4 | 98.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197.8 | 0 | 17197.8 | 173072 | 0 | 63 | 69 | 173072 | -1000000
6 | 14 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.3556 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10723.8 | 0 | 10723.8 | 159539 | 0 | 62 | 66 | 159539 | -1000000
6 | 14 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.0136 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10463.4 | 0 | 10463.4 | 148383 | 0 | 61 | 64 | 148383 | -1000000
6 | 14 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.7083 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 5.6 | 79.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.57 | 0 | 9104.57 | 143520 | 0 | 61 | 62 | 143520 | -1000000
6 | 14 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 8.0605 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.54 | 0 | 9104.54 | 141945 | 0 | 62 | 65 | 141945 | -1000000
6 | 15 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.0299 | 0 | 5.4889 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.59 | 0 | 9104.59 | 140819 | 0 | 60 | 61 | 140819 | -1000000
6 | 15 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0213 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.81 | 0 | 9104.81 | 139951 | 0 | 60 | 61 | 139951 | -1000000
6 | 15 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.6791 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.84 | 0 | 9104.84 | 138880 | 0 | 58 | 59 | 138880 | -1000000
6 | 15 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.6893 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 3.2 | 81.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10106.5 | 0 | 10106.5 | 142449 | 0 | 61 | 62 | 142449 | -1000000
6 | 15 | 5 | 4 | 24.0887 | 0 | 69.9783 | 0 | 12.0584 | 0 | 5.5759 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12335.8 | 0 | 12335.8 | 250074 | 0 | 61 | 62 | 250074 | -1000000
6 | 15 | 6 | 4 | 42.9767 | 0 | 140.608 | 0 | 41.0464 | 0 | 6.332 | 20.2978 | 0 | 0 | 0 | 0 | 251.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33335.3 | 0 | 33335.3 | 756134 | -9316.56 | 60 | 62 | 756134 | -1009316.56
6 | 15 | 7 | 4 | 39.7044 | 0 | 168.222 | 0 | 45.7079 | 0 | 6.9752 | 20.4366 | 0 | 0 | 0 | 0 | 281.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36562.2 | 0 | 36562.2 | 849137 | -21681.8 | 60 | 62 | 849137 | -1021681.8
6 | 15 | 8 | 4 | 39.9347 | 0 | 173.795 | 0 | 47.1059 | 0 | 25.335 | 20.7873 | 0 | 0 | 0 | 0 | 306.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46269.4 | 0 | 46269.4 | 870177 | -21439.8 | 60 | 63 | 870177 | -1021439.8
6 | 15 | 9 | 4 | 41.0791 | 0 | 172.186 | 0 | 51.5316 | 0 | 25.335 | 21.3272 | 0 | 0 | 0 | 0 | 311.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116.9 | 0 | 72116.9 | 929289 | -21612 | 61 | 65 | 929289 | -1021612
6 | 15 | 10 | 4 | 41.6546 | 0 | 163.102 | 0 | 54.112 | 0 | 25.335 | 21.3156 | 0 | 0 | 0 | 0 | 305.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733 | 0 | 73733 | 967983 | -18459.1 | 62 | 67 | 967983 | -1018459.1
6 | 15 | 11 | 4 | 40.9107 | 0 | 149.692 | 0 | 51.3118 | 0 | 25.335 | 21.5247 | 0 | 0 | 0 | 0 | 288.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.3 | 0 | 73733.3 | 917104 | -14650.2 | 63 | 68 | 917104 | -1014650.2
6 | 15 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 58.7761 | 0 | 25.335 | 22.6435 | 0 | 0 | 0 | 0 | 296.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.6 | 0 | 73733.6 | 1000560 | -12474.8 | 64 | 72 | 1000560 | -1012474.8
6 | 15 | 13 | 4 | 41.233 | 0 | 165.698 | 0 | 68.8261 | 0 | 25.335 | 23.1746 | 0 | 0 | 0 | 0 | 324.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.2 | 0 | 73734.2 | 1163950 | -15138.4 | 65 | 74 | 1163950 | -1015138.4
6 | 15 | 14 | 4 | 40.6158 | 0 | 172.702 | 0 | 75.0989 | 0 | 25.335 | 22.9078 | 0 | 0 | 0 | 0 | 336.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.1 | 0 | 72119.1 | 1259510 | -18434.1 | 66 | 76 | 1259510 | -1018434.1
6 | 15 | 15 | 4 | 40.506 | 0 | 173.986 | 0 | 79.808 | 0 | 25.335 | 23.0961 | 0 | 0 | 0 | 0 | 342.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.6 | 0 | 65657.6 | 1342860 | -19519.8 | 67 | 78 | 1342860 | -1019519.8
6 | 15 | 16 | 4 | 40.2607 | 0 | 169.782 | 0 | 79.5192 | 0 | 25.335 | 23.2499 | 0 | 0 | 0 | 0 | 338.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349.9 | 0 | 54349.9 | 1350820 | -18331.2 | 67 | 78 | 1350820 | -1018331.2
6 | 15 | 17 | 4 | 35.4556 | 0 | 152.497 | 0 | 71.6437 | 0 | 25.335 | 23.1286 | 0 | 0 | 0 | 0 | 308.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.7 | 0 | 41426.7 | 1240200 | -14743.7 | 67 | 76 | 1240200 | -1014743.7
6 | 15 | 18 | 4 | 24.6185 | 0 | 93.4203 | 0 | 46.2984 | 0 | 25.335 | 20.9423 | 0 | 0 | 0 | 0 | 210.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.9 | 0 | 25272.9 | 833075 | -11607 | 66 | 73 | 833075 | -1011607
6 | 15 | 19 | 4 | 18.1467 | 0 | 62.7906 | 0 | 10.8382 | 0 | 10.3937 | 8.818 | 0 | 0 | 0 | 1.2 | 112.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.7 | 0 | 18003.7 | 193359 | 0 | 64 | 71 | 193359 | -1000000
6 | 15 | 20 | 4 | 17.4541 | 0 | 54.6418 | 0 | 8.7692 | 0 | 5.4917 | 8.818 | 0 | 0 | 0 | 4 | 99.1748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17197.5 | 0 | 17197.5 | 173932 | 0 | 65 | 70 | 173932 | -1000000
6 | 15 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 8.0569 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 7.2 | 92.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10723.1 | 0 | 10723.1 | 160257 | 0 | 65 | 69 | 160257 | -1000000
6 | 15 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 8.112 | 0 | 5.4831 | 8.818 | 0 | 0 | 0 | 6.4 | 84.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10462.6 | 0 | 10462.6 | 149233 | 0 | 66 | 70 | 149233 | -1000000
6 | 15 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 8.2369 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 5.6 | 80.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.6 | 0 | 9103.6 | 144293 | 0 | 67 | 72 | 144293 | -1000000
6 | 15 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.9343 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.25 | 0 | 9103.25 | 142799 | 0 | 68 | 73 | 142799 | -1000000
6 | 16 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.9358 | 0 | 5.4831 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.82 | 0 | 9102.82 | 141861 | 0 | 68 | 74 | 141861 | -1000000
6 | 16 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.6167 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.26 | 0 | 9102.26 | 141027 | 0 | 68 | 74 | 141027 | -1000000
6 | 16 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.5574 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.58 | 0 | 9101.58 | 139822 | 0 | 65 | 74 | 139822 | -1000000
6 | 16 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.3737 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 3.2 | 81.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10102.3 | 0 | 10102.3 | 142701 | 0 | 60 | 73 | 142701 | -1000000
6 | 16 | 5 | 5 | 23.3999 | 0 | 69.9783 | 0 | 13.4784 | 0 | 5.6908 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12330.7 | 0 | 12330.7 | 270655 | 0 | 58 | 72 | 270655 | -1000000
6 | 16 | 6 | 5 | 37.6844 | 0 | 140.608 | 0 | 48.8823 | 0 | 7.5364 | 22.4982 | 0 | 0 | 0 | 0 | 257.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33329.1 | 0 | 33329.1 | 989205 | -4428.8 | 60 | 70 | 989205 | -1004428.8
6 | 16 | 7 | 5 | 38.8485 | 0 | 168.222 | 0 | 57.9191 | 0 | 6.332 | 22.8434 | 0 | 0 | 0 | 0 | 294.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36555.4 | 0 | 36555.4 | 1108160 | -19443.3 | 62 | 69 | 1108160 | -1019443.3
6 | 16 | 8 | 5 | 39.6916 | 0 | 173.795 | 0 | 59.6487 | 0 | 23.9306 | 22.5086 | 0 | 0 | 0 | 0 | 319.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46267.3 | 0 | 46267.3 | 1116780 | -20787.4 | 63 | 70 | 1116780 | -1020787.4
6 | 16 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 61.2885 | 0 | 25.335 | 21.7891 | 0 | 0 | 0 | 0 | 321.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115.4 | 0 | 72115.4 | 1082210 | -21561 | 61 | 71 | 1082210 | -1021561
6 | 16 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 57.7836 | 0 | 25.335 | 22.0386 | 0 | 0 | 0 | 0 | 309.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732 | 0 | 73732 | 1014840 | -18681.4 | 59 | 72 | 1014840 | -1018681.4
6 | 16 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 52.217 | 0 | 25.335 | 22.5414 | 0 | 0 | 0 | 0 | 290.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.5 | 0 | 73734.5 | 921123 | -15080 | 59 | 72 | 921123 | -1015080
6 | 16 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 54.1144 | 0 | 25.335 | 22.9346 | 0 | 0 | 0 | 0 | 292.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.7 | 0 | 73734.7 | 937110 | -13995.5 | 59 | 73 | 937110 | -1013995.5
6 | 16 | 13 | 5 | 41.2603 | 0 | 165.698 | 0 | 62.0742 | 0 | 25.335 | 23.1235 | 0 | 0 | 0 | 0 | 317.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.5 | 0 | 73734.5 | 1054510 | -17339.2 | 60 | 75 | 1054510 | -1017339.2
6 | 16 | 14 | 5 | 40.6774 | 0 | 172.702 | 0 | 63.853 | 0 | 25.335 | 22.7522 | 0 | 0 | 0 | 0 | 325.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.2 | 0 | 72119.2 | 1097330 | -20734.4 | 60 | 75 | 1097330 | -1020734.4
6 | 16 | 15 | 5 | 40.573 | 0 | 173.986 | 0 | 61.7947 | 0 | 25.335 | 22.8815 | 0 | 0 | 0 | 0 | 324.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.7 | 0 | 65657.7 | 1068190 | -22152.1 | 58 | 76 | 1068190 | -1022152.1
6 | 16 | 16 | 5 | 40.3002 | 0 | 169.782 | 0 | 62.0735 | 0 | 25.335 | 23.0597 | 0 | 0 | 0 | 0 | 320.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349.7 | 0 | 54349.7 | 1093170 | -21264.6 | 59 | 76 | 1093170 | -1021264.6
6 | 16 | 17 | 5 | 35.4768 | 0 | 152.497 | 0 | 54.5662 | 0 | 25.335 | 22.6356 | 0 | 0 | 0 | 0 | 290.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.1 | 0 | 41426.1 | 970703 | -26074.8 | 57 | 75 | 970703 | -1026074.8
6 | 16 | 18 | 5 | 24.5841 | 0 | 93.4203 | 0 | 37.663 | 0 | 6.332 | 20.3452 | 0 | 0 | 0 | 0 | 182.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.1 | 0 | 25272.1 | 709643 | -29942.2 | 55 | 73 | 709643 | -1029942.2
6 | 16 | 19 | 5 | 19.0673 | 0 | 62.7906 | 0 | 9.9268 | 0 | 5.5189 | 8.818 | 0 | 0 | 0 | 1.2 | 107.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18002.9 | 0 | 18002.9 | 194042 | 0 | 54 | 71 | 194042 | -1000000
6 | 16 | 20 | 5 | 17.3608 | 0 | 54.6418 | 0 | 7.2109 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4 | 97.5102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196.9 | 0 | 17196.9 | 174068 | 0 | 53 | 65 | 174068 | -1000000
6 | 16 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.2392 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 91.4563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10722.5 | 0 | 10722.5 | 160487 | 0 | 53 | 62 | 160487 | -1000000
6 | 16 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 6.9007 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10461.9 | 0 | 10461.9 | 149172 | 0 | 52 | 58 | 149172 | -1000000
6 | 16 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1749 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.21 | 0 | 9103.21 | 144050 | 0 | 51 | 56 | 144050 | -1000000
6 | 16 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0922 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.4 | 0 | 9103.4 | 142295 | 0 | 52 | 56 | 142295 | -1000000
6 | 17 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0255 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.77 | 0 | 9103.77 | 140839 | 0 | 50 | 55 | 140839 | -1000000
6 | 17 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9873 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.93 | 0 | 9104.93 | 140016 | 0 | 49 | 52 | 140016 | -1000000
6 | 17 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9432 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9105.25 | 0 | 9105.25 | 139046 | 0 | 49 | 51 | 139046 | -1000000
6 | 17 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8954 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 3.2 | 73.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9105.78 | 0 | 9105.78 | 138000 | 0 | 48 | 50 | 138000 | -1000000
6 | 17 | 5 | 6 | 6.1959 | 0 | 42.7453 | 0 | 6.8535 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 1.6 | 71.6936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.84 | 0 | 9106.84 | 137085 | 0 | 47 | 50 | 137085 | -1000000
6 | 17 | 6 | 6 | 4.8288 | 0 | 42.7453 | 0 | 6.8335 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 0 | 68.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.26 | 0 | 9107.26 | 136654 | 0 | 50 | 54 | 136654 | -1000000
6 | 17 | 7 | 6 | 4.5915 | 0 | 42.7453 | 0 | 15.2089 | 0 | 6.0032 | 18.8896 | 0 | 0 | 0 | 0 | 87.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.88 | 0 | 9107.88 | 223587 | -12733.6 | 51 | 58 | 223587 | -1012733.6
6 | 17 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 16.8041 | 0 | 6.074 | 18.8896 | 0 | 0 | 0 | 0 | 89.4441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.22 | 0 | 9108.22 | 240874 | -13492.3 | 54 | 61 | 240874 | -1013492.3
6 | 17 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.3878 | 0 | 17.7673 | 18.8896 | 0 | 0 | 0 | 0 | 100.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9119.9 | 0 | 9119.9 | 266805 | -16971.9 | 55 | 64 | 266805 | -1016971.9
6 | 17 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 18.359 | 0 | 25.335 | 18.8896 | 0 | 0 | 0 | 0 | 110.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9121.28 | 0 | 9121.28 | 310780 | -17916.1 | 56 | 68 | 310780 | -1017916.1
6 | 17 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 20.2351 | 0 | 25.335 | 18.959 | 0 | 0 | 0 | 0 | 112.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9122.89 | 0 | 9122.89 | 342689 | -17405.4 | 57 | 71 | 342689 | -1017405.4
6 | 17 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 21.8499 | 0 | 25.335 | 19.0272 | 0 | 0 | 0 | 0 | 114.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9123.68 | 0 | 9123.68 | 370319 | -17293 | 58 | 73 | 370319 | -1017293
6 | 17 | 13 | 6 | 5.4694 | 0 | 42.7453 | 0 | 23.9201 | 0 | 25.335 | 19.1866 | 0 | 0 | 0 | 0 | 116.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9124.03 | 0 | 9124.03 | 399942 | -16884 | 58 | 75 | 399942 | -1016884
6 | 17 | 14 | 6 | 5.4721 | 0 | 42.7453 | 0 | 11.5482 | 0 | 11.3366 | 12.8287 | 0 | 0 | 0 | 0 | 83.9308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9124.56 | 0 | 9124.56 | 188100 | 0 | 59 | 75 | 188100 | -1000000
6 | 17 | 15 | 6 | 5.4721 | 0 | 42.7453 | 0 | 11.3062 | 0 | 11.0804 | 12.8287 | 0 | 0 | 0 | 0 | 83.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9125.07 | 0 | 9125.07 | 189487 | 0 | 61 | 77 | 189487 | -1000000
6 | 17 | 16 | 6 | 5.4717 | 0 | 42.7453 | 0 | 8.0159 | 0 | 7.5046 | 8.818 | 0 | 0 | 0 | 0 | 72.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9118.97 | 0 | 9118.97 | 132005 | 0 | 61 | 77 | 132005 | -1000000
6 | 17 | 17 | 6 | 5.4724 | 0 | 42.7453 | 0 | 10.1988 | 0 | 9.8326 | 10.866 | 0 | 0 | 0 | 0 | 79.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9115.75 | 0 | 9115.75 | 176260 | 0 | 62 | 78 | 176260 | -1000000
6 | 17 | 18 | 6 | 5.4746 | 0 | 42.7453 | 0 | 7.6402 | 0 | 7.376 | 8.818 | 0 | 0 | 0 | 0 | 72.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9113.36 | 0 | 9113.36 | 131631 | 0 | 61 | 77 | 131631 | -1000000
6 | 17 | 19 | 6 | 6.8345 | 0 | 42.7453 | 0 | 6.5559 | 0 | 5.5219 | 8.818 | 0 | 0 | 0 | 1.2 | 71.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.34 | 0 | 9111.34 | 131638 | 0 | 61 | 73 | 131638 | -1000000
6 | 17 | 20 | 6 | 8.5615 | 0 | 42.7453 | 0 | 6.4647 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4 | 76.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9109.79 | 0 | 9109.79 | 131364 | 0 | 61 | 71 | 131364 | -1000000
6 | 17 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.6947 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 7.2 | 79.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9108.51 | 0 | 9108.51 | 131304 | 0 | 62 | 70 | 131304 | -1000000
6 | 17 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3276 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 6.4 | 78.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.67 | 0 | 9107.67 | 130846 | 0 | 61 | 68 | 130846 | -1000000
6 | 17 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.1527 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 78.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9107.12 | 0 | 9107.12 | 130419 | 0 | 60 | 69 | 130419 | -1000000
6 | 17 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.5655 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 73.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.87 | 0 | 3452.87 | 130218 | 0 | 60 | 68 | 130218 | -1000000
6 | 18 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2147 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.59 | 0 | 3452.59 | 129976 | 0 | 60 | 66 | 129976 | -1000000
6 | 18 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.1318 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 4.8 | 73.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.42 | 0 | 3452.42 | 129676 | 0 | 60 | 64 | 129676 | -1000000
6 | 18 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.0445 | 0 | 5.4883 | 8.818 | 0 | 0 | 0 | 4.8 | 73.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.27 | 0 | 3452.27 | 129219 | 0 | 59 | 62 | 129219 | -1000000
6 | 18 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 5.9642 | 0 | 5.4903 | 8.818 | 0 | 0 | 0 | 3.2 | 71.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.3 | 0 | 3452.3 | 128860 | 0 | 58 | 60 | 128860 | -1000000
6 | 18 | 5 | 7 | 5.0253 | 0 | 42.7453 | 0 | 6.4642 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 1.6 | 70.1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.13 | 0 | 3452.13 | 128575 | 0 | 58 | 60 | 128575 | -1000000
6 | 18 | 6 | 7 | 4.7675 | 0 | 42.7453 | 0 | 6.7484 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 0 | 68.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.14 | 0 | 3452.14 | 128407 | 0 | 59 | 61 | 128407 | -1000000
6 | 18 | 7 | 7 | 4.5432 | 0 | 42.7453 | 0 | 7.0782 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 0 | 68.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.57 | 0 | 3452.57 | 128327 | 0 | 61 | 63 | 128327 | -1000000
6 | 18 | 8 | 7 | 4.1273 | 0 | 42.7453 | 0 | 6.5476 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 0 | 67.7206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.9 | 0 | 3452.9 | 128126 | 0 | 62 | 63 | 128126 | -1000000
6 | 18 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.1347 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453.17 | 0 | 3453.17 | 127857 | 0 | 63 | 65 | 127857 | -1000000
6 | 18 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.1374 | 0 | 5.5015 | 8.818 | 0 | 0 | 0 | 0 | 70.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3453.04 | 0 | 3453.04 | 127987 | 0 | 67 | 73 | 127987 | -1000000
6 | 18 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.065 | 0 | 5.6023 | 12.8287 | 0 | 0 | 0 | 0 | 75.3853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.78 | 0 | 3452.78 | 178913 | 0 | 67 | 76 | 178913 | -1000000
6 | 18 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.493 | 0 | 10.7192 | 12.8287 | 0 | 0 | 0 | 0 | 80.9301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451.6 | 0 | 3451.6 | 191772 | 0 | 69 | 78 | 191772 | -1000000
6 | 18 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.1808 | 0 | 11.6543 | 12.8287 | 0 | 0 | 0 | 0 | 82.5531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449.67 | 0 | 3449.67 | 202172 | 0 | 71 | 81 | 202172 | -1000000
6 | 18 | 14 | 7 | 4.1456 | 0 | 42.7453 | 0 | 11.4574 | 0 | 11.8993 | 12.8287 | 0 | 0 | 0 | 0 | 83.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.08 | 0 | 3448.08 | 203351 | 0 | 71 | 81 | 203351 | -1000000
6 | 18 | 15 | 7 | 4.1469 | 0 | 42.7453 | 0 | 13.9009 | 0 | 18.0351 | 14.8767 | 0 | 0 | 0 | 0 | 93.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3446.21 | 0 | 3446.21 | 264038 | 0 | 72 | 84 | 264038 | -1000000
6 | 18 | 16 | 7 | 4.1464 | 0 | 42.7453 | 0 | 14.257 | 0 | 6.6767 | 14.8767 | 0 | 0 | 0 | 0 | 82.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3444.32 | 0 | 3444.32 | 273741 | 0 | 74 | 86 | 273741 | -1000000
6 | 18 | 17 | 7 | 4.147 | 0 | 42.7453 | 0 | 14.326 | 0 | 5.769 | 14.8767 | 0 | 0 | 0 | 0 | 81.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3442.84 | 0 | 3442.84 | 274988 | 0 | 75 | 86 | 274988 | -1000000
6 | 18 | 18 | 7 | 4.1478 | 0 | 42.7453 | 0 | 14.2808 | 0 | 5.7654 | 14.8767 | 0 | 0 | 0 | 0 | 81.8159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3441.02 | 0 | 3441.02 | 274042 | 0 | 75 | 85 | 274042 | -1000000
6 | 18 | 19 | 7 | 5.0452 | 0 | 42.7453 | 0 | 11.3721 | 0 | 5.5826 | 12.8287 | 0 | 0 | 0 | 1.2 | 78.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439.38 | 0 | 3439.38 | 214577 | 0 | 75 | 84 | 214577 | -1000000
6 | 18 | 20 | 7 | 6.2157 | 0 | 42.7453 | 0 | 7.1053 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4 | 74.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3438.03 | 0 | 3438.03 | 128390 | 0 | 75 | 80 | 128390 | -1000000
6 | 18 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0354 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 77.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.8 | 0 | 3436.8 | 128424 | 0 | 74 | 79 | 128424 | -1000000
6 | 18 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0391 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 77.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3435.7 | 0 | 3435.7 | 128497 | 0 | 74 | 78 | 128497 | -1000000
6 | 18 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0287 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 76.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.58 | 0 | 3434.58 | 128285 | 0 | 72 | 76 | 128285 | -1000000
6 | 18 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 7.0432 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9087.27 | 0 | 9087.27 | 128585 | 0 | 72 | 76 | 128585 | -1000000
6 | 19 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.0373 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9086.42 | 0 | 9086.42 | 128460 | 0 | 71 | 76 | 128460 | -1000000
6 | 19 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.0339 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9084.88 | 0 | 9084.88 | 128392 | 0 | 71 | 77 | 128392 | -1000000
6 | 19 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.03 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9083.79 | 0 | 9083.79 | 128313 | 0 | 71 | 77 | 128313 | -1000000
6 | 19 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 7.2384 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 3.2 | 81.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10084.2 | 0 | 10084.2 | 132570 | 0 | 71 | 77 | 132570 | -1000000
6 | 19 | 5 | 1 | 23.8095 | 0 | 69.9783 | 0 | 15.0466 | 0 | 5.8286 | 12.8287 | 0 | 0 | 0 | 1.6 | 129.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12312.3 | 0 | 12312.3 | 292122 | 0 | 71 | 77 | 292122 | -1000000
6 | 19 | 6 | 1 | 38.0101 | 0 | 140.608 | 0 | 90.7582 | 0 | 6.332 | 23.765 | 0 | 0 | 0 | 0 | 299.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33310.4 | 0 | 33310.4 | 1677950 | -3716.32 | 71 | 77 | 1677950 | -1003716.32
6 | 19 | 7 | 1 | 38.9409 | 0 | 168.222 | 0 | 96.9594 | 0 | 6.332 | 23.3037 | 0 | 0 | 0 | 0 | 333.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36536.3 | 0 | 36536.3 | 1680600 | -27947.9 | 71 | 79 | 1680600 | -1027947.9
6 | 19 | 8 | 1 | 39.6631 | 0 | 173.795 | 0 | 95.9852 | 0 | 6.332 | 22.8079 | 0 | 0 | 0 | 0 | 338.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46258 | 0 | 46258 | 1675220 | -19511.4 | 73 | 84 | 1675220 | -1019511.4
6 | 19 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 97.0667 | 0 | 6.332 | 23.2618 | 0 | 0 | 0 | 0 | 339.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72108.3 | 0 | 72108.3 | 1729020 | -16787 | 74 | 86 | 1729020 | -1016787
6 | 19 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 106.923 | 0 | 6.332 | 22.9748 | 0 | 0 | 0 | 0 | 340.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73726.5 | 0 | 73726.5 | 1733930 | -26965.1 | 73 | 89 | 1733930 | -1026965.1
6 | 19 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 106.293 | 0 | 6.332 | 22.5773 | 0 | 0 | 0 | 0 | 325.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73727.8 | 0 | 73727.8 | 1630640 | -34532.1 | 74 | 88 | 1630640 | -1034532.1
6 | 19 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 108.899 | 0 | 6.332 | 22.7862 | 0 | 0 | 0 | 0 | 327.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73728.7 | 0 | 73728.7 | 1642590 | -34965.4 | 73 | 89 | 1642590 | -1034965.4
6 | 19 | 13 | 1 | 41.2469 | 0 | 165.698 | 0 | 120.89 | 0 | 6.332 | 23.3124 | 0 | 0 | 0 | 0 | 357.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729 | 0 | 73729 | 1838300 | -31925.2 | 75 | 93 | 1838300 | -1031925.2
6 | 19 | 14 | 1 | 40.6711 | 0 | 172.702 | 0 | 113.727 | 0 | 6.332 | 23.196 | 0 | 0 | 0 | 0 | 356.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72114 | 0 | 72114 | 1749580 | -32011.6 | 73 | 93 | 1749580 | -1032011.6
6 | 19 | 15 | 1 | 40.55 | 0 | 173.986 | 0 | 117.796 | 0 | 6.332 | 23.4657 | 0 | 0 | 0 | 0 | 362.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65652.9 | 0 | 65652.9 | 1804560 | -32181.6 | 73 | 93 | 1804560 | -1032181.6
6 | 19 | 16 | 1 | 40.2844 | 0 | 169.782 | 0 | 119.689 | 0 | 6.332 | 23.8343 | 0 | 0 | 0 | 0 | 359.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54345 | 0 | 54345 | 1817380 | -31754.7 | 73 | 93 | 1817380 | -1031754.7
6 | 19 | 17 | 1 | 35.4614 | 0 | 152.497 | 0 | 122.571 | 0 | 6.332 | 23.3992 | 0 | 0 | 0 | 0 | 340.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41422 | 0 | 41422 | 1790470 | -34686 | 74 | 92 | 1790470 | -1034686
6 | 19 | 18 | 1 | 24.5865 | 0 | 93.4203 | 0 | 100.555 | 0 | 6.332 | 21.5612 | 0 | 0 | 0 | 0 | 246.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25268.5 | 0 | 25268.5 | 1360970 | -46147.6 | 74 | 91 | 1360970 | -1046147.6
6 | 19 | 19 | 1 | 17.8383 | 0 | 62.7906 | 0 | 11.1514 | 0 | 5.5725 | 8.818 | 0 | 0 | 0 | 1.2 | 107.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17999.8 | 0 | 17999.8 | 191641 | 0 | 73 | 89 | 191641 | -1000000
6 | 19 | 20 | 1 | 17.5136 | 0 | 54.6418 | 0 | 9.1849 | 0 | 5.5049 | 8.818 | 0 | 0 | 0 | 4 | 99.6632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17192.8 | 0 | 17192.8 | 171268 | 0 | 74 | 84 | 171268 | -1000000
6 | 19 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 8.5334 | 0 | 5.4917 | 8.818 | 0 | 0 | 0 | 7.2 | 92.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10715.4 | 0 | 10715.4 | 158300 | 0 | 74 | 81 | 158300 | -1000000
6 | 19 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.9937 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 6.4 | 84.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10452.4 | 0 | 10452.4 | 147494 | 0 | 73 | 79 | 147494 | -1000000
6 | 19 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.7448 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 5.6 | 80.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9091.88 | 0 | 9091.88 | 142592 | 0 | 73 | 78 | 142592 | -1000000
6 | 19 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.6682 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9090.14 | 0 | 9090.14 | 141110 | 0 | 72 | 77 | 141110 | -1000000
6 | 20 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.6303 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9088.73 | 0 | 9088.73 | 140360 | 0 | 72 | 76 | 140360 | -1000000
6 | 20 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.5899 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9087.53 | 0 | 9087.53 | 139549 | 0 | 71 | 76 | 139549 | -1000000
6 | 20 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.2239 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9086.41 | 0 | 9086.41 | 138702 | 0 | 69 | 74 | 138702 | -1000000
6 | 20 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 10.8981 | 0 | 5.5541 | 12.8287 | 0 | 0 | 0 | 3.2 | 89.1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10086.9 | 0 | 10086.9 | 222703 | 0 | 68 | 72 | 222703 | -1000000
6 | 20 | 5 | 2 | 23.4954 | 0 | 69.9783 | 0 | 14.0849 | 0 | 5.722 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12315 | 0 | 12315 | 291146 | 0 | 65 | 70 | 291146 | -1000000
6 | 20 | 6 | 2 | 37.9505 | 0 | 140.608 | 0 | 61.2256 | 0 | 5.9138 | 23.2111 | 0 | 0 | 0 | 0 | 268.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33313.4 | 0 | 33313.4 | 1261260 | 0 | 62 | 68 | 1261260 | -1000000
6 | 20 | 7 | 2 | 39.0538 | 0 | 168.222 | 0 | 59.0658 | 0 | 6.332 | 23.0146 | 0 | 0 | 0 | 0 | 295.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36539.7 | 0 | 36539.7 | 1177100 | -18903.6 | 60 | 69 | 1177100 | -1018903.6
6 | 20 | 8 | 2 | 39.7279 | 0 | 173.795 | 0 | 64.4245 | 0 | 25.335 | 22.1828 | 0 | 0 | 0 | 0 | 325.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46260 | 0 | 46260 | 1203650 | -19118.8 | 62 | 72 | 1203650 | -1019118.8
6 | 20 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 75.0808 | 0 | 25.335 | 22.3808 | 0 | 0 | 0 | 0 | 335.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72110.7 | 0 | 72110.7 | 1272000 | -19624.3 | 64 | 75 | 1272000 | -1019624.3
6 | 20 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 78.0851 | 0 | 25.335 | 22.7909 | 0 | 0 | 0 | 0 | 330.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73728.5 | 0 | 73728.5 | 1344340 | -16426.1 | 66 | 77 | 1344340 | -1016426.1
6 | 20 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 75.528 | 0 | 25.335 | 23.5104 | 0 | 0 | 0 | 0 | 314.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729.8 | 0 | 73729.8 | 1292360 | -11726.5 | 68 | 81 | 1292360 | -1011726.5
6 | 20 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 82.1908 | 0 | 25.335 | 23.1684 | 0 | 0 | 0 | 0 | 320.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.4 | 0 | 73730.4 | 1395810 | -22647.7 | 69 | 83 | 1395810 | -1022647.7
6 | 20 | 13 | 2 | 41.2565 | 0 | 165.698 | 0 | 91.6266 | 0 | 25.335 | 23.3961 | 0 | 0 | 0 | 0 | 347.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.6 | 0 | 73730.6 | 1546470 | -25419.3 | 70 | 84 | 1546470 | -1025419.3
6 | 20 | 14 | 2 | 40.6631 | 0 | 172.702 | 0 | 99.1893 | 0 | 25.335 | 23.1318 | 0 | 0 | 0 | 0 | 361.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115.3 | 0 | 72115.3 | 1661800 | -28687.1 | 72 | 86 | 1661800 | -1028687.1
6 | 20 | 15 | 2 | 40.5449 | 0 | 173.986 | 0 | 108.515 | 0 | 25.335 | 23.1176 | 0 | 0 | 0 | 0 | 371.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65654 | 0 | 65654 | 1720850 | -34633.6 | 72 | 87 | 1720850 | -1034633.6
6 | 20 | 16 | 2 | 40.2872 | 0 | 169.782 | 0 | 114.031 | 0 | 25.335 | 23.4215 | 0 | 0 | 0 | 0 | 372.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54346.2 | 0 | 54346.2 | 1778900 | -34304.3 | 73 | 88 | 1778900 | -1034304.3
6 | 20 | 17 | 2 | 35.4691 | 0 | 152.497 | 0 | 116.443 | 0 | 8.0457 | 23.0748 | 0 | 0 | 0 | 0 | 335.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41423 | 0 | 41423 | 1750720 | -37276.1 | 74 | 87 | 1750720 | -1037276.1
6 | 20 | 18 | 2 | 24.5807 | 0 | 93.4203 | 0 | 95.4254 | 0 | 6.332 | 21.4534 | 0 | 0 | 0 | 0 | 241.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25269.4 | 0 | 25269.4 | 1331270 | -49134.7 | 74 | 85 | 1331270 | -1049134.7
6 | 20 | 19 | 2 | 20.0745 | 0 | 62.7906 | 0 | 12.2559 | 0 | 13.0935 | 8.818 | 0 | 0 | 0 | 1.2 | 118.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000.6 | 0 | 18000.6 | 195650 | 0 | 73 | 83 | 195650 | -1000000
6 | 20 | 20 | 2 | 18.3703 | 0 | 54.6418 | 0 | 9.3669 | 0 | 5.5094 | 8.818 | 0 | 0 | 0 | 4 | 100.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17193.5 | 0 | 17193.5 | 174921 | 0 | 73 | 82 | 174921 | -1000000
6 | 20 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.705 | 0 | 5.4947 | 8.818 | 0 | 0 | 0 | 7.2 | 92.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10717.1 | 0 | 10717.1 | 161746 | 0 | 73 | 81 | 161746 | -1000000
6 | 20 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 8.1559 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 6.4 | 84.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10454.6 | 0 | 10454.6 | 150748 | 0 | 72 | 79 | 150748 | -1000000
6 | 20 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.8992 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 5.6 | 80.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.39 | 0 | 9094.39 | 145690 | 0 | 72 | 79 | 145690 | -1000000
6 | 20 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.82 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 80.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9092.74 | 0 | 9092.74 | 144158 | 0 | 72 | 79 | 144158 | -1000000
6 | 21 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.7695 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 80.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9091.39 | 0 | 9091.39 | 143153 | 0 | 71 | 78 | 143153 | -1000000
6 | 21 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.7232 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 80.0022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9090.11 | 0 | 9090.11 | 142224 | 0 | 70 | 78 | 142224 | -1000000
6 | 21 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.6803 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9088.85 | 0 | 9088.85 | 141363 | 0 | 69 | 77 | 141363 | -1000000
6 | 21 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.8424 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 3.2 | 81.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10089.1 | 0 | 10089.1 | 144690 | 0 | 68 | 76 | 144690 | -1000000
6 | 21 | 5 | 3 | 24.0905 | 0 | 69.9783 | 0 | 14.3755 | 0 | 5.7486 | 12.8287 | 0 | 0 | 0 | 1.6 | 128.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12317.1 | 0 | 12317.1 | 308239 | 0 | 69 | 71 | 308239 | -1000000
6 | 21 | 6 | 3 | 46.1978 | 0 | 140.608 | 0 | 78.1387 | 0 | 5.9138 | 23.9907 | 0 | 0 | 0 | 0 | 294.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33315.3 | 0 | 33315.3 | 1554460 | 0 | 69 | 71 | 1554460 | -1000000
6 | 21 | 7 | 3 | 43.8842 | 0 | 168.222 | 0 | 79.1602 | 0 | 6.332 | 23.8398 | 0 | 0 | 0 | 0 | 321.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36541.2 | 0 | 36541.2 | 1552800 | -22182.4 | 70 | 71 | 1552800 | -1022182.4
6 | 21 | 8 | 3 | 40.4906 | 0 | 173.795 | 0 | 73.8961 | 0 | 25.335 | 23.2752 | 0 | 0 | 0 | 0 | 336.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46260.6 | 0 | 46260.6 | 1443980 | -22657.2 | 70 | 71 | 1443980 | -1022657.2
6 | 21 | 9 | 3 | 41.4679 | 0 | 172.186 | 0 | 81.5804 | 0 | 25.335 | 23.5981 | 0 | 0 | 0 | 0 | 344.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72110.1 | 0 | 72110.1 | 1436280 | -23188.2 | 70 | 72 | 1436280 | -1023188.2
6 | 21 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 89.3069 | 0 | 25.335 | 23.2084 | 0 | 0 | 0 | 0 | 342.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73726.4 | 0 | 73726.4 | 1504300 | -19797.5 | 71 | 75 | 1504300 | -1019797.5
6 | 21 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 86.0212 | 0 | 25.335 | 23.4449 | 0 | 0 | 0 | 0 | 325.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73727 | 0 | 73727 | 1459590 | -14741.1 | 73 | 80 | 1459590 | -1014741.1
6 | 21 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 91.3434 | 0 | 25.335 | 23.4813 | 0 | 0 | 0 | 0 | 330.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729 | 0 | 73729 | 1527040 | -17981.3 | 73 | 82 | 1527040 | -1017981.3
6 | 21 | 13 | 3 | 41.259 | 0 | 165.698 | 0 | 104.344 | 0 | 25.335 | 23.7579 | 0 | 0 | 0 | 0 | 360.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.3 | 0 | 73730.3 | 1747180 | -25313.8 | 75 | 85 | 1747180 | -1025313.8
6 | 21 | 14 | 3 | 40.6597 | 0 | 172.702 | 0 | 102.634 | 0 | 25.335 | 23.4096 | 0 | 0 | 0 | 0 | 364.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115.2 | 0 | 72115.2 | 1709640 | -31481 | 74 | 83 | 1709640 | -1031481
6 | 21 | 15 | 3 | 40.8576 | 0 | 173.986 | 0 | 107.315 | 0 | 25.335 | 23.8277 | 0 | 0 | 0 | 0 | 371.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65653.7 | 0 | 65653.7 | 1764020 | -34959.6 | 75 | 81 | 1764020 | -1034959.6
6 | 21 | 16 | 3 | 40.4855 | 0 | 169.782 | 0 | 103.211 | 0 | 25.335 | 24.0918 | 0 | 0 | 0 | 0 | 362.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54345.9 | 0 | 54345.9 | 1750840 | -25249.9 | 75 | 81 | 1750840 | -1025249.9
6 | 21 | 17 | 3 | 35.4777 | 0 | 152.497 | 0 | 96.5573 | 0 | 25.335 | 23.5912 | 0 | 0 | 0 | 0 | 333.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41422.2 | 0 | 41422.2 | 1672150 | -22792.3 | 75 | 80 | 1672150 | -1022792.3
6 | 21 | 18 | 3 | 25.0999 | 0 | 93.4203 | 0 | 64.8768 | 0 | 25.335 | 21.9879 | 0 | 0 | 0 | 0 | 230.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25268.8 | 0 | 25268.8 | 1154170 | -19412.2 | 74 | 78 | 1154170 | -1019412.2
6 | 21 | 19 | 3 | 19.1524 | 0 | 62.7906 | 0 | 10.8294 | 0 | 6.1365 | 8.818 | 0 | 0 | 0 | 1.2 | 108.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18000.3 | 0 | 18000.3 | 195636 | 0 | 68 | 74 | 195636 | -1000000
6 | 21 | 20 | 3 | 18.0573 | 0 | 54.6418 | 0 | 8.9909 | 0 | 5.4984 | 8.818 | 0 | 0 | 0 | 4 | 100.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17193.1 | 0 | 17193.1 | 175203 | 0 | 68 | 73 | 175203 | -1000000
6 | 21 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.9478 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10717.6 | 0 | 10717.6 | 161666 | 0 | 66 | 71 | 161666 | -1000000
6 | 21 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 8.9403 | 0 | 5.4984 | 8.818 | 0 | 0 | 0 | 6.4 | 85.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10456.1 | 0 | 10456.1 | 150771 | 0 | 68 | 74 | 150771 | -1000000
6 | 21 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.1885 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.66 | 0 | 9096.66 | 145293 | 0 | 65 | 72 | 145293 | -1000000
6 | 21 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.0296 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.87 | 0 | 9095.87 | 143827 | 0 | 64 | 70 | 143827 | -1000000
6 | 22 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.5295 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.79 | 0 | 9094.79 | 142958 | 0 | 64 | 70 | 142958 | -1000000
6 | 22 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.1715 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.13 | 0 | 9094.13 | 142031 | 0 | 64 | 69 | 142031 | -1000000
6 | 22 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.1803 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.48 | 0 | 9093.48 | 141203 | 0 | 64 | 65 | 141203 | -1000000
6 | 22 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0585 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10094.4 | 0 | 10094.4 | 143964 | 0 | 63 | 64 | 143964 | -1000000
6 | 22 | 5 | 4 | 24.0015 | 0 | 69.9783 | 0 | 13.707 | 0 | 5.6723 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12322.9 | 0 | 12322.9 | 275763 | 0 | 64 | 65 | 275763 | -1000000
6 | 22 | 6 | 4 | 38.8763 | 0 | 140.608 | 0 | 56.7283 | 0 | 6.332 | 22.8417 | 0 | 0 | 0 | 0 | 265.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33321.9 | 0 | 33321.9 | 1163730 | -4780.4 | 65 | 66 | 1163730 | -1004780.4
6 | 22 | 7 | 4 | 39.0205 | 0 | 168.222 | 0 | 62.7456 | 0 | 25.335 | 22.9244 | 0 | 0 | 0 | 0 | 318.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36548.6 | 0 | 36548.6 | 1213570 | -24064.7 | 64 | 67 | 1213570 | -1024064.7
6 | 22 | 8 | 4 | 39.6631 | 0 | 173.795 | 0 | 71.9961 | 0 | 25.335 | 22.1689 | 0 | 0 | 0 | 0 | 332.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46262.2 | 0 | 46262.2 | 1257640 | -23711.9 | 66 | 70 | 1257640 | -1023711.9
6 | 22 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 76.552 | 0 | 25.335 | 22.3751 | 0 | 0 | 0 | 0 | 337.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72111.9 | 0 | 72111.9 | 1318630 | -23203.6 | 67 | 72 | 1318630 | -1023203.6
6 | 22 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 81.7822 | 0 | 25.335 | 22.2558 | 0 | 0 | 0 | 0 | 333.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729.6 | 0 | 73729.6 | 1369320 | -19663.7 | 68 | 75 | 1369320 | -1019663.7
6 | 22 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 75.5354 | 0 | 25.335 | 22.992 | 0 | 0 | 0 | 0 | 314.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.9 | 0 | 73730.9 | 1274670 | -15112.2 | 69 | 77 | 1274670 | -1015112.2
6 | 22 | 12 | 4 | 39.9339 | 0 | 150.207 | 0 | 73.6109 | 0 | 25.335 | 23.6386 | 0 | 0 | 0 | 0 | 312.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.2 | 0 | 73732.2 | 1238870 | -13661.2 | 68 | 79 | 1238870 | -1013661.2
6 | 22 | 13 | 4 | 41.2527 | 0 | 165.698 | 0 | 85.0743 | 0 | 25.335 | 23.8945 | 0 | 0 | 0 | 0 | 341.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.3 | 0 | 73732.3 | 1420670 | -17377.7 | 69 | 79 | 1420670 | -1017377.7
6 | 22 | 14 | 4 | 40.6372 | 0 | 172.702 | 0 | 81.3472 | 0 | 25.335 | 23.4641 | 0 | 0 | 0 | 0 | 343.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116 | 0 | 72116 | 1355100 | -20934.2 | 66 | 79 | 1355100 | -1020934.2
6 | 22 | 15 | 4 | 40.5471 | 0 | 173.986 | 0 | 81.4868 | 0 | 25.335 | 23.5483 | 0 | 0 | 0 | 0 | 344.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65654.9 | 0 | 65654.9 | 1362560 | -22416.5 | 65 | 81 | 1362560 | -1022416.5
6 | 22 | 16 | 4 | 40.285 | 0 | 169.782 | 0 | 77.1862 | 0 | 25.335 | 23.6276 | 0 | 0 | 0 | 0 | 336.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54347.1 | 0 | 54347.1 | 1309860 | -21895 | 64 | 77 | 1309860 | -1021895
6 | 22 | 17 | 4 | 35.4645 | 0 | 152.497 | 0 | 74.1526 | 0 | 25.335 | 23.1431 | 0 | 0 | 0 | 0 | 310.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41423.9 | 0 | 41423.9 | 1273770 | -26800.8 | 65 | 78 | 1273770 | -1026800.8
6 | 22 | 18 | 4 | 24.5821 | 0 | 93.4203 | 0 | 51.0618 | 0 | 25.335 | 20.9768 | 0 | 0 | 0 | 0 | 215.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25270 | 0 | 25270 | 881790 | -32883.9 | 63 | 76 | 881790 | -1032883.9
6 | 22 | 19 | 4 | 18.9421 | 0 | 62.7906 | 0 | 11.9017 | 0 | 12.3398 | 8.818 | 0 | 0 | 0 | 1.2 | 115.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18001.1 | 0 | 18001.1 | 194546 | 0 | 61 | 75 | 194546 | -1000000
6 | 22 | 20 | 4 | 17.2695 | 0 | 54.6418 | 0 | 8.7081 | 0 | 8.0218 | 8.818 | 0 | 0 | 0 | 4 | 101.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17194.5 | 0 | 17194.5 | 174991 | 0 | 62 | 71 | 174991 | -1000000
6 | 22 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 8.1751 | 0 | 7.8622 | 8.818 | 0 | 0 | 0 | 7.2 | 94.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10719.4 | 0 | 10719.4 | 161197 | 0 | 61 | 70 | 161197 | -1000000
6 | 22 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 6.6469 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 6.4 | 82.8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10458.1 | 0 | 10458.1 | 150181 | 0 | 60 | 66 | 150181 | -1000000
6 | 22 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.1675 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.84 | 0 | 9098.84 | 145323 | 0 | 61 | 65 | 145323 | -1000000
6 | 22 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.046 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.28 | 0 | 9098.28 | 143622 | 0 | 61 | 64 | 143622 | -1000000
6 | 23 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2513 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.98 | 0 | 9097.98 | 142412 | 0 | 60 | 64 | 142412 | -1000000
6 | 23 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9114 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.81 | 0 | 9097.81 | 141564 | 0 | 60 | 63 | 141564 | -1000000
6 | 23 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.7255 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 80.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.69 | 0 | 9097.69 | 140429 | 0 | 59 | 65 | 140429 | -1000000
6 | 23 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.9619 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 3.2 | 82.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10099.1 | 0 | 10099.1 | 143636 | 0 | 59 | 67 | 143636 | -1000000
6 | 23 | 5 | 5 | 23.6599 | 0 | 69.9783 | 0 | 12.8805 | 0 | 5.6327 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12328.2 | 0 | 12328.2 | 260429 | 0 | 59 | 67 | 260429 | -1000000
6 | 23 | 6 | 5 | 37.8099 | 0 | 140.608 | 0 | 46.8719 | 0 | 6.332 | 21.9671 | 0 | 0 | 0 | 0 | 253.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33327.2 | 0 | 33327.2 | 923913 | -5866.04 | 59 | 66 | 923913 | -1005866.04
6 | 23 | 7 | 5 | 39.0141 | 0 | 168.222 | 0 | 59.1635 | 0 | 25.335 | 21.6955 | 0 | 0 | 0 | 0 | 313.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36553.8 | 0 | 36553.8 | 1060590 | -23680.5 | 60 | 70 | 1060590 | -1023680.5
6 | 23 | 8 | 5 | 39.6808 | 0 | 173.795 | 0 | 65.6979 | 0 | 25.335 | 21.3291 | 0 | 0 | 0 | 0 | 325.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46265.2 | 0 | 46265.2 | 1130820 | -23132 | 62 | 73 | 1130820 | -1023132
6 | 23 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 71.8727 | 0 | 25.335 | 21.7613 | 0 | 0 | 0 | 0 | 331.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115.8 | 0 | 72115.8 | 1217700 | -22453.8 | 64 | 77 | 1217700 | -1022453.8
6 | 23 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 74.0496 | 0 | 25.335 | 22.2547 | 0 | 0 | 0 | 0 | 325.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.4 | 0 | 73733.4 | 1265960 | -18568.5 | 65 | 81 | 1265960 | -1018568.5
6 | 23 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 66.5654 | 0 | 25.335 | 22.9146 | 0 | 0 | 0 | 0 | 305.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.4 | 0 | 73734.4 | 1141270 | -14041.7 | 64 | 82 | 1141270 | -1014041.7
6 | 23 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 74.1158 | 0 | 25.335 | 23.0108 | 0 | 0 | 0 | 0 | 312.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.7 | 0 | 73734.7 | 1258880 | -19307.4 | 66 | 83 | 1258880 | -1019307.4
6 | 23 | 13 | 5 | 41.245 | 0 | 165.698 | 0 | 74.6648 | 0 | 25.335 | 23.4537 | 0 | 0 | 0 | 0 | 330.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.6 | 0 | 73734.6 | 1262170 | -23899.4 | 64 | 79 | 1262170 | -1023899.4
6 | 23 | 14 | 5 | 40.6758 | 0 | 172.702 | 0 | 78.2394 | 0 | 25.335 | 23.3001 | 0 | 0 | 0 | 0 | 340.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.1 | 0 | 72119.1 | 1315130 | -26734.9 | 65 | 79 | 1315130 | -1026734.9
6 | 23 | 15 | 5 | 40.5352 | 0 | 173.986 | 0 | 68.9028 | 0 | 25.335 | 23.2804 | 0 | 0 | 0 | 0 | 332.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657 | 0 | 65657 | 1267120 | -24650.4 | 64 | 67 | 1267120 | -1024650.4
6 | 23 | 16 | 5 | 40.2812 | 0 | 169.782 | 0 | 82.8791 | 0 | 25.335 | 23.2747 | 0 | 0 | 0 | 0 | 341.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349 | 0 | 54349 | 1378530 | -23403.1 | 67 | 74 | 1378530 | -1023403.1
6 | 23 | 17 | 5 | 35.6887 | 0 | 152.497 | 0 | 77.8722 | 0 | 25.335 | 23.3906 | 0 | 0 | 0 | 0 | 314.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41425.2 | 0 | 41425.2 | 1331200 | -19477.7 | 69 | 78 | 1331200 | -1019477.7
6 | 23 | 18 | 5 | 24.7001 | 0 | 93.4203 | 0 | 39.1287 | 0 | 25.335 | 21.1785 | 0 | 0 | 0 | 0 | 203.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25271.4 | 0 | 25271.4 | 716356 | -15196.5 | 60 | 71 | 716356 | -1015196.5
6 | 23 | 19 | 5 | 18.5834 | 0 | 62.7906 | 0 | 11.4075 | 0 | 11.21 | 8.818 | 0 | 0 | 0 | 1.2 | 114.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18002.5 | 0 | 18002.5 | 194908 | 0 | 61 | 71 | 194908 | -1000000
6 | 23 | 20 | 5 | 17.286 | 0 | 54.6418 | 0 | 8.3783 | 0 | 7.8522 | 8.818 | 0 | 0 | 0 | 4 | 100.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196 | 0 | 17196 | 174544 | 0 | 60 | 68 | 174544 | -1000000
6 | 23 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.3858 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10721.4 | 0 | 10721.4 | 161060 | 0 | 59 | 65 | 161060 | -1000000
6 | 23 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 6.4455 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 6.4 | 82.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10460.7 | 0 | 10460.7 | 149695 | 0 | 57 | 61 | 149695 | -1000000
6 | 23 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.5392 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 80.2937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.71 | 0 | 9101.71 | 144670 | 0 | 57 | 62 | 144670 | -1000000
6 | 23 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.6067 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.57 | 0 | 9101.57 | 142898 | 0 | 57 | 60 | 142898 | -1000000
6 | 24 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0671 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.69 | 0 | 9101.69 | 141756 | 0 | 57 | 60 | 141756 | -1000000
6 | 24 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.3236 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.47 | 0 | 9102.47 | 140919 | 0 | 58 | 61 | 140919 | -1000000
6 | 24 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0078 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102.96 | 0 | 9102.96 | 139650 | 0 | 56 | 61 | 139650 | -1000000
6 | 24 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6736 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 3.2 | 73.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.44 | 0 | 9103.44 | 138762 | 0 | 54 | 58 | 138762 | -1000000
6 | 24 | 5 | 6 | 6.2596 | 0 | 42.7453 | 0 | 6.8852 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9103.82 | 0 | 9103.82 | 137777 | 0 | 52 | 57 | 137777 | -1000000
6 | 24 | 6 | 6 | 4.9178 | 0 | 42.7453 | 0 | 6.9407 | 0 | 6.6449 | 8.818 | 0 | 0 | 0 | 0 | 70.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.23 | 0 | 9104.23 | 137108 | 0 | 51 | 56 | 137108 | -1000000
6 | 24 | 7 | 6 | 4.615 | 0 | 42.7453 | 0 | 16.1911 | 0 | 6.0405 | 18.8896 | 0 | 0 | 0 | 0 | 88.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9104.78 | 0 | 9104.78 | 238378 | -16210.1 | 51 | 57 | 238378 | -1016210.1
6 | 24 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 12.9801 | 0 | 12.5633 | 18.8896 | 0 | 0 | 0 | 0 | 92.1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9105.29 | 0 | 9105.29 | 241920 | -18087.3 | 51 | 58 | 241920 | -1018087.3
6 | 24 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.3378 | 0 | 6.0388 | 18.8896 | 0 | 0 | 0 | 0 | 88.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9118.17 | 0 | 9118.17 | 248035 | -26309.4 | 53 | 60 | 248035 | -1026309.4
6 | 24 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 14.0927 | 0 | 14.587 | 18.8896 | 0 | 0 | 0 | 0 | 95.7835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9120.14 | 0 | 9120.14 | 247485 | -17540.6 | 54 | 62 | 247485 | -1017540.6
6 | 24 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 14.0068 | 0 | 14.2884 | 18.8996 | 0 | 0 | 0 | 0 | 95.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9121.44 | 0 | 9121.44 | 254734 | -17461.8 | 54 | 62 | 254734 | -1017461.8
6 | 24 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.0666 | 0 | 16.3854 | 18.9224 | 0 | 0 | 0 | 0 | 98.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9122.4 | 0 | 9122.4 | 266168 | -18045.7 | 54 | 63 | 266168 | -1018045.7
6 | 24 | 13 | 6 | 5.4693 | 0 | 42.7453 | 0 | 16.0222 | 0 | 18.6684 | 19.0037 | 0 | 0 | 0 | 0 | 101.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9123.18 | 0 | 9123.18 | 282212 | -18400.2 | 55 | 64 | 282212 | -1018400.2
6 | 24 | 14 | 6 | 5.4724 | 0 | 42.7453 | 0 | 8.6069 | 0 | 7.4953 | 8.818 | 0 | 0 | 0 | 0 | 73.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9123.84 | 0 | 9123.84 | 132485 | 0 | 56 | 66 | 132485 | -1000000
6 | 24 | 15 | 6 | 5.473 | 0 | 42.7453 | 0 | 8.1543 | 0 | 7.2257 | 8.818 | 0 | 0 | 0 | 0 | 72.4162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9124.55 | 0 | 9124.55 | 132066 | 0 | 56 | 67 | 132066 | -1000000
6 | 24 | 16 | 6 | 5.4732 | 0 | 42.7453 | 0 | 8.0631 | 0 | 7.2453 | 8.818 | 0 | 0 | 0 | 0 | 72.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9119.22 | 0 | 9119.22 | 131811 | 0 | 56 | 68 | 131811 | -1000000
6 | 24 | 17 | 6 | 5.4733 | 0 | 42.7453 | 0 | 7.9609 | 0 | 7.2623 | 8.818 | 0 | 0 | 0 | 0 | 72.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9116.7 | 0 | 9116.7 | 131550 | 0 | 56 | 69 | 131550 | -1000000
6 | 24 | 18 | 6 | 5.474 | 0 | 42.7453 | 0 | 7.6063 | 0 | 7.0404 | 8.818 | 0 | 0 | 0 | 0 | 71.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9114.96 | 0 | 9114.96 | 131356 | 0 | 56 | 69 | 131356 | -1000000
6 | 24 | 19 | 6 | 6.6797 | 0 | 42.7453 | 0 | 6.9216 | 0 | 6.5901 | 8.818 | 0 | 0 | 0 | 1.2 | 72.9547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9113.67 | 0 | 9113.67 | 131306 | 0 | 57 | 67 | 131306 | -1000000
6 | 24 | 20 | 6 | 8.1492 | 0 | 42.7453 | 0 | 6.1482 | 0 | 6.1696 | 8.818 | 0 | 0 | 0 | 4 | 76.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9112.77 | 0 | 9112.77 | 130862 | 0 | 56 | 63 | 130862 | -1000000
6 | 24 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.9743 | 0 | 6.1442 | 8.818 | 0 | 0 | 0 | 7.2 | 79.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9112.07 | 0 | 9112.07 | 130513 | 0 | 55 | 60 | 130513 | -1000000
6 | 24 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.538 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 6.4 | 78.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.63 | 0 | 9111.63 | 130190 | 0 | 54 | 57 | 130190 | -1000000
6 | 24 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5198 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 5.6 | 77.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9111.6 | 0 | 9111.6 | 129791 | 0 | 53 | 56 | 129791 | -1000000
6 | 24 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.5052 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.31 | 0 | 3458.31 | 129472 | 0 | 53 | 55 | 129472 | -1000000
6 | 25 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4825 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.8 | 0 | 3458.8 | 128971 | 0 | 52 | 55 | 128971 | -1000000
6 | 25 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4712 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459.58 | 0 | 3459.58 | 128729 | 0 | 52 | 54 | 128729 | -1000000
6 | 25 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4536 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460.38 | 0 | 3460.38 | 128342 | 0 | 52 | 54 | 128342 | -1000000
6 | 25 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4384 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 3.2 | 71.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461.21 | 0 | 3461.21 | 128011 | 0 | 52 | 54 | 128011 | -1000000
6 | 25 | 5 | 7 | 4.9609 | 0 | 42.7453 | 0 | 6.4233 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 1.6 | 70.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462.07 | 0 | 3462.07 | 127680 | 0 | 52 | 54 | 127680 | -1000000
6 | 25 | 6 | 7 | 3.8608 | 0 | 42.7453 | 0 | 6.8206 | 0 | 6.4688 | 8.818 | 0 | 0 | 0 | 0 | 68.7135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462.94 | 0 | 3462.94 | 127449 | 0 | 53 | 56 | 127449 | -1000000
6 | 25 | 7 | 7 | 3.7462 | 0 | 42.7453 | 0 | 6.407 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 0 | 67.2013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.77 | 0 | 3463.77 | 127326 | 0 | 55 | 59 | 127326 | -1000000
6 | 25 | 8 | 7 | 3.8459 | 0 | 42.7453 | 0 | 6.9881 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 0 | 67.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464.57 | 0 | 3464.57 | 127202 | 0 | 57 | 62 | 127202 | -1000000
6 | 25 | 9 | 7 | 4.1684 | 0 | 42.7453 | 0 | 7.6683 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 0 | 68.8791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464.65 | 0 | 3464.65 | 127086 | 0 | 59 | 66 | 127086 | -1000000
6 | 25 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.5314 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 0 | 68.7178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464.88 | 0 | 3464.88 | 127082 | 0 | 61 | 69 | 127082 | -1000000
6 | 25 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.342 | 0 | 5.53 | 8.818 | 0 | 0 | 0 | 0 | 68.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464.02 | 0 | 3464.02 | 126963 | 0 | 62 | 71 | 126963 | -1000000
6 | 25 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.2387 | 0 | 10.2123 | 12.8287 | 0 | 0 | 0 | 0 | 80.1689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.32 | 0 | 3463.32 | 170473 | 0 | 64 | 74 | 170473 | -1000000
6 | 25 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.5852 | 0 | 10.5297 | 12.8287 | 0 | 0 | 0 | 0 | 80.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462.02 | 0 | 3462.02 | 181122 | 0 | 64 | 76 | 181122 | -1000000
6 | 25 | 14 | 7 | 4.1455 | 0 | 42.7453 | 0 | 10.9662 | 0 | 10.7603 | 12.8287 | 0 | 0 | 0 | 0 | 81.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460.26 | 0 | 3460.26 | 187064 | 0 | 66 | 78 | 187064 | -1000000
6 | 25 | 15 | 7 | 4.1465 | 0 | 42.7453 | 0 | 11.2397 | 0 | 11.1806 | 12.8287 | 0 | 0 | 0 | 0 | 82.1408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.78 | 0 | 3458.78 | 192350 | 0 | 67 | 79 | 192350 | -1000000
6 | 25 | 16 | 7 | 4.1465 | 0 | 42.7453 | 0 | 10.4759 | 0 | 10.0823 | 10.866 | 0 | 0 | 0 | 0 | 78.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457.18 | 0 | 3457.18 | 177783 | 0 | 68 | 80 | 177783 | -1000000
6 | 25 | 17 | 7 | 4.1462 | 0 | 42.7453 | 0 | 10.3067 | 0 | 9.9108 | 10.866 | 0 | 0 | 0 | 0 | 77.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455.56 | 0 | 3455.56 | 176052 | 0 | 68 | 81 | 176052 | -1000000
6 | 25 | 18 | 7 | 4.168 | 0 | 42.7453 | 0 | 7.621 | 0 | 7.253 | 8.818 | 0 | 0 | 0 | 0 | 70.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454.04 | 0 | 3454.04 | 126858 | 0 | 66 | 78 | 126858 | -1000000
6 | 25 | 19 | 7 | 4.972 | 0 | 42.7453 | 0 | 7.218 | 0 | 7.1279 | 8.818 | 0 | 0 | 0 | 1.2 | 72.0812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3452.54 | 0 | 3452.54 | 127095 | 0 | 66 | 76 | 127095 | -1000000
6 | 25 | 20 | 7 | 6.2984 | 0 | 42.7453 | 0 | 6.9705 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4 | 74.3108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3451.09 | 0 | 3451.09 | 127120 | 0 | 66 | 75 | 127120 | -1000000
6 | 25 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.65 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 77.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449.88 | 0 | 3449.88 | 127117 | 0 | 66 | 74 | 127117 | -1000000
6 | 25 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.9138 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 77.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3449.01 | 0 | 3449.01 | 126828 | 0 | 65 | 74 | 126828 | -1000000
6 | 25 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.6043 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 5.6 | 75.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3448.35 | 0 | 3448.35 | 127010 | 0 | 65 | 73 | 127010 | -1000000
6 | 25 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.7982 | 0 | 5.5183 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9101.31 | 0 | 9101.31 | 187358 | 0 | 65 | 73 | 187358 | -1000000
6 | 26 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.6218 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.73 | 0 | 9100.73 | 127174 | 0 | 65 | 72 | 127174 | -1000000
6 | 26 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5224 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.36 | 0 | 9099.36 | 126938 | 0 | 64 | 71 | 126938 | -1000000
6 | 26 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.8046 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.55 | 0 | 9098.55 | 127138 | 0 | 65 | 71 | 127138 | -1000000
6 | 26 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.9871 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 3.2 | 81.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10099.1 | 0 | 10099.1 | 130955 | 0 | 65 | 71 | 130955 | -1000000
6 | 26 | 5 | 1 | 23.663 | 0 | 69.9783 | 0 | 13.4428 | 0 | 5.6837 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12327.6 | 0 | 12327.6 | 266075 | 0 | 65 | 71 | 266075 | -1000000
6 | 26 | 6 | 1 | 36.4728 | 0 | 140.608 | 0 | 77.7843 | 0 | 6.332 | 22.2035 | 0 | 0 | 0 | 0 | 283.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33326.1 | 0 | 33326.1 | 1294540 | -7769.82 | 66 | 72 | 1294540 | -1007769.82
6 | 26 | 7 | 1 | 39.0503 | 0 | 168.222 | 0 | 80.1842 | 0 | 6.332 | 22.1844 | 0 | 0 | 0 | 0 | 315.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36552.3 | 0 | 36552.3 | 1345030 | -15998.2 | 67 | 74 | 1345030 | -1015998.2
6 | 26 | 8 | 1 | 39.7863 | 0 | 173.795 | 0 | 83.9113 | 0 | 6.332 | 22.1334 | 0 | 0 | 0 | 0 | 325.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46264.8 | 0 | 46264.8 | 1427730 | -11027.5 | 70 | 78 | 1427730 | -1011027.5
6 | 26 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 89.2208 | 0 | 6.332 | 22.7627 | 0 | 0 | 0 | 0 | 331.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116.1 | 0 | 72116.1 | 1536080 | -10540.9 | 72 | 82 | 1536080 | -1010540.9
6 | 26 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 90.2415 | 0 | 6.332 | 23.4022 | 0 | 0 | 0 | 0 | 324.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.6 | 0 | 73733.6 | 1601110 | -9006.9 | 73 | 84 | 1601110 | -1009006.9
6 | 26 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 84.8699 | 0 | 6.332 | 23.2001 | 0 | 0 | 0 | 0 | 304.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.5 | 0 | 73734.5 | 1546750 | -12081.3 | 75 | 85 | 1546750 | -1012081.3
6 | 26 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 99.835 | 0 | 6.332 | 22.9893 | 0 | 0 | 0 | 0 | 319.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.7 | 0 | 73734.7 | 1725940 | -19314.8 | 77 | 89 | 1725940 | -1019314.8
6 | 26 | 13 | 1 | 41.233 | 0 | 165.698 | 0 | 121.106 | 0 | 6.332 | 22.9301 | 0 | 0 | 0 | 0 | 357.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734.7 | 0 | 73734.7 | 1886510 | -31124.9 | 77 | 91 | 1886510 | -1031124.9
6 | 26 | 14 | 1 | 40.6328 | 0 | 172.702 | 0 | 115.607 | 0 | 6.332 | 22.8386 | 0 | 0 | 0 | 0 | 358.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72119.3 | 0 | 72119.3 | 1830170 | -32584.8 | 76 | 89 | 1830170 | -1032584.8
6 | 26 | 15 | 1 | 40.5292 | 0 | 173.986 | 0 | 114.196 | 0 | 6.332 | 22.9621 | 0 | 0 | 0 | 0 | 358.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65657.9 | 0 | 65657.9 | 1824130 | -33167.7 | 75 | 87 | 1824130 | -1033167.7
6 | 26 | 16 | 1 | 40.33 | 0 | 169.782 | 0 | 118.558 | 0 | 6.332 | 23.1322 | 0 | 0 | 0 | 0 | 358.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54349.8 | 0 | 54349.8 | 1866410 | -33250.9 | 76 | 88 | 1866410 | -1033250.9
6 | 26 | 17 | 1 | 35.4895 | 0 | 152.497 | 0 | 123.431 | 0 | 6.332 | 22.7679 | 0 | 0 | 0 | 0 | 340.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41426.5 | 0 | 41426.5 | 1847850 | -36180.5 | 77 | 89 | 1847850 | -1036180.5
6 | 26 | 18 | 1 | 24.6552 | 0 | 93.4203 | 0 | 96.9753 | 0 | 6.332 | 21.2236 | 0 | 0 | 0 | 0 | 242.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25272.8 | 0 | 25272.8 | 1363570 | -45534.9 | 76 | 88 | 1363570 | -1045534.9
6 | 26 | 19 | 1 | 17.9523 | 0 | 62.7906 | 0 | 11.1363 | 0 | 5.5718 | 8.818 | 0 | 0 | 0 | 1.2 | 107.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18003.9 | 0 | 18003.9 | 191287 | 0 | 75 | 86 | 191287 | -1000000
6 | 26 | 20 | 1 | 18.0442 | 0 | 54.6418 | 0 | 9.1463 | 0 | 5.504 | 8.818 | 0 | 0 | 0 | 4 | 100.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196.8 | 0 | 17196.8 | 170487 | 0 | 74 | 80 | 170487 | -1000000
6 | 26 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 8.5001 | 0 | 5.4911 | 8.818 | 0 | 0 | 0 | 7.2 | 92.7295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10720.7 | 0 | 10720.7 | 157635 | 0 | 75 | 79 | 157635 | -1000000
6 | 26 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.9676 | 0 | 5.4839 | 8.818 | 0 | 0 | 0 | 6.4 | 84.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10458.1 | 0 | 10458.1 | 146972 | 0 | 75 | 79 | 146972 | -1000000
6 | 26 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.0442 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.93 | 0 | 9097.93 | 141475 | 0 | 70 | 73 | 141475 | -1000000
6 | 26 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.5295 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.53 | 0 | 9096.53 | 140184 | 0 | 71 | 73 | 140184 | -1000000
6 | 27 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.8152 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.27 | 0 | 9095.27 | 139426 | 0 | 71 | 74 | 139426 | -1000000
6 | 27 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5454 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.33 | 0 | 9094.33 | 138629 | 0 | 70 | 71 | 138629 | -1000000
6 | 27 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.3314 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.58 | 0 | 9093.58 | 137966 | 0 | 70 | 71 | 137966 | -1000000
6 | 27 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.4038 | 0 | 5.5755 | 12.8287 | 0 | 0 | 0 | 3.2 | 89.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10094.2 | 0 | 10094.2 | 216108 | 0 | 71 | 72 | 216108 | -1000000
6 | 27 | 5 | 2 | 24.1008 | 0 | 69.9783 | 0 | 14.9536 | 0 | 5.8001 | 12.8287 | 0 | 0 | 0 | 1.6 | 129.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12322.6 | 0 | 12322.6 | 294426 | 0 | 71 | 72 | 294426 | -1000000
6 | 27 | 6 | 2 | 44.6544 | 0 | 140.608 | 0 | 74.8684 | 0 | 6.332 | 23.1247 | 0 | 0 | 0 | 0 | 289.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33321.1 | 0 | 33321.1 | 1467310 | -4584.94 | 69 | 73 | 1467310 | -1004584.94
6 | 27 | 7 | 2 | 43.3698 | 0 | 168.222 | 0 | 78.5795 | 0 | 6.332 | 23.5166 | 0 | 0 | 0 | 0 | 320.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36547.4 | 0 | 36547.4 | 1523480 | -15957.3 | 71 | 73 | 1523480 | -1015957.3
6 | 27 | 8 | 2 | 39.8693 | 0 | 173.795 | 0 | 86.1999 | 0 | 6.332 | 23.6631 | 0 | 0 | 0 | 0 | 329.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46263.2 | 0 | 46263.2 | 1499610 | -17135.8 | 72 | 75 | 1499610 | -1017135.8
6 | 27 | 9 | 2 | 41.0525 | 0 | 172.186 | 0 | 86.0878 | 0 | 6.332 | 23.8855 | 0 | 0 | 0 | 0 | 329.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72112.6 | 0 | 72112.6 | 1565080 | -17859.6 | 73 | 78 | 1565080 | -1017859.6
6 | 27 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 80.7988 | 0 | 25.335 | 23.5098 | 0 | 0 | 0 | 0 | 333.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73728.7 | 0 | 73728.7 | 1537980 | -15291 | 72 | 78 | 1537980 | -1015291
6 | 27 | 11 | 2 | 40.944 | 0 | 149.692 | 0 | 77.4656 | 0 | 25.335 | 23.8324 | 0 | 0 | 0 | 0 | 317.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729.8 | 0 | 73729.8 | 1455910 | -10739.3 | 74 | 82 | 1455910 | -1010739.3
6 | 27 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 86.3952 | 0 | 25.335 | 23.5338 | 0 | 0 | 0 | 0 | 325.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.2 | 0 | 73731.2 | 1593020 | -16960.1 | 75 | 84 | 1593020 | -1016960.1
6 | 27 | 13 | 2 | 41.2375 | 0 | 165.698 | 0 | 99.2304 | 0 | 25.335 | 24.1292 | 0 | 0 | 0 | 0 | 355.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.5 | 0 | 73731.5 | 1701490 | -13113.1 | 75 | 84 | 1701490 | -1013113.1
6 | 27 | 14 | 2 | 40.6358 | 0 | 172.702 | 0 | 103.952 | 0 | 25.335 | 23.7263 | 0 | 0 | 0 | 0 | 366.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72116.9 | 0 | 72116.9 | 1785090 | -17194.3 | 76 | 86 | 1785090 | -1017194.3
6 | 27 | 15 | 2 | 40.5519 | 0 | 173.986 | 0 | 114.229 | 0 | 18.1218 | 23.1449 | 0 | 0 | 0 | 0 | 370.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65655.7 | 0 | 65655.7 | 1827020 | -32682.7 | 75 | 87 | 1827020 | -1032682.7
6 | 27 | 16 | 2 | 40.3005 | 0 | 169.782 | 0 | 105.718 | 0 | 10.2317 | 23.3586 | 0 | 0 | 0 | 0 | 349.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54348 | 0 | 54348 | 1670150 | -33475.5 | 71 | 88 | 1670150 | -1033475.5
6 | 27 | 17 | 2 | 35.4713 | 0 | 152.497 | 0 | 107.65 | 0 | 6.332 | 22.9957 | 0 | 0 | 0 | 0 | 324.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41424.7 | 0 | 41424.7 | 1638240 | -36715.9 | 72 | 87 | 1638240 | -1036715.9
6 | 27 | 18 | 2 | 24.5847 | 0 | 93.4203 | 0 | 87.5456 | 0 | 6.332 | 21.4002 | 0 | 0 | 0 | 0 | 233.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25271.1 | 0 | 25271.1 | 1247200 | -47071.4 | 72 | 85 | 1247200 | -1047071.4
6 | 27 | 19 | 2 | 18.7218 | 0 | 62.7906 | 0 | 11.2202 | 0 | 5.5756 | 8.818 | 0 | 0 | 0 | 1.2 | 108.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18002.2 | 0 | 18002.2 | 194975 | 0 | 71 | 82 | 194975 | -1000000
6 | 27 | 20 | 2 | 17.3871 | 0 | 54.6418 | 0 | 9.348 | 0 | 5.5089 | 8.818 | 0 | 0 | 0 | 4 | 99.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17195 | 0 | 17195 | 174546 | 0 | 72 | 78 | 174546 | -1000000
6 | 27 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.6813 | 0 | 5.4943 | 8.818 | 0 | 0 | 0 | 7.2 | 92.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10719.1 | 0 | 10719.1 | 161267 | 0 | 71 | 75 | 161267 | -1000000
6 | 27 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.4796 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10456.9 | 0 | 10456.9 | 150237 | 0 | 70 | 73 | 150237 | -1000000
6 | 27 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1367 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.97 | 0 | 9096.97 | 145112 | 0 | 69 | 71 | 145112 | -1000000
6 | 27 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.274 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.87 | 0 | 9095.87 | 143265 | 0 | 66 | 70 | 143265 | -1000000
6 | 28 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8461 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.02 | 0 | 9095.02 | 141687 | 0 | 62 | 68 | 141687 | -1000000
6 | 28 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7369 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.35 | 0 | 9094.35 | 141033 | 0 | 60 | 66 | 141033 | -1000000
6 | 28 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.632 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.8 | 0 | 9093.8 | 140384 | 0 | 60 | 64 | 140384 | -1000000
6 | 28 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.2971 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 3.2 | 81.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10094.9 | 0 | 10094.9 | 143466 | 0 | 60 | 64 | 143466 | -1000000
6 | 28 | 5 | 3 | 24.0552 | 0 | 69.9783 | 0 | 13.3154 | 0 | 5.6449 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12323.7 | 0 | 12323.7 | 274594 | 0 | 60 | 64 | 274594 | -1000000
6 | 28 | 6 | 3 | 40.3368 | 0 | 140.608 | 0 | 54.9527 | 0 | 6.332 | 22.644 | 0 | 0 | 0 | 0 | 264.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33322.8 | 0 | 33322.8 | 1101600 | -4839.19 | 62 | 68 | 1101600 | -1004839.19
6 | 28 | 7 | 3 | 39.1903 | 0 | 168.222 | 0 | 56.389 | 0 | 6.332 | 22.6839 | 0 | 0 | 0 | 0 | 292.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36549.5 | 0 | 36549.5 | 1139290 | -22251.2 | 62 | 68 | 1139290 | -1022251.2
6 | 28 | 8 | 3 | 39.6947 | 0 | 173.795 | 0 | 65.1052 | 0 | 6.332 | 22.7258 | 0 | 0 | 0 | 0 | 307.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46263.2 | 0 | 46263.2 | 1167190 | -21580.6 | 63 | 73 | 1167190 | -1021580.6
6 | 28 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 61.646 | 0 | 6.332 | 22.6829 | 0 | 0 | 0 | 0 | 303.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72112.4 | 0 | 72112.4 | 1192780 | -22442.4 | 64 | 70 | 1192780 | -1022442.4
6 | 28 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 61.5495 | 0 | 25.335 | 22.4538 | 0 | 0 | 0 | 0 | 313.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73729.5 | 0 | 73729.5 | 1179090 | -19221.2 | 63 | 72 | 1179090 | -1019221.2
6 | 28 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 63.6883 | 0 | 25.335 | 22.9645 | 0 | 0 | 0 | 0 | 302.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73730.3 | 0 | 73730.3 | 1141910 | -14609.1 | 65 | 75 | 1141910 | -1014609.1
6 | 28 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 65.1247 | 0 | 25.335 | 23.2315 | 0 | 0 | 0 | 0 | 303.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.9 | 0 | 73731.9 | 1176470 | -15235.7 | 65 | 77 | 1176470 | -1015235.7
6 | 28 | 13 | 3 | 41.233 | 0 | 165.698 | 0 | 72.6468 | 0 | 25.335 | 23.7148 | 0 | 0 | 0 | 0 | 328.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.4 | 0 | 73732.4 | 1256390 | -15986.8 | 64 | 81 | 1256390 | -1015986.8
6 | 28 | 14 | 3 | 40.6539 | 0 | 172.702 | 0 | 75.0767 | 0 | 25.335 | 23.3276 | 0 | 0 | 0 | 0 | 337.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72117.1 | 0 | 72117.1 | 1301900 | -19645.5 | 64 | 81 | 1301900 | -1019645.5
6 | 28 | 15 | 3 | 40.546 | 0 | 173.986 | 0 | 79.7407 | 0 | 25.335 | 23.4663 | 0 | 0 | 0 | 0 | 343.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65655.8 | 0 | 65655.8 | 1379830 | -21174.6 | 65 | 81 | 1379830 | -1021174.6
6 | 28 | 16 | 3 | 40.2881 | 0 | 169.782 | 0 | 81.7134 | 0 | 25.335 | 23.2273 | 0 | 0 | 0 | 0 | 340.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54347.9 | 0 | 54347.9 | 1424190 | -29237.3 | 66 | 81 | 1424190 | -1029237.3
6 | 28 | 17 | 3 | 35.466 | 0 | 152.497 | 0 | 81.0581 | 0 | 7.1904 | 22.8302 | 0 | 0 | 0 | 0 | 299.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41424.7 | 0 | 41424.7 | 1347220 | -33700.1 | 66 | 81 | 1347220 | -1033700.1
6 | 28 | 18 | 3 | 24.5811 | 0 | 93.4203 | 0 | 60.1978 | 0 | 6.332 | 21.311 | 0 | 0 | 0 | 0 | 205.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25270.8 | 0 | 25270.8 | 992379 | -34769.2 | 66 | 80 | 992379 | -1034769.2
6 | 28 | 19 | 3 | 18.2752 | 0 | 62.7906 | 0 | 11.0318 | 0 | 5.5672 | 8.818 | 0 | 0 | 0 | 1.2 | 107.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18001.8 | 0 | 18001.8 | 195444 | 0 | 66 | 78 | 195444 | -1000000
6 | 28 | 20 | 3 | 17.6025 | 0 | 54.6418 | 0 | 9.3818 | 0 | 5.5098 | 8.818 | 0 | 0 | 0 | 4 | 99.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17194.9 | 0 | 17194.9 | 175227 | 0 | 66 | 76 | 175227 | -1000000
6 | 28 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.4108 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 91.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10719.7 | 0 | 10719.7 | 161845 | 0 | 66 | 71 | 161845 | -1000000
6 | 28 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.0075 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10458.1 | 0 | 10458.1 | 150519 | 0 | 65 | 68 | 150519 | -1000000
6 | 28 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.5662 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 5.6 | 80.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.44 | 0 | 9098.44 | 145483 | 0 | 65 | 68 | 145483 | -1000000
6 | 28 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.4872 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.52 | 0 | 9097.52 | 143884 | 0 | 65 | 68 | 143884 | -1000000
6 | 29 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.4393 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.07 | 0 | 9097.07 | 142892 | 0 | 65 | 68 | 142892 | -1000000
6 | 29 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0876 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.66 | 0 | 9096.66 | 141994 | 0 | 65 | 67 | 141994 | -1000000
6 | 29 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.3127 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.28 | 0 | 9096.28 | 141123 | 0 | 65 | 67 | 141123 | -1000000
6 | 29 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.8336 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 3.2 | 80.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10097.4 | 0 | 10097.4 | 143951 | 0 | 63 | 65 | 143951 | -1000000
6 | 29 | 5 | 4 | 23.8459 | 0 | 69.9783 | 0 | 13.4501 | 0 | 5.6569 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12326.2 | 0 | 12326.2 | 275904 | 0 | 64 | 65 | 275904 | -1000000
6 | 29 | 6 | 4 | 37.5414 | 0 | 140.608 | 0 | 58.1472 | 0 | 6.332 | 22.5814 | 0 | 0 | 0 | 0 | 265.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33325.1 | 0 | 33325.1 | 1184250 | -5021.27 | 66 | 67 | 1184250 | -1005021.27
6 | 29 | 7 | 4 | 38.9787 | 0 | 168.222 | 0 | 66.5885 | 0 | 6.332 | 22.0906 | 0 | 0 | 0 | 0 | 302.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36551.8 | 0 | 36551.8 | 1218550 | -23184.5 | 64 | 70 | 1218550 | -1023184.5
6 | 29 | 8 | 4 | 39.6631 | 0 | 173.795 | 0 | 61.5794 | 0 | 6.332 | 21.9436 | 0 | 0 | 0 | 0 | 303.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46264.3 | 0 | 46264.3 | 1136810 | -23003.8 | 62 | 71 | 1136810 | -1023003.8
6 | 29 | 9 | 4 | 40.675 | 0 | 172.186 | 0 | 67.6906 | 0 | 25.335 | 22.7146 | 0 | 0 | 0 | 0 | 328.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72115 | 0 | 72115 | 1203370 | -22716.6 | 64 | 74 | 1203370 | -1022716.6
6 | 29 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 72.9499 | 0 | 25.335 | 22.5112 | 0 | 0 | 0 | 0 | 325.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.9 | 0 | 73731.9 | 1253410 | -19257.9 | 65 | 76 | 1253410 | -1019257.9
6 | 29 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 66.3907 | 0 | 25.335 | 23.0182 | 0 | 0 | 0 | 0 | 305.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.8 | 0 | 73731.8 | 1143720 | -14972.5 | 65 | 77 | 1143720 | -1014972.5
6 | 29 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 67.4218 | 0 | 25.335 | 23.1974 | 0 | 0 | 0 | 0 | 305.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.1 | 0 | 73733.1 | 1156060 | -15384 | 64 | 78 | 1156060 | -1015384
6 | 29 | 13 | 4 | 41.233 | 0 | 165.698 | 0 | 73.4187 | 0 | 25.335 | 23.6931 | 0 | 0 | 0 | 0 | 329.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73733.3 | 0 | 73733.3 | 1248940 | -17230.6 | 64 | 79 | 1248940 | -1017230.6
6 | 29 | 14 | 4 | 40.6341 | 0 | 172.702 | 0 | 77.1516 | 0 | 25.335 | 23.4358 | 0 | 0 | 0 | 0 | 339.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72118 | 0 | 72118 | 1307290 | -21066.9 | 65 | 79 | 1307290 | -1021066.9
6 | 29 | 15 | 4 | 40.5266 | 0 | 173.986 | 0 | 76.4445 | 0 | 25.335 | 23.4699 | 0 | 0 | 0 | 0 | 339.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65656.4 | 0 | 65656.4 | 1302420 | -23133.6 | 64 | 77 | 1302420 | -1023133.6
6 | 29 | 16 | 4 | 40.3814 | 0 | 169.782 | 0 | 70.8659 | 0 | 25.335 | 23.7022 | 0 | 0 | 0 | 0 | 330.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54348.3 | 0 | 54348.3 | 1235270 | -22637.1 | 63 | 75 | 1235270 | -1022637.1
6 | 29 | 17 | 4 | 36.0956 | 0 | 152.497 | 0 | 62.2633 | 0 | 25.335 | 23.576 | 0 | 0 | 0 | 0 | 299.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41425 | 0 | 41425 | 1109750 | -19136.8 | 63 | 74 | 1109750 | -1019136.8
6 | 29 | 18 | 4 | 28.8398 | 0 | 93.4203 | 0 | 41.9795 | 0 | 25.335 | 21.0046 | 0 | 0 | 0 | 0 | 210.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25271.1 | 0 | 25271.1 | 791152 | -14520.5 | 64 | 72 | 791152 | -1014520.5
6 | 29 | 19 | 4 | 21.0868 | 0 | 62.7906 | 0 | 10.3481 | 0 | 10.4262 | 8.818 | 0 | 0 | 0 | 1.2 | 114.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18001.8 | 0 | 18001.8 | 194770 | 0 | 62 | 71 | 194770 | -1000000
6 | 29 | 20 | 4 | 18.2418 | 0 | 54.6418 | 0 | 8.7889 | 0 | 5.492 | 8.818 | 0 | 0 | 0 | 4 | 99.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17195.6 | 0 | 17195.6 | 174323 | 0 | 60 | 70 | 174323 | -1000000
6 | 29 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7477 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10720.9 | 0 | 10720.9 | 160365 | 0 | 56 | 68 | 160365 | -1000000
6 | 29 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 6.8546 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 6.4 | 83.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10460.1 | 0 | 10460.1 | 149791 | 0 | 56 | 65 | 149791 | -1000000
6 | 29 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.7056 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 80.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.98 | 0 | 9100.98 | 144636 | 0 | 56 | 66 | 144636 | -1000000
6 | 29 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.7612 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.58 | 0 | 9100.58 | 143137 | 0 | 56 | 64 | 143137 | -1000000
6 | 30 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9422 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.38 | 0 | 9100.38 | 142227 | 0 | 57 | 63 | 142227 | -1000000
6 | 30 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.562 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.21 | 0 | 9100.21 | 141176 | 0 | 57 | 61 | 141176 | -1000000
6 | 30 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7254 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100.11 | 0 | 9100.11 | 139889 | 0 | 54 | 57 | 139889 | -1000000
6 | 30 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.1051 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10101.6 | 0 | 10101.6 | 142652 | 0 | 52 | 54 | 142652 | -1000000
6 | 30 | 5 | 5 | 24.1092 | 0 | 69.9783 | 0 | 11.3338 | 0 | 5.5431 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12330.9 | 0 | 12330.9 | 236760 | 0 | 52 | 54 | 236760 | -1000000
6 | 30 | 6 | 5 | 45.8613 | 0 | 140.608 | 0 | 28.2254 | 0 | 6.332 | 20.2605 | 0 | 0 | 0 | 0 | 241.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33330.5 | 0 | 33330.5 | 565727 | -9699.37 | 52 | 54 | 565727 | -1009699.37
6 | 30 | 7 | 5 | 39.5955 | 0 | 168.222 | 0 | 34.0034 | 0 | 8.5064 | 20.0815 | 0 | 0 | 0 | 0 | 270.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36558 | 0 | 36558 | 654814 | -31442.6 | 53 | 54 | 654814 | -1031442.6
6 | 30 | 8 | 5 | 39.9137 | 0 | 173.795 | 0 | 35.2519 | 0 | 25.335 | 20.3284 | 0 | 0 | 0 | 0 | 294.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46266.8 | 0 | 46266.8 | 673680 | -31832.9 | 53 | 55 | 673680 | -1031832.9
6 | 30 | 9 | 5 | 41.5828 | 0 | 172.186 | 0 | 36.7557 | 0 | 25.335 | 20.3312 | 0 | 0 | 0 | 0 | 296.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72114.9 | 0 | 72114.9 | 698034 | -30869.4 | 54 | 56 | 698034 | -1030869.4
6 | 30 | 10 | 5 | 41.5499 | 0 | 163.102 | 0 | 39.7959 | 0 | 25.335 | 20.5257 | 0 | 0 | 0 | 0 | 290.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.3 | 0 | 73731.3 | 753459 | -26170.1 | 56 | 59 | 753459 | -1026170.1
6 | 30 | 11 | 5 | 40.7709 | 0 | 149.692 | 0 | 35.8226 | 0 | 25.335 | 20.5732 | 0 | 0 | 0 | 0 | 272.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73731.8 | 0 | 73731.8 | 671402 | -24440.3 | 55 | 57 | 671402 | -1024440.3
6 | 30 | 12 | 5 | 39.7779 | 0 | 150.207 | 0 | 36.6874 | 0 | 25.335 | 20.8018 | 0 | 0 | 0 | 0 | 272.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.2 | 0 | 73732.2 | 687075 | -21287.7 | 56 | 58 | 687075 | -1021287.7
6 | 30 | 13 | 5 | 41.2526 | 0 | 165.698 | 0 | 42.8807 | 0 | 25.335 | 21.3856 | 0 | 0 | 0 | 0 | 296.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73732.9 | 0 | 73732.9 | 803536 | -24396.7 | 57 | 60 | 803536 | -1024396.7
6 | 30 | 14 | 5 | 40.6762 | 0 | 172.702 | 0 | 44.658 | 0 | 25.335 | 22.1427 | 0 | 0 | 0 | 0 | 305.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72117.8 | 0 | 72117.8 | 825812 | -25780.7 | 56 | 61 | 825812 | -1025780.7
6 | 30 | 15 | 5 | 40.7032 | 0 | 173.986 | 0 | 48.2222 | 0 | 25.335 | 22.3535 | 0 | 0 | 0 | 0 | 310.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65655.8 | 0 | 65655.8 | 885368 | -26124.4 | 57 | 62 | 885368 | -1026124.4
6 | 30 | 16 | 5 | 40.7613 | 0 | 169.782 | 0 | 46.4358 | 0 | 25.335 | 21.531 | 0 | 0 | 0 | 0 | 303.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54347.7 | 0 | 54347.7 | 869102 | -25532.8 | 57 | 62 | 869102 | -1025532.8
6 | 30 | 17 | 5 | 35.9717 | 0 | 152.497 | 0 | 41.7424 | 0 | 25.335 | 21.0807 | 0 | 0 | 0 | 0 | 276.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41424.5 | 0 | 41424.5 | 793447 | -22420.3 | 58 | 62 | 793447 | -1022420.3
6 | 30 | 18 | 5 | 24.9575 | 0 | 93.4203 | 0 | 26.154 | 0 | 25.335 | 19.2416 | 0 | 0 | 0 | 0 | 189.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25270.9 | 0 | 25270.9 | 502099 | -19165.3 | 57 | 61 | 502099 | -1019165.3
6 | 30 | 19 | 5 | 19.3466 | 0 | 62.7906 | 0 | 10.6047 | 0 | 9.3024 | 8.818 | 0 | 0 | 0 | 1.2 | 112.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18002.6 | 0 | 18002.6 | 192808 | 0 | 58 | 61 | 192808 | -1000000
6 | 30 | 20 | 5 | 18.0024 | 0 | 54.6418 | 0 | 8.9621 | 0 | 7.7514 | 8.818 | 0 | 0 | 0 | 4 | 102.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17196.9 | 0 | 17196.9 | 172609 | 0 | 57 | 60 | 172609 | -1000000
6 | 30 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.4281 | 0 | 7.4185 | 8.818 | 0 | 0 | 0 | 7.2 | 94.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10723.9 | 0 | 10723.9 | 159247 | 0 | 57 | 60 | 159247 | -1000000
6 | 30 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.7143 | 0 | 7.0096 | 8.818 | 0 | 0 | 0 | 6.4 | 85.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10464.5 | 0 | 10464.5 | 148111 | 0 | 57 | 60 | 148111 | -1000000
6 | 30 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.4718 | 0 | 6.8601 | 8.818 | 0 | 0 | 0 | 5.6 | 81.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.25 | 0 | 9106.25 | 143147 | 0 | 57 | 60 | 143147 | -1000000
6 | 30 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.3802 | 0 | 6.806 | 8.818 | 0 | 0 | 0 | 4.8 | 76.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9106.7 | 0 | 9106.7 | 141285 | 0 | 57 | 60 | 141285 | -1000000
7 | 1 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.3449 | 0 | 6.7854 | 8.818 | 0 | 0 | 0 | 4.8 | 76.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8392.41 | 0 | 8392.41 | 140565 | 0 | 57 | 60 | 140565 | -1000000
7 | 1 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.3034 | 0 | 6.7615 | 8.818 | 0 | 0 | 0 | 4.8 | 76.8099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8393.37 | 0 | 8393.37 | 139695 | 0 | 57 | 60 | 139695 | -1000000
7 | 1 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2591 | 0 | 6.7364 | 8.818 | 0 | 0 | 0 | 4.8 | 76.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8393.91 | 0 | 8393.91 | 138770 | 0 | 56 | 59 | 138770 | -1000000
7 | 1 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2236 | 0 | 6.7163 | 8.818 | 0 | 0 | 0 | 3.2 | 75.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.49 | 0 | 8394.49 | 138030 | 0 | 56 | 59 | 138030 | -1000000
7 | 1 | 5 | 6 | 6.2591 | 0 | 42.7453 | 0 | 7.1863 | 0 | 6.6955 | 8.818 | 0 | 0 | 0 | 1.6 | 73.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.99 | 0 | 8394.99 | 137250 | 0 | 56 | 60 | 137250 | -1000000
7 | 1 | 6 | 6 | 4.994 | 0 | 42.7453 | 0 | 7.1916 | 0 | 6.8214 | 8.818 | 0 | 0 | 0 | 0 | 70.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.54 | 0 | 8395.54 | 136578 | 0 | 56 | 61 | 136578 | -1000000
7 | 1 | 7 | 6 | 4.6118 | 0 | 42.7453 | 0 | 20.9179 | 0 | 6.2748 | 18.8896 | 0 | 0 | 0 | 0 | 93.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.09 | 0 | 8396.09 | 257768 | -19009.2 | 57 | 64 | 257768 | -1019009.2
7 | 1 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 16.6384 | 0 | 21.0405 | 18.8896 | 0 | 0 | 0 | 0 | 104.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.43 | 0 | 8396.43 | 289258 | -13077.3 | 58 | 66 | 289258 | -1013077.3
7 | 1 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 19.3803 | 0 | 25.335 | 18.8896 | 0 | 0 | 0 | 0 | 111.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8406.72 | 0 | 8406.72 | 328282 | -15726.3 | 59 | 69 | 328282 | -1015726.3
7 | 1 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 21.0012 | 0 | 25.335 | 18.8896 | 0 | 0 | 0 | 0 | 113.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8408.27 | 0 | 8408.27 | 358106 | -16102.4 | 60 | 71 | 358106 | -1016102.4
7 | 1 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 22.8214 | 0 | 25.335 | 18.971 | 0 | 0 | 0 | 0 | 115.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8409.52 | 0 | 8409.52 | 392663 | -16341.3 | 61 | 72 | 392663 | -1016341.3
7 | 1 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 24.4942 | 0 | 25.335 | 19.0882 | 0 | 0 | 0 | 0 | 117.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8410.11 | 0 | 8410.11 | 411083 | -16502.7 | 61 | 74 | 411083 | -1016502.7
7 | 1 | 13 | 6 | 5.4689 | 0 | 42.7453 | 0 | 23.6969 | 0 | 25.335 | 19.1564 | 0 | 0 | 0 | 0 | 116.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8410.4 | 0 | 8410.4 | 415717 | -16608.8 | 61 | 73 | 415717 | -1016608.8
7 | 1 | 14 | 6 | 5.4705 | 0 | 42.7453 | 0 | 8.4011 | 0 | 7.6244 | 8.818 | 0 | 0 | 0 | 0 | 73.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8410.79 | 0 | 8410.79 | 132718 | 0 | 61 | 73 | 132718 | -1000000
7 | 1 | 15 | 6 | 5.4722 | 0 | 42.7453 | 0 | 7.7314 | 0 | 7.1157 | 8.818 | 0 | 0 | 0 | 0 | 71.8826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8411.26 | 0 | 8411.26 | 132508 | 0 | 61 | 72 | 132508 | -1000000
7 | 1 | 16 | 6 | 5.4714 | 0 | 42.7453 | 0 | 7.9763 | 0 | 7.3064 | 8.818 | 0 | 0 | 0 | 0 | 72.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8405.33 | 0 | 8405.33 | 132194 | 0 | 61 | 72 | 132194 | -1000000
7 | 1 | 17 | 6 | 5.4733 | 0 | 42.7453 | 0 | 7.5341 | 0 | 7.0029 | 8.818 | 0 | 0 | 0 | 0 | 71.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8402.2 | 0 | 8402.2 | 131826 | 0 | 60 | 71 | 131826 | -1000000
7 | 1 | 18 | 6 | 5.836 | 0 | 42.7453 | 0 | 7.78 | 0 | 7.187 | 8.818 | 0 | 0 | 0 | 0 | 72.3662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8400.11 | 0 | 8400.11 | 131628 | 0 | 60 | 71 | 131628 | -1000000
7 | 1 | 19 | 6 | 6.9164 | 0 | 42.7453 | 0 | 6.9796 | 0 | 6.6715 | 8.818 | 0 | 0 | 0 | 1.2 | 73.3307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8398.39 | 0 | 8398.39 | 131302 | 0 | 59 | 69 | 131302 | -1000000
7 | 1 | 20 | 6 | 8.5513 | 0 | 42.7453 | 0 | 6.5284 | 0 | 6.3858 | 8.818 | 0 | 0 | 0 | 4 | 77.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8397.22 | 0 | 8397.22 | 130836 | 0 | 57 | 66 | 130836 | -1000000
7 | 1 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.1944 | 0 | 6.353 | 8.818 | 0 | 0 | 0 | 7.2 | 80.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.37 | 0 | 8396.37 | 130591 | 0 | 56 | 64 | 130591 | -1000000
7 | 1 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3905 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.89 | 0 | 8395.89 | 130356 | 0 | 56 | 63 | 130356 | -1000000
7 | 1 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3359 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 5.6 | 77.7812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.72 | 0 | 8395.72 | 129915 | 0 | 55 | 62 | 129915 | -1000000
7 | 1 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.6493 | 0 | 6.4166 | 8.818 | 0 | 0 | 0 | 4.8 | 74.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.44 | 0 | 3242.44 | 129657 | 0 | 55 | 61 | 129657 | -1000000
7 | 2 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5908 | 0 | 6.3715 | 8.818 | 0 | 0 | 0 | 4.8 | 74.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.56 | 0 | 3242.56 | 129165 | 0 | 54 | 60 | 129165 | -1000000
7 | 2 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.846 | 0 | 6.4945 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.94 | 0 | 3242.94 | 128837 | 0 | 53 | 59 | 128837 | -1000000
7 | 2 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8353 | 0 | 6.4891 | 8.818 | 0 | 0 | 0 | 4.8 | 74.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3243.32 | 0 | 3243.32 | 128617 | 0 | 53 | 58 | 128617 | -1000000
7 | 2 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8149 | 0 | 6.479 | 8.818 | 0 | 0 | 0 | 3.2 | 73.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3243.78 | 0 | 3243.78 | 128191 | 0 | 52 | 57 | 128191 | -1000000
7 | 2 | 5 | 7 | 5.0624 | 0 | 42.7453 | 0 | 6.7984 | 0 | 6.4709 | 8.818 | 0 | 0 | 0 | 1.6 | 71.4949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.29 | 0 | 3244.29 | 127851 | 0 | 51 | 57 | 127851 | -1000000
7 | 2 | 6 | 7 | 4.5631 | 0 | 42.7453 | 0 | 6.9329 | 0 | 6.4911 | 8.818 | 0 | 0 | 0 | 0 | 69.5503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.87 | 0 | 3244.87 | 127588 | 0 | 50 | 56 | 127588 | -1000000
7 | 2 | 7 | 7 | 3.7164 | 0 | 42.7453 | 0 | 6.4144 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 0 | 67.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.53 | 0 | 3245.53 | 127489 | 0 | 51 | 57 | 127489 | -1000000
7 | 2 | 8 | 7 | 3.9532 | 0 | 42.7453 | 0 | 6.4581 | 0 | 6.4008 | 8.818 | 0 | 0 | 0 | 0 | 68.3754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.17 | 0 | 3246.17 | 127111 | 0 | 51 | 59 | 127111 | -1000000
7 | 2 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.6486 | 0 | 6.4331 | 8.818 | 0 | 0 | 0 | 0 | 68.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.77 | 0 | 3246.77 | 127099 | 0 | 52 | 60 | 127099 | -1000000
7 | 2 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.1538 | 0 | 6.6424 | 8.818 | 0 | 0 | 0 | 0 | 69.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.81 | 0 | 3246.81 | 126798 | 0 | 52 | 61 | 126798 | -1000000
7 | 2 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.4247 | 0 | 6.7324 | 8.818 | 0 | 0 | 0 | 0 | 69.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.64 | 0 | 3246.64 | 126762 | 0 | 53 | 62 | 126762 | -1000000
7 | 2 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.474 | 0 | 6.7755 | 8.818 | 0 | 0 | 0 | 0 | 69.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.03 | 0 | 3246.03 | 126496 | 0 | 53 | 63 | 126496 | -1000000
7 | 2 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.2994 | 0 | 8.1375 | 12.8287 | 0 | 0 | 0 | 0 | 77.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.3 | 0 | 3245.3 | 154266 | 0 | 54 | 65 | 154266 | -1000000
7 | 2 | 14 | 7 | 4.1468 | 0 | 42.7453 | 0 | 8.004 | 0 | 7.1944 | 8.818 | 0 | 0 | 0 | 0 | 70.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.34 | 0 | 3244.34 | 126395 | 0 | 55 | 67 | 126395 | -1000000
7 | 2 | 15 | 7 | 4.1464 | 0 | 42.7453 | 0 | 9.9814 | 0 | 9.0023 | 12.8287 | 0 | 0 | 0 | 0 | 78.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3243.82 | 0 | 3243.82 | 162933 | 0 | 55 | 69 | 162933 | -1000000
7 | 2 | 16 | 7 | 4.1469 | 0 | 42.7453 | 0 | 7.4715 | 0 | 6.9144 | 8.818 | 0 | 0 | 0 | 0 | 70.0961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.96 | 0 | 3242.96 | 126266 | 0 | 55 | 69 | 126266 | -1000000
7 | 2 | 17 | 7 | 4.1478 | 0 | 42.7453 | 0 | 7.0337 | 0 | 6.6579 | 8.818 | 0 | 0 | 0 | 0 | 69.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.19 | 0 | 3242.19 | 126267 | 0 | 55 | 68 | 126267 | -1000000
7 | 2 | 18 | 7 | 4.1483 | 0 | 42.7453 | 0 | 7.2714 | 0 | 6.8137 | 8.818 | 0 | 0 | 0 | 0 | 69.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3241.36 | 0 | 3241.36 | 126221 | 0 | 55 | 68 | 126221 | -1000000
7 | 2 | 19 | 7 | 5.1671 | 0 | 42.7453 | 0 | 6.2329 | 0 | 6.2413 | 8.818 | 0 | 0 | 0 | 1.2 | 70.4045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3240.62 | 0 | 3240.62 | 126147 | 0 | 54 | 65 | 126147 | -1000000
7 | 2 | 20 | 7 | 6.156 | 0 | 42.7453 | 0 | 5.5196 | 0 | 5.9898 | 8.818 | 0 | 0 | 0 | 4 | 73.2286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3240.15 | 0 | 3240.15 | 126247 | 0 | 54 | 61 | 126247 | -1000000
7 | 2 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0813 | 0 | 5.5036 | 8.818 | 0 | 0 | 0 | 7.2 | 77.0115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.82 | 0 | 3239.82 | 125808 | 0 | 52 | 58 | 125808 | -1000000
7 | 2 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3425 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 6.4 | 76.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.76 | 0 | 3239.76 | 125919 | 0 | 52 | 56 | 125919 | -1000000
7 | 2 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.336 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 5.6 | 75.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3240.03 | 0 | 3240.03 | 125771 | 0 | 52 | 54 | 125771 | -1000000
7 | 2 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 7.4354 | 0 | 5.4787 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8393.84 | 0 | 8393.84 | 150243 | 0 | 51 | 52 | 150243 | -1000000
7 | 3 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3434 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.12 | 0 | 8394.12 | 125524 | 0 | 50 | 51 | 125524 | -1000000
7 | 3 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.322 | 0 | 5.4857 | 8.818 | 0 | 0 | 0 | 4.8 | 78.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.06 | 0 | 8394.06 | 125466 | 0 | 50 | 50 | 125466 | -1000000
7 | 3 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3087 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.66 | 0 | 8394.66 | 125171 | 0 | 49 | 49 | 125171 | -1000000
7 | 3 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.4714 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 3.2 | 80.6179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9308.17 | 0 | 9308.17 | 128797 | 0 | 50 | 50 | 128797 | -1000000
7 | 3 | 5 | 1 | 23.8468 | 0 | 69.9783 | 0 | 11.9462 | 0 | 5.9293 | 12.8287 | 0 | 0 | 0 | 1.6 | 126.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11340.9 | 0 | 11340.9 | 191167 | -6481.01 | 51 | 52 | 191167 | -1006481.01
7 | 3 | 6 | 1 | 37.4152 | 0 | 140.608 | 0 | 25.8032 | 0 | 6.332 | 19.7889 | 0 | 0 | 0 | 0 | 229.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30482.8 | 0 | 30482.8 | 409542 | -26380.5 | 52 | 53 | 409542 | -1026380.5
7 | 3 | 7 | 1 | 38.9069 | 0 | 168.222 | 0 | 38.5002 | 0 | 6.332 | 19.8305 | 0 | 0 | 0 | 0 | 271.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33424.6 | 0 | 33424.6 | 601378 | -23332 | 55 | 57 | 601378 | -1023332
7 | 3 | 8 | 1 | 39.6631 | 0 | 173.795 | 0 | 45.8017 | 0 | 6.332 | 20.0688 | 0 | 0 | 0 | 0 | 285.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42270.1 | 0 | 42270.1 | 741258 | -16632.1 | 57 | 62 | 741258 | -1016632.1
7 | 3 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 52.0929 | 0 | 6.332 | 20.4762 | 0 | 0 | 0 | 0 | 291.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65829.9 | 0 | 65829.9 | 856483 | -14502.2 | 59 | 66 | 856483 | -1014502.2
7 | 3 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 52.0179 | 0 | 6.332 | 20.9037 | 0 | 0 | 0 | 0 | 283.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67304.4 | 0 | 67304.4 | 876602 | -11762.1 | 59 | 68 | 876602 | -1011762.1
7 | 3 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 48.5679 | 0 | 6.332 | 21.6047 | 0 | 0 | 0 | 0 | 266.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67305.5 | 0 | 67305.5 | 819105 | -8095.66 | 59 | 71 | 819105 | -1008095.66
7 | 3 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 52.3188 | 0 | 6.7962 | 21.6534 | 0 | 0 | 0 | 0 | 270.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67305.6 | 0 | 67305.6 | 872729 | -15302.4 | 59 | 73 | 872729 | -1015302.4
7 | 3 | 13 | 1 | 41.233 | 0 | 165.698 | 0 | 57.0618 | 0 | 19.1515 | 22.6727 | 0 | 0 | 0 | 0 | 305.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67305.6 | 0 | 67305.6 | 977999 | -9080.59 | 60 | 74 | 977999 | -1009080.59
7 | 3 | 14 | 1 | 40.6259 | 0 | 172.702 | 0 | 64.3779 | 0 | 14.2144 | 22.6321 | 0 | 0 | 0 | 0 | 314.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65832.7 | 0 | 65832.7 | 1080340 | -12027.3 | 61 | 76 | 1080340 | -1012027.3
7 | 3 | 15 | 1 | 40.5193 | 0 | 173.986 | 0 | 67.2303 | 0 | 19.4949 | 22.8523 | 0 | 0 | 0 | 0 | 324.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59942.4 | 0 | 59942.4 | 1131410 | -13624.7 | 61 | 77 | 1131410 | -1013624.7
7 | 3 | 16 | 1 | 40.2771 | 0 | 169.782 | 0 | 66.266 | 0 | 25.335 | 22.7127 | 0 | 0 | 0 | 0 | 324.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49635.1 | 0 | 49635.1 | 1129870 | -18141.8 | 61 | 76 | 1129870 | -1018141.8
7 | 3 | 17 | 1 | 35.4634 | 0 | 152.497 | 0 | 59.7169 | 0 | 25.335 | 22.4488 | 0 | 0 | 0 | 0 | 295.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37855.3 | 0 | 37855.3 | 1046370 | -18800.5 | 61 | 76 | 1046370 | -1018800.5
7 | 3 | 18 | 1 | 24.5827 | 0 | 93.4203 | 0 | 41.6115 | 0 | 25.335 | 20.5415 | 0 | 0 | 0 | 0 | 205.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23130.5 | 0 | 23130.5 | 734795 | -17002.4 | 61 | 75 | 734795 | -1017002.4
7 | 3 | 19 | 1 | 17.9442 | 0 | 62.7906 | 0 | 9.5865 | 0 | 9.0835 | 8.818 | 0 | 0 | 0 | 1.2 | 109.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16504.5 | 0 | 16504.5 | 188303 | 0 | 61 | 71 | 188303 | -1000000
7 | 3 | 20 | 1 | 17.3199 | 0 | 54.6418 | 0 | 7.8609 | 0 | 5.9774 | 8.818 | 0 | 0 | 0 | 4 | 98.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15769.7 | 0 | 15769.7 | 168250 | 0 | 60 | 68 | 168250 | -1000000
7 | 3 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 6.8049 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 91.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.49 | 0 | 9867.49 | 155108 | 0 | 59 | 64 | 155108 | -1000000
7 | 3 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.3435 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9629.74 | 0 | 9629.74 | 144227 | 0 | 59 | 64 | 144227 | -1000000
7 | 3 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.118 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8391.03 | 0 | 8391.03 | 139498 | 0 | 59 | 64 | 139498 | -1000000
7 | 3 | 24 | 1 | 5.1054 | 0 | 42.7453 | 0 | 7.444 | 0 | 6.9178 | 8.818 | 0 | 0 | 0 | 4.8 | 75.8305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.65 | 0 | 3237.65 | 137931 | 0 | 60 | 64 | 137931 | -1000000
7 | 4 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 7.3926 | 0 | 6.886 | 8.818 | 0 | 0 | 0 | 4.8 | 75.7472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.61 | 0 | 3237.61 | 136897 | 0 | 59 | 64 | 136897 | -1000000
7 | 4 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 7.3607 | 0 | 6.8665 | 8.818 | 0 | 0 | 0 | 4.8 | 75.6958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.39 | 0 | 3238.39 | 136258 | 0 | 59 | 64 | 136258 | -1000000
7 | 4 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 7.3288 | 0 | 6.8471 | 8.818 | 0 | 0 | 0 | 4.8 | 75.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.67 | 0 | 3238.67 | 135611 | 0 | 59 | 64 | 135611 | -1000000
7 | 4 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 7.2991 | 0 | 6.8293 | 8.818 | 0 | 0 | 0 | 3.2 | 73.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.96 | 0 | 3238.96 | 135011 | 0 | 59 | 64 | 135011 | -1000000
7 | 4 | 5 | 8 | 5.058 | 0 | 42.7453 | 0 | 7.5877 | 0 | 7.0364 | 8.818 | 0 | 0 | 0 | 1.6 | 72.8454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.16 | 0 | 3239.16 | 134399 | 0 | 59 | 65 | 134399 | -1000000
7 | 4 | 6 | 8 | 4.0337 | 0 | 42.7453 | 0 | 7.4508 | 0 | 6.8855 | 8.818 | 0 | 0 | 0 | 0 | 69.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.35 | 0 | 3239.35 | 134075 | 0 | 60 | 65 | 134075 | -1000000
7 | 4 | 7 | 8 | 3.7033 | 0 | 42.7453 | 0 | 7.8048 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 0 | 68.5563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.52 | 0 | 3239.52 | 133713 | 0 | 62 | 68 | 133713 | -1000000
7 | 4 | 8 | 8 | 3.7847 | 0 | 42.7453 | 0 | 7.9949 | 0 | 7.7141 | 8.818 | 0 | 0 | 0 | 0 | 71.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.59 | 0 | 3239.59 | 133267 | 0 | 63 | 71 | 133267 | -1000000
7 | 4 | 9 | 8 | 4.144 | 0 | 42.7453 | 0 | 8.3618 | 0 | 8.03 | 8.818 | 0 | 0 | 0 | 0 | 72.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.94 | 0 | 3238.94 | 132917 | 0 | 64 | 74 | 132917 | -1000000
7 | 4 | 10 | 8 | 4.144 | 0 | 42.7453 | 0 | 10.9954 | 0 | 11.0919 | 12.8287 | 0 | 0 | 0 | 0 | 81.8052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.66 | 0 | 3237.66 | 188663 | 0 | 65 | 75 | 188663 | -1000000
7 | 4 | 11 | 8 | 4.144 | 0 | 42.7453 | 0 | 11.4795 | 0 | 11.5029 | 12.8287 | 0 | 0 | 0 | 0 | 82.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3235.71 | 0 | 3235.71 | 195811 | 0 | 66 | 77 | 195811 | -1000000
7 | 4 | 12 | 8 | 4.144 | 0 | 42.7453 | 0 | 11.8224 | 0 | 12.0214 | 12.8287 | 0 | 0 | 0 | 0 | 83.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3233.58 | 0 | 3233.58 | 201371 | 0 | 67 | 78 | 201371 | -1000000
7 | 4 | 13 | 8 | 4.1445 | 0 | 42.7453 | 0 | 12.142 | 0 | 12.5256 | 12.8287 | 0 | 0 | 0 | 0 | 84.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3231.75 | 0 | 3231.75 | 206493 | 0 | 67 | 80 | 206493 | -1000000
7 | 4 | 14 | 8 | 4.1467 | 0 | 42.7453 | 0 | 12.3603 | 0 | 12.8704 | 12.8287 | 0 | 0 | 0 | 0 | 84.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3229.95 | 0 | 3229.95 | 209735 | 0 | 68 | 81 | 209735 | -1000000
7 | 4 | 15 | 8 | 4.1477 | 0 | 42.7453 | 0 | 15.1597 | 0 | 19.0881 | 14.8767 | 0 | 0 | 0 | 0 | 96.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.39 | 0 | 3228.39 | 261405 | 0 | 68 | 83 | 261405 | -1000000
7 | 4 | 16 | 8 | 4.1474 | 0 | 42.7453 | 0 | 15.2225 | 0 | 19.2936 | 14.8767 | 0 | 0 | 0 | 0 | 96.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3226.65 | 0 | 3226.65 | 262104 | 0 | 68 | 82 | 262104 | -1000000
7 | 4 | 17 | 8 | 4.1475 | 0 | 42.7453 | 0 | 10.8956 | 0 | 10.6589 | 10.866 | 0 | 0 | 0 | 0 | 79.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.94 | 0 | 3224.94 | 184381 | 0 | 67 | 82 | 184381 | -1000000
7 | 4 | 18 | 8 | 4.1484 | 0 | 42.7453 | 0 | 15.1761 | 0 | 19.5846 | 14.8767 | 0 | 0 | 0 | 0 | 96.5311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3223.29 | 0 | 3223.29 | 267235 | 0 | 67 | 81 | 267235 | -1000000
7 | 4 | 19 | 8 | 5.036 | 0 | 42.7453 | 0 | 12.2212 | 0 | 12.9859 | 12.8287 | 0 | 0 | 0 | 1.2 | 87.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3221.74 | 0 | 3221.74 | 212333 | 0 | 66 | 77 | 212333 | -1000000
7 | 4 | 20 | 8 | 6.1972 | 0 | 42.7453 | 0 | 6.4499 | 0 | 6.5771 | 8.818 | 0 | 0 | 0 | 4 | 74.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.27 | 0 | 3220.27 | 130743 | 0 | 66 | 72 | 130743 | -1000000
7 | 4 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.7585 | 0 | 5.4935 | 8.818 | 0 | 0 | 0 | 7.2 | 76.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3219.08 | 0 | 3219.08 | 130153 | 0 | 64 | 68 | 130153 | -1000000
7 | 4 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.2101 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 6.4 | 76.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3218.21 | 0 | 3218.21 | 129880 | 0 | 62 | 66 | 129880 | -1000000
7 | 4 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.8357 | 0 | 5.4908 | 8.818 | 0 | 0 | 0 | 5.6 | 75.1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3217.68 | 0 | 3217.68 | 129636 | 0 | 60 | 63 | 129636 | -1000000
7 | 4 | 24 | 8 | 10.8489 | 0 | 42.3304 | 0 | 6.4369 | 0 | 6.3008 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.88 | 0 | 8370.88 | 129688 | 0 | 59 | 61 | 129688 | -1000000
7 | 5 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.662 | 0 | 6.3866 | 8.818 | 0 | 0 | 0 | 4.8 | 79.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.89 | 0 | 8370.89 | 129379 | 0 | 58 | 60 | 129379 | -1000000
7 | 5 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9203 | 0 | 6.5114 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.26 | 0 | 8370.26 | 129061 | 0 | 57 | 59 | 129061 | -1000000
7 | 5 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9105 | 0 | 6.5066 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.22 | 0 | 8370.22 | 128863 | 0 | 57 | 58 | 128863 | -1000000
7 | 5 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.0859 | 0 | 6.5962 | 8.818 | 0 | 0 | 0 | 3.2 | 82.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9283.15 | 0 | 9283.15 | 132525 | 0 | 58 | 59 | 132525 | -1000000
7 | 5 | 5 | 3 | 23.8878 | 0 | 69.9783 | 0 | 12.5823 | 0 | 12.1903 | 12.8287 | 0 | 0 | 0 | 1.6 | 133.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11315.2 | 0 | 11315.2 | 240085 | 0 | 59 | 61 | 240085 | -1000000
7 | 5 | 6 | 3 | 38.1574 | 0 | 140.608 | 0 | 58.9945 | 0 | 6.332 | 21.5055 | 0 | 0 | 0 | 0 | 265.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30456.6 | 0 | 30456.6 | 993689 | -11292.4 | 59 | 62 | 993689 | -1011292.4
7 | 5 | 7 | 3 | 39.0502 | 0 | 168.222 | 0 | 62.7332 | 0 | 6.332 | 21.4356 | 0 | 0 | 0 | 0 | 297.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33397.7 | 0 | 33397.7 | 1060290 | -21230.3 | 61 | 65 | 1060290 | -1021230.3
7 | 5 | 8 | 3 | 39.7278 | 0 | 173.795 | 0 | 62.3714 | 0 | 7.6417 | 21.5038 | 0 | 0 | 0 | 0 | 305.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42255.9 | 0 | 42255.9 | 1089970 | -15608.2 | 62 | 68 | 1089970 | -1015608.2
7 | 5 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 66.2312 | 0 | 7.4228 | 21.7963 | 0 | 0 | 0 | 0 | 308.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65820 | 0 | 65820 | 1140650 | -16109.8 | 63 | 71 | 1140650 | -1016109.8
7 | 5 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 66.0798 | 0 | 6.332 | 22.1202 | 0 | 0 | 0 | 0 | 298.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67294.9 | 0 | 67294.9 | 1148360 | -13118.6 | 63 | 74 | 1148360 | -1013118.6
7 | 5 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 59.0278 | 0 | 6.332 | 22.8754 | 0 | 0 | 0 | 0 | 278.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.2 | 0 | 67296.2 | 1059130 | -9500.5 | 63 | 76 | 1059130 | -1009500.5
7 | 5 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 64.542 | 0 | 6.332 | 22.5063 | 0 | 0 | 0 | 0 | 283.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.9 | 0 | 67296.9 | 1128030 | -22053.4 | 63 | 79 | 1128030 | -1022053.4
7 | 5 | 13 | 3 | 41.241 | 0 | 165.698 | 0 | 65.7719 | 0 | 6.332 | 23.8345 | 0 | 0 | 0 | 0 | 302.877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.1 | 0 | 67297.1 | 1199820 | -10402 | 63 | 80 | 1199820 | -1010402
7 | 5 | 14 | 3 | 40.663 | 0 | 172.702 | 0 | 68.5496 | 0 | 6.332 | 23.418 | 0 | 0 | 0 | 0 | 311.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65824.7 | 0 | 65824.7 | 1211660 | -14331.1 | 62 | 80 | 1211660 | -1014331.1
7 | 5 | 15 | 3 | 40.5567 | 0 | 173.986 | 0 | 72.6707 | 0 | 9.1726 | 23.4435 | 0 | 0 | 0 | 0 | 319.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59935.2 | 0 | 59935.2 | 1264020 | -18057.5 | 62 | 81 | 1264020 | -1018057.5
7 | 5 | 16 | 3 | 40.2987 | 0 | 169.782 | 0 | 72.6972 | 0 | 25.335 | 23.0673 | 0 | 0 | 0 | 0 | 331.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49628 | 0 | 49628 | 1266580 | -27651.4 | 62 | 80 | 1266580 | -1027651.4
7 | 5 | 17 | 3 | 35.4682 | 0 | 152.497 | 0 | 68.5767 | 0 | 12.3068 | 22.7368 | 0 | 0 | 0 | 0 | 291.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37848.4 | 0 | 37848.4 | 1184090 | -30741.9 | 62 | 80 | 1184090 | -1030741.9
7 | 5 | 18 | 3 | 24.5808 | 0 | 93.4203 | 0 | 48.9496 | 0 | 6.332 | 21.2472 | 0 | 0 | 0 | 0 | 194.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23124 | 0 | 23124 | 837068 | -31670.3 | 61 | 79 | 837068 | -1031670.3
7 | 5 | 19 | 3 | 18.308 | 0 | 62.7906 | 0 | 10.6509 | 0 | 5.5513 | 8.818 | 0 | 0 | 0 | 1.2 | 107.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16498.4 | 0 | 16498.4 | 190290 | 0 | 61 | 75 | 190290 | -1000000
7 | 5 | 20 | 3 | 17.2801 | 0 | 54.6418 | 0 | 7.5112 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4 | 97.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15762.9 | 0 | 15762.9 | 170333 | 0 | 61 | 70 | 170333 | -1000000
7 | 5 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 6.9617 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 7.2 | 91.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.13 | 0 | 9859.13 | 156808 | 0 | 59 | 66 | 156808 | -1000000
7 | 5 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 6.9031 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9620.43 | 0 | 9620.43 | 146022 | 0 | 59 | 64 | 146022 | -1000000
7 | 5 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.6028 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 5.6 | 79.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.15 | 0 | 8381.15 | 141238 | 0 | 59 | 62 | 141238 | -1000000
7 | 5 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.458 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.67 | 0 | 8380.67 | 139644 | 0 | 58 | 60 | 139644 | -1000000
7 | 6 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9263 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.05 | 0 | 8380.05 | 138677 | 0 | 57 | 59 | 138677 | -1000000
7 | 6 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8868 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.89 | 0 | 8379.89 | 137814 | 0 | 56 | 58 | 137814 | -1000000
7 | 6 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8513 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.94 | 0 | 8379.94 | 137038 | 0 | 55 | 57 | 137038 | -1000000
7 | 6 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0035 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 3.2 | 81.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9293.02 | 0 | 9293.02 | 140440 | 0 | 57 | 58 | 140440 | -1000000
7 | 6 | 5 | 4 | 23.8806 | 0 | 69.9783 | 0 | 11.7747 | 0 | 5.5591 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11325.2 | 0 | 11325.2 | 246619 | 0 | 58 | 59 | 246619 | -1000000
7 | 6 | 6 | 4 | 37.8134 | 0 | 140.608 | 0 | 42.0629 | 0 | 6.332 | 21.3895 | 0 | 0 | 0 | 0 | 248.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30466.6 | 0 | 30466.6 | 810449 | -8875.61 | 59 | 60 | 810449 | -1008875.61
7 | 6 | 7 | 4 | 38.9784 | 0 | 168.222 | 0 | 56.2885 | 0 | 25.335 | 21.165 | 0 | 0 | 0 | 0 | 309.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33407.9 | 0 | 33407.9 | 990411 | -22323.2 | 61 | 64 | 990411 | -1022323.2
7 | 6 | 8 | 4 | 39.6631 | 0 | 173.795 | 0 | 62.9299 | 0 | 25.335 | 21.1711 | 0 | 0 | 0 | 0 | 322.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42261 | 0 | 42261 | 1089910 | -20447.2 | 63 | 69 | 1089910 | -1020447.2
7 | 6 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 68.2634 | 0 | 25.335 | 21.5482 | 0 | 0 | 0 | 0 | 327.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65824 | 0 | 65824 | 1158930 | -19373.7 | 64 | 73 | 1158930 | -1019373.7
7 | 6 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 74.1374 | 0 | 25.335 | 21.8993 | 0 | 0 | 0 | 0 | 325.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.1 | 0 | 67299.1 | 1253140 | -15731.3 | 66 | 76 | 1253140 | -1015731.3
7 | 6 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 69.9061 | 0 | 25.335 | 22.5775 | 0 | 0 | 0 | 0 | 308.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.4 | 0 | 67300.4 | 1190570 | -11269.3 | 67 | 80 | 1190570 | -1011269.3
7 | 6 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 79.5795 | 0 | 25.335 | 22.4932 | 0 | 0 | 0 | 0 | 317.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67301 | 0 | 67301 | 1344310 | -21379.5 | 69 | 83 | 1344310 | -1021379.5
7 | 6 | 13 | 4 | 41.2364 | 0 | 165.698 | 0 | 83.042 | 0 | 25.335 | 23.7691 | 0 | 0 | 0 | 0 | 339.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67301 | 0 | 67301 | 1392180 | -12183.3 | 68 | 83 | 1392180 | -1012183.3
7 | 6 | 14 | 4 | 40.6354 | 0 | 172.702 | 0 | 86.3888 | 0 | 25.335 | 23.3317 | 0 | 0 | 0 | 0 | 348.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65828.4 | 0 | 65828.4 | 1441460 | -18156.7 | 68 | 84 | 1441460 | -1018156.7
7 | 6 | 15 | 4 | 40.52 | 0 | 173.986 | 0 | 89.7017 | 0 | 25.335 | 23.2821 | 0 | 0 | 0 | 0 | 352.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59938.7 | 0 | 59938.7 | 1496340 | -24520.7 | 68 | 84 | 1496340 | -1024520.7
7 | 6 | 16 | 4 | 40.2829 | 0 | 169.782 | 0 | 88.1394 | 0 | 25.335 | 23.3067 | 0 | 0 | 0 | 0 | 346.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49631.4 | 0 | 49631.4 | 1487850 | -27441.2 | 68 | 83 | 1487850 | -1027441.2
7 | 6 | 17 | 4 | 35.472 | 0 | 152.497 | 0 | 81.0625 | 0 | 25.335 | 23.1776 | 0 | 0 | 0 | 0 | 317.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37851.7 | 0 | 37851.7 | 1384220 | -24056 | 68 | 81 | 1384220 | -1024056
7 | 6 | 18 | 4 | 24.8197 | 0 | 93.4203 | 0 | 56.3725 | 0 | 25.335 | 21.8378 | 0 | 0 | 0 | 0 | 221.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127.3 | 0 | 23127.3 | 977945 | -19193.2 | 68 | 80 | 977945 | -1019193.2
7 | 6 | 19 | 4 | 18.8333 | 0 | 62.7906 | 0 | 11.9648 | 0 | 12.4492 | 8.818 | 0 | 0 | 0 | 1.2 | 116.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16501.5 | 0 | 16501.5 | 194098 | 0 | 67 | 78 | 194098 | -1000000
7 | 6 | 20 | 4 | 18.3419 | 0 | 54.6418 | 0 | 10.097 | 0 | 9.7267 | 8.818 | 0 | 0 | 0 | 4 | 105.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15765.7 | 0 | 15765.7 | 173870 | 0 | 66 | 76 | 173870 | -1000000
7 | 6 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 8.3635 | 0 | 8.1973 | 8.818 | 0 | 0 | 0 | 7.2 | 95.299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.06 | 0 | 9862.06 | 160501 | 0 | 65 | 74 | 160501 | -1000000
7 | 6 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.395 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9623.15 | 0 | 9623.15 | 149424 | 0 | 64 | 72 | 149424 | -1000000
7 | 6 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0594 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.55 | 0 | 8383.55 | 144385 | 0 | 63 | 70 | 144385 | -1000000
7 | 6 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.897 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.55 | 0 | 8382.55 | 142751 | 0 | 62 | 68 | 142751 | -1000000
7 | 7 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.39 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.8 | 0 | 8381.8 | 141861 | 0 | 62 | 68 | 141861 | -1000000
7 | 7 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0425 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.21 | 0 | 8381.21 | 141046 | 0 | 62 | 67 | 141046 | -1000000
7 | 7 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2703 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.74 | 0 | 8380.74 | 140231 | 0 | 62 | 67 | 140231 | -1000000
7 | 7 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.122 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9293.18 | 0 | 9293.18 | 143644 | 0 | 63 | 66 | 143644 | -1000000
7 | 7 | 5 | 5 | 24.2227 | 0 | 69.9783 | 0 | 13.4033 | 0 | 5.6585 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11324.7 | 0 | 11324.7 | 273273 | 0 | 63 | 66 | 273273 | -1000000
7 | 7 | 6 | 5 | 46.6628 | 0 | 140.608 | 0 | 58.7947 | 0 | 25.335 | 22.8312 | 0 | 0 | 0 | 0 | 294.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30465.4 | 0 | 30465.4 | 1109420 | -5842.01 | 64 | 65 | 1109420 | -1005842.01
7 | 7 | 7 | 5 | 39.4132 | 0 | 168.222 | 0 | 64.5371 | 0 | 25.335 | 22.3311 | 0 | 0 | 0 | 0 | 319.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33406.1 | 0 | 33406.1 | 1170820 | -24342.4 | 64 | 66 | 1170820 | -1024342.4
7 | 7 | 8 | 5 | 39.9371 | 0 | 173.795 | 0 | 62.2568 | 0 | 25.335 | 22.3166 | 0 | 0 | 0 | 0 | 323.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42261.4 | 0 | 42261.4 | 1127620 | -24491.6 | 64 | 66 | 1127620 | -1024491.6
7 | 7 | 9 | 5 | 41.6345 | 0 | 172.186 | 0 | 64.7081 | 0 | 25.335 | 22.4228 | 0 | 0 | 0 | 0 | 326.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65823.5 | 0 | 65823.5 | 1152380 | -24643.3 | 65 | 67 | 1152380 | -1024643.3
7 | 7 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 72.836 | 0 | 25.335 | 22.2748 | 0 | 0 | 0 | 0 | 324.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.7 | 0 | 67296.7 | 1257720 | -21212.7 | 67 | 70 | 1257720 | -1021212.7
7 | 7 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 70.9429 | 0 | 25.335 | 22.6975 | 0 | 0 | 0 | 0 | 309.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.1 | 0 | 67297.1 | 1181640 | -16161.7 | 68 | 74 | 1181640 | -1016161.7
7 | 7 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 79.7099 | 0 | 25.335 | 22.921 | 0 | 0 | 0 | 0 | 317.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.9 | 0 | 67298.9 | 1326830 | -15875.2 | 70 | 77 | 1326830 | -1015875.2
7 | 7 | 13 | 5 | 41.233 | 0 | 165.698 | 0 | 87.0088 | 0 | 25.335 | 23.4898 | 0 | 0 | 0 | 0 | 342.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.7 | 0 | 67299.7 | 1443960 | -17157.8 | 70 | 79 | 1443960 | -1017157.8
7 | 7 | 14 | 5 | 40.6421 | 0 | 172.702 | 0 | 92.3213 | 0 | 25.335 | 23.3814 | 0 | 0 | 0 | 0 | 354.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65827.9 | 0 | 65827.9 | 1533920 | -20853.5 | 71 | 81 | 1533920 | -1020853.5
7 | 7 | 15 | 5 | 40.5404 | 0 | 173.986 | 0 | 95.6646 | 0 | 25.335 | 23.5727 | 0 | 0 | 0 | 0 | 359.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59938.2 | 0 | 59938.2 | 1583560 | -21917.6 | 71 | 83 | 1583560 | -1021917.6
7 | 7 | 16 | 5 | 40.2904 | 0 | 169.782 | 0 | 94.9418 | 0 | 25.335 | 23.6458 | 0 | 0 | 0 | 0 | 353.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49630.9 | 0 | 49630.9 | 1592390 | -23104.4 | 71 | 83 | 1592390 | -1023104.4
7 | 7 | 17 | 5 | 35.4699 | 0 | 152.497 | 0 | 89.0142 | 0 | 25.335 | 23.0374 | 0 | 0 | 0 | 0 | 325.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37851.3 | 0 | 37851.3 | 1495510 | -30571.7 | 70 | 82 | 1495510 | -1030571.7
7 | 7 | 18 | 5 | 24.5872 | 0 | 93.4203 | 0 | 65.3718 | 0 | 25.335 | 21.4887 | 0 | 0 | 0 | 0 | 230.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127 | 0 | 23127 | 1075750 | -32568.1 | 69 | 82 | 1075750 | -1032568.1
7 | 7 | 19 | 5 | 18.7076 | 0 | 62.7906 | 0 | 12.1234 | 0 | 12.7287 | 8.818 | 0 | 0 | 0 | 1.2 | 116.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16501.2 | 0 | 16501.2 | 195407 | 0 | 69 | 79 | 195407 | -1000000
7 | 7 | 20 | 5 | 17.3455 | 0 | 54.6418 | 0 | 10.2493 | 0 | 9.8489 | 8.818 | 0 | 0 | 0 | 4 | 104.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15765.6 | 0 | 15765.6 | 174970 | 0 | 69 | 77 | 174970 | -1000000
7 | 7 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 9.1137 | 0 | 8.5136 | 8.818 | 0 | 0 | 0 | 7.2 | 96.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.89 | 0 | 9861.89 | 161623 | 0 | 68 | 74 | 161623 | -1000000
7 | 7 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 8.2279 | 0 | 7.7807 | 8.818 | 0 | 0 | 0 | 6.4 | 86.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9622.93 | 0 | 9622.93 | 150640 | 0 | 68 | 73 | 150640 | -1000000
7 | 7 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.9141 | 0 | 7.4834 | 8.818 | 0 | 0 | 0 | 5.6 | 82.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.28 | 0 | 8383.28 | 145617 | 0 | 68 | 72 | 145617 | -1000000
7 | 7 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.7707 | 0 | 7.3391 | 8.818 | 0 | 0 | 0 | 4.8 | 77.8548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.33 | 0 | 8382.33 | 143787 | 0 | 68 | 71 | 143787 | -1000000
7 | 8 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.674 | 0 | 7.2361 | 8.818 | 0 | 0 | 0 | 4.8 | 77.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.54 | 0 | 8381.54 | 142797 | 0 | 68 | 70 | 142797 | -1000000
7 | 8 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.9101 | 0 | 7.4121 | 8.818 | 0 | 0 | 0 | 4.8 | 78.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.54 | 0 | 8381.54 | 141801 | 0 | 67 | 70 | 141801 | -1000000
7 | 8 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.5324 | 0 | 7.1066 | 8.818 | 0 | 0 | 0 | 4.8 | 77.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.24 | 0 | 8381.24 | 140885 | 0 | 66 | 69 | 140885 | -1000000
7 | 8 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.7824 | 0 | 7.284 | 8.818 | 0 | 0 | 0 | 3.2 | 76.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.03 | 0 | 8381.03 | 140193 | 0 | 67 | 69 | 140193 | -1000000
7 | 8 | 5 | 6 | 6.3122 | 0 | 42.7453 | 0 | 8.0713 | 0 | 7.5382 | 8.818 | 0 | 0 | 0 | 1.6 | 75.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.78 | 0 | 8380.78 | 139341 | 0 | 66 | 70 | 139341 | -1000000
7 | 8 | 6 | 6 | 4.8298 | 0 | 42.7453 | 0 | 8.1155 | 0 | 7.3959 | 8.818 | 0 | 0 | 0 | 0 | 71.9045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.54 | 0 | 8380.54 | 138732 | 0 | 67 | 70 | 138732 | -1000000
7 | 8 | 7 | 6 | 4.5858 | 0 | 42.7453 | 0 | 40.8837 | 0 | 25.335 | 19.9409 | 0 | 0 | 0 | 0 | 133.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.3 | 0 | 8380.3 | 709195 | -2834.54 | 68 | 73 | 709195 | -1002834.54
7 | 8 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 40.3314 | 0 | 25.335 | 20.0862 | 0 | 0 | 0 | 0 | 133.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.93 | 0 | 8379.93 | 684455 | -3473.35 | 69 | 77 | 684455 | -1003473.35
7 | 8 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 40.599 | 0 | 25.335 | 19.826 | 0 | 0 | 0 | 0 | 133.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8398.9 | 0 | 8398.9 | 697755 | -8438.64 | 70 | 80 | 697755 | -1008438.64
7 | 8 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 43.1952 | 0 | 25.335 | 20.0226 | 0 | 0 | 0 | 0 | 136.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8401.93 | 0 | 8401.93 | 740073 | -10525.9 | 71 | 82 | 740073 | -1010525.9
7 | 8 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 46.2857 | 0 | 25.335 | 20.0253 | 0 | 0 | 0 | 0 | 139.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8403.73 | 0 | 8403.73 | 789927 | -16871.4 | 72 | 84 | 789927 | -1016871.4
7 | 8 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 50.7773 | 0 | 25.335 | 19.8602 | 0 | 0 | 0 | 0 | 144.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8404.72 | 0 | 8404.72 | 850766 | -26983.5 | 73 | 86 | 850766 | -1026983.5
7 | 8 | 13 | 6 | 5.4709 | 0 | 42.7453 | 0 | 54.8176 | 0 | 25.335 | 19.7138 | 0 | 0 | 0 | 0 | 148.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8405.36 | 0 | 8405.36 | 869593 | -33218 | 73 | 87 | 869593 | -1033218
7 | 8 | 14 | 6 | 5.4722 | 0 | 42.7453 | 0 | 13.7915 | 0 | 15.1949 | 12.8287 | 0 | 0 | 0 | 0 | 90.0325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8405.7 | 0 | 8405.7 | 217229 | 0 | 73 | 88 | 217229 | -1000000
7 | 8 | 15 | 6 | 5.4718 | 0 | 42.7453 | 0 | 13.5901 | 0 | 14.7774 | 12.8287 | 0 | 0 | 0 | 0 | 89.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8406.2 | 0 | 8406.2 | 224707 | 0 | 73 | 89 | 224707 | -1000000
7 | 8 | 16 | 6 | 5.4733 | 0 | 42.7453 | 0 | 13.6417 | 0 | 15.083 | 12.8287 | 0 | 0 | 0 | 0 | 89.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8397.53 | 0 | 8397.53 | 228430 | 0 | 73 | 87 | 228430 | -1000000
7 | 8 | 17 | 6 | 5.5937 | 0 | 42.7453 | 0 | 13.4269 | 0 | 14.8121 | 12.8287 | 0 | 0 | 0 | 0 | 89.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8392.46 | 0 | 8392.46 | 227060 | 0 | 73 | 84 | 227060 | -1000000
7 | 8 | 18 | 6 | 7.1076 | 0 | 42.7453 | 0 | 8.2477 | 0 | 7.6494 | 8.818 | 0 | 0 | 0 | 0 | 74.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.69 | 0 | 8388.69 | 134055 | 0 | 73 | 82 | 134055 | -1000000
7 | 8 | 19 | 6 | 7.3949 | 0 | 42.7453 | 0 | 8.0196 | 0 | 7.525 | 8.818 | 0 | 0 | 0 | 1.2 | 75.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.62 | 0 | 8385.62 | 133687 | 0 | 71 | 79 | 133687 | -1000000
7 | 8 | 20 | 6 | 8.5082 | 0 | 42.7453 | 0 | 7.9484 | 0 | 7.4919 | 8.818 | 0 | 0 | 0 | 4 | 79.5118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.4 | 0 | 8383.4 | 133267 | 0 | 69 | 75 | 133267 | -1000000
7 | 8 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.832 | 0 | 6.6716 | 8.818 | 0 | 0 | 0 | 7.2 | 81.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.73 | 0 | 8381.73 | 132825 | 0 | 67 | 72 | 132825 | -1000000
7 | 8 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.1754 | 0 | 6.9271 | 8.818 | 0 | 0 | 0 | 6.4 | 80.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.42 | 0 | 8380.42 | 132450 | 0 | 66 | 71 | 132450 | -1000000
7 | 8 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.7924 | 0 | 6.6472 | 8.818 | 0 | 0 | 0 | 5.6 | 79.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.53 | 0 | 8379.53 | 132157 | 0 | 66 | 69 | 132157 | -1000000
7 | 8 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.6339 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 73.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3225.57 | 0 | 3225.57 | 131646 | 0 | 65 | 68 | 131646 | -1000000
7 | 9 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5745 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3225.01 | 0 | 3225.01 | 131194 | 0 | 64 | 67 | 131194 | -1000000
7 | 9 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.52 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.75 | 0 | 3224.75 | 130828 | 0 | 63 | 66 | 130828 | -1000000
7 | 9 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4692 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.49 | 0 | 3224.49 | 130523 | 0 | 62 | 65 | 130523 | -1000000
7 | 9 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4088 | 0 | 5.4833 | 8.818 | 0 | 0 | 0 | 3.2 | 71.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.37 | 0 | 3224.37 | 129991 | 0 | 60 | 64 | 129991 | -1000000
7 | 9 | 5 | 7 | 5.0498 | 0 | 42.7453 | 0 | 6.6541 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 1.6 | 70.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.32 | 0 | 3224.32 | 129635 | 0 | 59 | 64 | 129635 | -1000000
7 | 9 | 6 | 7 | 3.9295 | 0 | 42.7453 | 0 | 6.4715 | 0 | 6.4382 | 8.818 | 0 | 0 | 0 | 0 | 68.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.37 | 0 | 3224.37 | 129315 | 0 | 58 | 63 | 129315 | -1000000
7 | 9 | 7 | 7 | 3.6829 | 0 | 42.7453 | 0 | 7.1982 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 0 | 67.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.52 | 0 | 3224.52 | 129214 | 0 | 59 | 65 | 129214 | -1000000
7 | 9 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 7.2645 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 0 | 68.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.65 | 0 | 3224.65 | 128887 | 0 | 59 | 67 | 128887 | -1000000
7 | 9 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.3381 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 0 | 68.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.31 | 0 | 3224.31 | 128668 | 0 | 59 | 69 | 128668 | -1000000
7 | 9 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.9463 | 0 | 5.5195 | 12.8287 | 0 | 0 | 0 | 0 | 75.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3223.19 | 0 | 3223.19 | 181453 | 0 | 60 | 71 | 181453 | -1000000
7 | 9 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.697 | 0 | 5.5486 | 12.8287 | 0 | 0 | 0 | 0 | 75.9635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3221.68 | 0 | 3221.68 | 193609 | 0 | 61 | 73 | 193609 | -1000000
7 | 9 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.9502 | 0 | 5.5636 | 12.8287 | 0 | 0 | 0 | 0 | 76.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3219.93 | 0 | 3219.93 | 195892 | 0 | 61 | 75 | 195892 | -1000000
7 | 9 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.6412 | 0 | 5.5935 | 12.8287 | 0 | 0 | 0 | 0 | 75.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3218.24 | 0 | 3218.24 | 200961 | 0 | 61 | 75 | 200961 | -1000000
7 | 9 | 14 | 7 | 4.146 | 0 | 42.7453 | 0 | 10.8659 | 0 | 11.4172 | 12.8287 | 0 | 0 | 0 | 0 | 82.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.61 | 0 | 3216.61 | 201103 | 0 | 61 | 76 | 201103 | -1000000
7 | 9 | 15 | 7 | 4.1463 | 0 | 42.7453 | 0 | 14.4042 | 0 | 17.9993 | 14.8767 | 0 | 0 | 0 | 0 | 94.1717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.16 | 0 | 3215.16 | 257877 | 0 | 61 | 76 | 257877 | -1000000
7 | 9 | 16 | 7 | 4.1461 | 0 | 42.7453 | 0 | 14.392 | 0 | 17.593 | 14.8767 | 0 | 0 | 0 | 0 | 93.7529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213.72 | 0 | 3213.72 | 252144 | 0 | 60 | 75 | 252144 | -1000000
7 | 9 | 17 | 7 | 4.1467 | 0 | 42.7453 | 0 | 10.2623 | 0 | 10.0935 | 10.866 | 0 | 0 | 0 | 0 | 78.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3212.37 | 0 | 3212.37 | 179558 | 0 | 60 | 75 | 179558 | -1000000
7 | 9 | 18 | 7 | 4.1482 | 0 | 42.7453 | 0 | 9.3532 | 0 | 9.1122 | 10.866 | 0 | 0 | 0 | 0 | 76.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3211.09 | 0 | 3211.09 | 175725 | 0 | 59 | 74 | 175725 | -1000000
7 | 9 | 19 | 7 | 4.944 | 0 | 42.7453 | 0 | 5.4538 | 0 | 5.494 | 8.818 | 0 | 0 | 0 | 1.2 | 68.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3210.06 | 0 | 3210.06 | 127941 | 0 | 59 | 69 | 127941 | -1000000
7 | 9 | 20 | 7 | 6.2136 | 0 | 42.7453 | 0 | 5.5441 | 0 | 5.4945 | 8.818 | 0 | 0 | 0 | 4 | 72.8155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3209.09 | 0 | 3209.09 | 127660 | 0 | 58 | 65 | 127660 | -1000000
7 | 9 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.1298 | 0 | 5.5057 | 8.818 | 0 | 0 | 0 | 7.2 | 76.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3208.36 | 0 | 3208.36 | 127442 | 0 | 56 | 60 | 127442 | -1000000
7 | 9 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4007 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 6.4 | 76.5121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3208.06 | 0 | 3208.06 | 127185 | 0 | 55 | 60 | 127185 | -1000000
7 | 9 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3995 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 5.6 | 75.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3208.16 | 0 | 3208.16 | 127163 | 0 | 55 | 59 | 127163 | -1000000
7 | 9 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.3987 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8361.89 | 0 | 8361.89 | 127146 | 0 | 54 | 59 | 127146 | -1000000
7 | 10 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3991 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8362.32 | 0 | 8362.32 | 127156 | 0 | 54 | 58 | 127156 | -1000000
7 | 10 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3854 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8361.99 | 0 | 8361.99 | 126850 | 0 | 53 | 56 | 126850 | -1000000
7 | 10 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3787 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8362.14 | 0 | 8362.14 | 126707 | 0 | 53 | 55 | 126707 | -1000000
7 | 10 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 7.7017 | 0 | 5.4787 | 12.8287 | 0 | 0 | 0 | 3.2 | 85.8535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9275.23 | 0 | 9275.23 | 156157 | 0 | 53 | 55 | 156157 | -1000000
7 | 10 | 5 | 1 | 23.9637 | 0 | 69.9783 | 0 | 8.6775 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 1.6 | 118.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11307.5 | 0 | 11307.5 | 177379 | 0 | 53 | 55 | 177379 | -1000000
7 | 10 | 6 | 1 | 38.9318 | 0 | 140.608 | 0 | 54.17 | 0 | 6.332 | 21.5186 | 0 | 0 | 0 | 0 | 261.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30449.2 | 0 | 30449.2 | 794581 | -21098.7 | 53 | 55 | 794581 | -1021098.7
7 | 10 | 7 | 1 | 39.1241 | 0 | 168.222 | 0 | 39.3086 | 0 | 6.332 | 21.1798 | 0 | 0 | 0 | 0 | 274.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33390.8 | 0 | 33390.8 | 836623 | -23927 | 54 | 57 | 836623 | -1023927
7 | 10 | 8 | 1 | 39.8056 | 0 | 173.795 | 0 | 40.2339 | 0 | 11.0556 | 21.1014 | 0 | 0 | 0 | 0 | 285.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42251 | 0 | 42251 | 855725 | -21098 | 55 | 60 | 855725 | -1021098
7 | 10 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 46.8286 | 0 | 7.2576 | 21.2061 | 0 | 0 | 0 | 0 | 288.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65815.1 | 0 | 65815.1 | 869860 | -19631.4 | 55 | 62 | 869860 | -1019631.4
7 | 10 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 49.3093 | 0 | 25.335 | 21.4078 | 0 | 0 | 0 | 0 | 300.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67290.4 | 0 | 67290.4 | 913359 | -17650.6 | 57 | 65 | 913359 | -1017650.6
7 | 10 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 45.8803 | 0 | 25.335 | 22.119 | 0 | 0 | 0 | 0 | 283.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67291.9 | 0 | 67291.9 | 863497 | -13243.3 | 58 | 67 | 863497 | -1013243.3
7 | 10 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 52.7137 | 0 | 6.332 | 22.3907 | 0 | 0 | 0 | 0 | 271.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67292.5 | 0 | 67292.5 | 960833 | -18896.9 | 60 | 70 | 960833 | -1018896.9
7 | 10 | 13 | 1 | 41.2549 | 0 | 165.698 | 0 | 59.0293 | 0 | 8.7499 | 23.3049 | 0 | 0 | 0 | 0 | 298.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67292.8 | 0 | 67292.8 | 1074850 | -13984.6 | 61 | 72 | 1074850 | -1013984.6
7 | 10 | 14 | 1 | 40.6679 | 0 | 172.702 | 0 | 66.1131 | 0 | 25.335 | 23.1021 | 0 | 0 | 0 | 0 | 327.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65820.4 | 0 | 65820.4 | 1162880 | -16851.4 | 62 | 74 | 1162880 | -1016851.4
7 | 10 | 15 | 1 | 40.5608 | 0 | 173.986 | 0 | 69.4685 | 0 | 25.335 | 23.3575 | 0 | 0 | 0 | 0 | 332.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59930.9 | 0 | 59930.9 | 1211390 | -17746.8 | 62 | 76 | 1211390 | -1017746.8
7 | 10 | 16 | 1 | 40.2992 | 0 | 169.782 | 0 | 70.3889 | 0 | 11.5414 | 23.1028 | 0 | 0 | 0 | 0 | 315.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49624 | 0 | 49624 | 1227630 | -27129.4 | 62 | 76 | 1227630 | -1027129.4
7 | 10 | 17 | 1 | 35.4721 | 0 | 152.497 | 0 | 66.6848 | 0 | 6.9654 | 22.6069 | 0 | 0 | 0 | 0 | 284.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37844.5 | 0 | 37844.5 | 1189210 | -33192.2 | 63 | 75 | 1189210 | -1033192.2
7 | 10 | 18 | 1 | 24.5834 | 0 | 93.4203 | 0 | 49.1443 | 0 | 6.332 | 20.7628 | 0 | 0 | 0 | 0 | 194.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23120.3 | 0 | 23120.3 | 847679 | -36192.9 | 62 | 75 | 847679 | -1036192.9
7 | 10 | 19 | 1 | 18.7247 | 0 | 62.7906 | 0 | 9.5697 | 0 | 5.5106 | 8.818 | 0 | 0 | 0 | 1.2 | 106.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16494.7 | 0 | 16494.7 | 188744 | 0 | 62 | 72 | 188744 | -1000000
7 | 10 | 20 | 1 | 17.2964 | 0 | 54.6418 | 0 | 7.626 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4 | 97.8615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15759.9 | 0 | 15759.9 | 168948 | 0 | 62 | 68 | 168948 | -1000000
7 | 10 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.133 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 91.3501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.23 | 0 | 9856.23 | 155677 | 0 | 61 | 65 | 155677 | -1000000
7 | 10 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.7989 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 6.4 | 83.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9617.83 | 0 | 9617.83 | 144585 | 0 | 59 | 63 | 144585 | -1000000
7 | 10 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.5052 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 5.6 | 79.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.68 | 0 | 8378.68 | 139879 | 0 | 58 | 61 | 139879 | -1000000
7 | 10 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6515 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.39 | 0 | 8378.39 | 138266 | 0 | 56 | 59 | 138266 | -1000000
7 | 11 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8731 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.3 | 0 | 8378.3 | 137515 | 0 | 55 | 58 | 137515 | -1000000
7 | 11 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8446 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 78.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.4 | 0 | 8378.4 | 136895 | 0 | 55 | 56 | 136895 | -1000000
7 | 11 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8068 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.62 | 0 | 8378.62 | 136063 | 0 | 54 | 55 | 136063 | -1000000
7 | 11 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.9523 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 3.2 | 81.0951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9291.81 | 0 | 9291.81 | 139317 | 0 | 55 | 56 | 139317 | -1000000
7 | 11 | 5 | 2 | 24.0662 | 0 | 69.9783 | 0 | 11.2136 | 0 | 5.5391 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11324.1 | 0 | 11324.1 | 234139 | 0 | 55 | 58 | 234139 | -1000000
7 | 11 | 6 | 2 | 37.7935 | 0 | 140.608 | 0 | 37.5109 | 0 | 6.332 | 21.0499 | 0 | 0 | 0 | 0 | 243.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30465.7 | 0 | 30465.7 | 706812 | -9821.57 | 56 | 59 | 706812 | -1009821.57
7 | 11 | 7 | 2 | 38.8276 | 0 | 168.222 | 0 | 49.981 | 0 | 8.13 | 21.2873 | 0 | 0 | 0 | 0 | 286.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33407.2 | 0 | 33407.2 | 875241 | -23562.4 | 58 | 63 | 875241 | -1023562.4
7 | 11 | 8 | 2 | 39.6631 | 0 | 173.795 | 0 | 57.4225 | 0 | 25.335 | 21.3114 | 0 | 0 | 0 | 0 | 317.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42259.8 | 0 | 42259.8 | 1008260 | -21661.6 | 61 | 67 | 1008260 | -1021661.6
7 | 11 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 63.0611 | 0 | 25.335 | 21.6007 | 0 | 0 | 0 | 0 | 322.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65821.9 | 0 | 65821.9 | 1079520 | -20412.1 | 62 | 71 | 1079520 | -1020412.1
7 | 11 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 68.9117 | 0 | 25.335 | 21.8142 | 0 | 0 | 0 | 0 | 320.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.1 | 0 | 67297.1 | 1168980 | -16795.9 | 64 | 74 | 1168980 | -1016795.9
7 | 11 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 66.0172 | 0 | 25.335 | 22.4152 | 0 | 0 | 0 | 0 | 304.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.7 | 0 | 67298.7 | 1117690 | -12458.8 | 65 | 77 | 1117690 | -1012458.8
7 | 11 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 74.448 | 0 | 25.335 | 22.3684 | 0 | 0 | 0 | 0 | 312.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.3 | 0 | 67299.3 | 1257220 | -21608.7 | 67 | 80 | 1257220 | -1021608.7
7 | 11 | 13 | 2 | 41.233 | 0 | 165.698 | 0 | 82.3132 | 0 | 25.335 | 23.678 | 0 | 0 | 0 | 0 | 338.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.7 | 0 | 67299.7 | 1377670 | -13211.4 | 68 | 81 | 1377670 | -1013211.4
7 | 11 | 14 | 2 | 40.6406 | 0 | 172.702 | 0 | 87.9461 | 0 | 25.335 | 23.378 | 0 | 0 | 0 | 0 | 350.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65827.2 | 0 | 65827.2 | 1466870 | -17204.5 | 69 | 83 | 1466870 | -1017204.5
7 | 11 | 15 | 2 | 40.54 | 0 | 173.986 | 0 | 93.8813 | 0 | 25.335 | 23.4117 | 0 | 0 | 0 | 0 | 357.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59937.4 | 0 | 59937.4 | 1565510 | -21702.8 | 70 | 84 | 1565510 | -1021702.8
7 | 11 | 16 | 2 | 40.282 | 0 | 169.782 | 0 | 94.5595 | 0 | 25.335 | 23.1389 | 0 | 0 | 0 | 0 | 353.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49630.2 | 0 | 49630.2 | 1591250 | -30890.8 | 70 | 83 | 1591250 | -1030890.8
7 | 11 | 17 | 2 | 35.4699 | 0 | 152.497 | 0 | 95.2551 | 0 | 25.335 | 22.683 | 0 | 0 | 0 | 0 | 331.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37850.6 | 0 | 37850.6 | 1519840 | -36757.7 | 70 | 83 | 1519840 | -1036757.7
7 | 11 | 18 | 2 | 24.5825 | 0 | 93.4203 | 0 | 70.0509 | 0 | 25.335 | 21.3651 | 0 | 0 | 0 | 0 | 234.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23126.2 | 0 | 23126.2 | 1119170 | -36837.5 | 70 | 82 | 1119170 | -1036837.5
7 | 11 | 19 | 2 | 17.8601 | 0 | 62.7906 | 0 | 12.0624 | 0 | 12.6402 | 8.818 | 0 | 0 | 0 | 1.2 | 115.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16500.4 | 0 | 16500.4 | 193872 | 0 | 69 | 80 | 193872 | -1000000
7 | 11 | 20 | 2 | 17.7389 | 0 | 54.6418 | 0 | 10.0132 | 0 | 9.6681 | 8.818 | 0 | 0 | 0 | 4 | 104.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15764.7 | 0 | 15764.7 | 173442 | 0 | 68 | 77 | 173442 | -1000000
7 | 11 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.6308 | 0 | 5.4934 | 8.818 | 0 | 0 | 0 | 7.2 | 92.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.81 | 0 | 9860.81 | 160254 | 0 | 68 | 75 | 160254 | -1000000
7 | 11 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.7588 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 6.4 | 83.9889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9621.77 | 0 | 9621.77 | 149346 | 0 | 68 | 74 | 149346 | -1000000
7 | 11 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.7821 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 5.6 | 80.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.03 | 0 | 8382.03 | 144300 | 0 | 67 | 74 | 144300 | -1000000
7 | 11 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.3815 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 79.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.96 | 0 | 8380.96 | 142786 | 0 | 67 | 73 | 142786 | -1000000
7 | 12 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.2874 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.07 | 0 | 8380.07 | 141776 | 0 | 66 | 72 | 141776 | -1000000
7 | 12 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1923 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.23 | 0 | 8379.23 | 140710 | 0 | 64 | 71 | 140710 | -1000000
7 | 12 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1211 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.41 | 0 | 8378.41 | 140122 | 0 | 63 | 70 | 140122 | -1000000
7 | 12 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.5508 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 3.2 | 81.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9290.56 | 0 | 9290.56 | 143469 | 0 | 63 | 70 | 143469 | -1000000
7 | 12 | 5 | 3 | 24.2293 | 0 | 69.9783 | 0 | 14.0587 | 0 | 5.7202 | 12.8287 | 0 | 0 | 0 | 1.6 | 128.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11321.8 | 0 | 11321.8 | 280513 | 0 | 63 | 70 | 280513 | -1000000
7 | 12 | 6 | 3 | 46.659 | 0 | 140.608 | 0 | 62.97 | 0 | 25.335 | 23.591 | 0 | 0 | 0 | 0 | 299.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30462.3 | 0 | 30462.3 | 1216710 | -4727.52 | 64 | 70 | 1216710 | -1004727.52
7 | 12 | 7 | 3 | 41.099 | 0 | 168.222 | 0 | 65.5183 | 0 | 25.335 | 23.0744 | 0 | 0 | 0 | 0 | 323.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33402.8 | 0 | 33402.8 | 1232160 | -23386.6 | 64 | 69 | 1232160 | -1023386.6
7 | 12 | 8 | 3 | 39.9718 | 0 | 173.795 | 0 | 67.528 | 0 | 25.335 | 22.8489 | 0 | 0 | 0 | 0 | 329.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42260.1 | 0 | 42260.1 | 1207910 | -23809.2 | 65 | 69 | 1207910 | -1023809.2
7 | 12 | 9 | 3 | 42.0391 | 0 | 172.186 | 0 | 68.255 | 0 | 25.335 | 22.7041 | 0 | 0 | 0 | 0 | 330.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65822.4 | 0 | 65822.4 | 1224970 | -24611.4 | 66 | 68 | 1224970 | -1024611.4
7 | 12 | 10 | 3 | 41.6594 | 0 | 163.102 | 0 | 68.431 | 0 | 25.335 | 22.8529 | 0 | 0 | 0 | 0 | 321.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67295.7 | 0 | 67295.7 | 1218320 | -22117.5 | 66 | 68 | 1218320 | -1022117.5
7 | 12 | 11 | 3 | 41.0001 | 0 | 149.692 | 0 | 62.4037 | 0 | 25.335 | 22.8186 | 0 | 0 | 0 | 0 | 301.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.2 | 0 | 67296.2 | 1100140 | -18310.3 | 66 | 69 | 1100140 | -1018310.3
7 | 12 | 12 | 3 | 39.827 | 0 | 150.207 | 0 | 63.0443 | 0 | 25.335 | 23.0716 | 0 | 0 | 0 | 0 | 301.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.6 | 0 | 67296.6 | 1114000 | -17290.9 | 66 | 69 | 1114000 | -1017290.9
7 | 12 | 13 | 3 | 41.3355 | 0 | 165.698 | 0 | 76.0494 | 0 | 25.335 | 22.9879 | 0 | 0 | 0 | 0 | 331.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.4 | 0 | 67297.4 | 1302890 | -20417.5 | 68 | 71 | 1302890 | -1020417.5
7 | 12 | 14 | 3 | 40.6243 | 0 | 172.702 | 0 | 83.4011 | 0 | 25.335 | 22.9974 | 0 | 0 | 0 | 0 | 345.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65825.6 | 0 | 65825.6 | 1388350 | -23560.5 | 69 | 74 | 1388350 | -1023560.5
7 | 12 | 15 | 3 | 40.6456 | 0 | 173.986 | 0 | 87.6927 | 0 | 25.335 | 23.2933 | 0 | 0 | 0 | 0 | 350.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59936.5 | 0 | 59936.5 | 1461230 | -24261.9 | 70 | 76 | 1461230 | -1024261.9
7 | 12 | 16 | 3 | 40.2993 | 0 | 169.782 | 0 | 87.073 | 0 | 25.335 | 23.4246 | 0 | 0 | 0 | 0 | 345.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49629.5 | 0 | 49629.5 | 1471010 | -22767.1 | 70 | 77 | 1471010 | -1022767.1
7 | 12 | 17 | 3 | 35.4632 | 0 | 152.497 | 0 | 84.3369 | 0 | 25.335 | 23.1497 | 0 | 0 | 0 | 0 | 320.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37849.9 | 0 | 37849.9 | 1441020 | -18640.1 | 71 | 77 | 1441020 | -1018640.1
7 | 12 | 18 | 3 | 24.599 | 0 | 93.4203 | 0 | 60.5779 | 0 | 25.335 | 21.4893 | 0 | 0 | 0 | 0 | 225.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23125.7 | 0 | 23125.7 | 1043160 | -16194.1 | 71 | 78 | 1043160 | -1016194.1
7 | 12 | 19 | 3 | 17.8091 | 0 | 62.7906 | 0 | 12.0329 | 0 | 12.6273 | 8.818 | 0 | 0 | 0 | 1.2 | 115.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16500.1 | 0 | 16500.1 | 195291 | 0 | 70 | 76 | 195291 | -1000000
7 | 12 | 20 | 3 | 18.3439 | 0 | 54.6418 | 0 | 9.6008 | 0 | 9.1895 | 8.818 | 0 | 0 | 0 | 4 | 104.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15764.9 | 0 | 15764.9 | 174649 | 0 | 69 | 74 | 174649 | -1000000
7 | 12 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.9756 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.42 | 0 | 9861.42 | 161264 | 0 | 68 | 72 | 161264 | -1000000
7 | 12 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.9853 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 6.4 | 84.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9622.87 | 0 | 9622.87 | 150273 | 0 | 68 | 72 | 150273 | -1000000
7 | 12 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.4161 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 5.6 | 80.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.38 | 0 | 8383.38 | 145250 | 0 | 68 | 71 | 145250 | -1000000
7 | 12 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.6097 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.7678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.58 | 0 | 8382.58 | 143677 | 0 | 68 | 71 | 143677 | -1000000
7 | 13 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.2486 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.87 | 0 | 8381.87 | 142757 | 0 | 68 | 70 | 142757 | -1000000
7 | 13 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.4784 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.25 | 0 | 8381.25 | 141899 | 0 | 68 | 70 | 141899 | -1000000
7 | 13 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.127 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.6 | 0 | 8380.6 | 141107 | 0 | 68 | 69 | 141107 | -1000000
7 | 13 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.5492 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 3.2 | 81.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9292.88 | 0 | 9292.88 | 144351 | 0 | 67 | 69 | 144351 | -1000000
7 | 13 | 5 | 4 | 24.242 | 0 | 69.9783 | 0 | 13.7302 | 0 | 5.6879 | 12.8287 | 0 | 0 | 0 | 1.6 | 128.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11324.2 | 0 | 11324.2 | 282671 | 0 | 67 | 68 | 282671 | -1000000
7 | 13 | 6 | 4 | 43.091 | 0 | 140.608 | 0 | 62.4596 | 0 | 25.335 | 23.289 | 0 | 0 | 0 | 0 | 294.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30464.8 | 0 | 30464.8 | 1249850 | -4971.83 | 67 | 68 | 1249850 | -1004971.83
7 | 13 | 7 | 4 | 39.1316 | 0 | 168.222 | 0 | 76.8299 | 0 | 25.335 | 23.252 | 0 | 0 | 0 | 0 | 332.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33405.3 | 0 | 33405.3 | 1368520 | -24200.6 | 68 | 72 | 1368520 | -1024200.6
7 | 13 | 8 | 4 | 39.6932 | 0 | 173.795 | 0 | 81.2465 | 0 | 25.335 | 22.8862 | 0 | 0 | 0 | 0 | 342.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42260.8 | 0 | 42260.8 | 1378360 | -23824.2 | 69 | 75 | 1378360 | -1023824.2
7 | 13 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 84.0957 | 0 | 25.335 | 22.4288 | 0 | 0 | 0 | 0 | 344.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65823 | 0 | 65823 | 1430000 | -23232.5 | 69 | 79 | 1430000 | -1023232.5
7 | 13 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 90.9852 | 0 | 25.335 | 22.7568 | 0 | 0 | 0 | 0 | 343.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.2 | 0 | 67297.2 | 1537730 | -19158.3 | 71 | 82 | 1537730 | -1019158.3
7 | 13 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 85.6995 | 0 | 25.335 | 23.2082 | 0 | 0 | 0 | 0 | 324.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.9 | 0 | 67299.9 | 1440710 | -14425.5 | 72 | 85 | 1440710 | -1014425.5
7 | 13 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 97.84 | 0 | 25.335 | 23.0623 | 0 | 0 | 0 | 0 | 336.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.9 | 0 | 67300.9 | 1620230 | -25738.3 | 74 | 88 | 1620230 | -1025738.3
7 | 13 | 13 | 4 | 41.2606 | 0 | 165.698 | 0 | 115.545 | 0 | 25.335 | 23.1444 | 0 | 0 | 0 | 0 | 370.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67301.1 | 0 | 67301.1 | 1796420 | -33810.7 | 75 | 89 | 1796420 | -1033810.7
7 | 13 | 14 | 4 | 40.6469 | 0 | 172.702 | 0 | 119.592 | 0 | 25.335 | 23.0591 | 0 | 0 | 0 | 0 | 381.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65828.6 | 0 | 65828.6 | 1859760 | -33595.6 | 76 | 91 | 1859760 | -1033595.6
7 | 13 | 15 | 4 | 40.5327 | 0 | 173.986 | 0 | 127.708 | 0 | 25.335 | 23.2801 | 0 | 0 | 0 | 0 | 390.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59939 | 0 | 59939 | 1960500 | -33614.6 | 77 | 92 | 1960500 | -1033614.6
7 | 13 | 16 | 4 | 40.2924 | 0 | 169.782 | 0 | 126.357 | 0 | 25.335 | 23.5994 | 0 | 0 | 0 | 0 | 385.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49631.9 | 0 | 49631.9 | 1931360 | -33069.2 | 76 | 91 | 1931360 | -1033069.2
7 | 13 | 17 | 4 | 35.4781 | 0 | 152.497 | 0 | 118.32 | 0 | 8.3358 | 23.2066 | 0 | 0 | 0 | 0 | 337.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37852.2 | 0 | 37852.2 | 1759350 | -36041.4 | 74 | 89 | 1759350 | -1036041.4
7 | 13 | 18 | 4 | 24.5827 | 0 | 93.4203 | 0 | 98.3175 | 0 | 6.332 | 21.5029 | 0 | 0 | 0 | 0 | 244.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127.8 | 0 | 23127.8 | 1352460 | -47837.5 | 74 | 88 | 1352460 | -1047837.5
7 | 13 | 19 | 4 | 18.9388 | 0 | 62.7906 | 0 | 12.5372 | 0 | 13.4268 | 8.818 | 0 | 0 | 0 | 1.2 | 117.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16502 | 0 | 16502 | 197398 | 0 | 74 | 85 | 197398 | -1000000
7 | 13 | 20 | 4 | 17.3733 | 0 | 54.6418 | 0 | 10.3113 | 0 | 9.9414 | 8.818 | 0 | 0 | 0 | 4 | 105.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15766.2 | 0 | 15766.2 | 176387 | 0 | 73 | 83 | 176387 | -1000000
7 | 13 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 9.528 | 0 | 9.0332 | 8.818 | 0 | 0 | 0 | 7.2 | 97.2994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.38 | 0 | 9861.38 | 163171 | 0 | 73 | 80 | 163171 | -1000000
7 | 13 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 8.7469 | 0 | 8.3297 | 8.818 | 0 | 0 | 0 | 6.4 | 87.8251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9621.6 | 0 | 9621.6 | 152230 | 0 | 73 | 80 | 152230 | -1000000
7 | 13 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 8.4649 | 0 | 8.0568 | 8.818 | 0 | 0 | 0 | 5.6 | 83.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.33 | 0 | 8381.33 | 146993 | 0 | 72 | 80 | 146993 | -1000000
7 | 13 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 8.3779 | 0 | 7.9761 | 8.818 | 0 | 0 | 0 | 4.8 | 83.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.77 | 0 | 8379.77 | 145410 | 0 | 72 | 80 | 145410 | -1000000
7 | 14 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.3275 | 0 | 7.93 | 8.818 | 0 | 0 | 0 | 4.8 | 83.0549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.4 | 0 | 8378.4 | 144468 | 0 | 72 | 80 | 144468 | -1000000
7 | 14 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.282 | 0 | 7.8889 | 8.818 | 0 | 0 | 0 | 4.8 | 82.9683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8377.08 | 0 | 8377.08 | 143610 | 0 | 72 | 79 | 143610 | -1000000
7 | 14 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.2344 | 0 | 7.8464 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8375.75 | 0 | 8375.75 | 142710 | 0 | 71 | 79 | 142710 | -1000000
7 | 14 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.4199 | 0 | 8.0149 | 8.818 | 0 | 0 | 0 | 3.2 | 85.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9287.31 | 0 | 9287.31 | 146291 | 0 | 71 | 77 | 146291 | -1000000
7 | 14 | 5 | 5 | 24.2354 | 0 | 69.9783 | 0 | 17.1897 | 0 | 24.9169 | 12.8287 | 0 | 0 | 0 | 1.6 | 150.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11317.9 | 0 | 11317.9 | 314769 | 0 | 71 | 76 | 314769 | -1000000
7 | 14 | 6 | 5 | 42.0591 | 0 | 140.608 | 0 | 89.344 | 0 | 24.9169 | 24.3626 | 0 | 0 | 0 | 0 | 321.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30457.8 | 0 | 30457.8 | 1666380 | 0 | 71 | 74 | 1666380 | -1000000
7 | 14 | 7 | 5 | 39.2405 | 0 | 168.222 | 0 | 101.918 | 0 | 25.335 | 24.0764 | 0 | 0 | 0 | 0 | 358.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33397.7 | 0 | 33397.7 | 1700130 | -26868.2 | 72 | 76 | 1700130 | -1026868.2
7 | 14 | 8 | 5 | 39.8367 | 0 | 173.795 | 0 | 95.7742 | 0 | 25.335 | 24.0362 | 0 | 0 | 0 | 0 | 358.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42259.6 | 0 | 42259.6 | 1601460 | -25823.6 | 72 | 79 | 1601460 | -1025823.6
7 | 14 | 9 | 5 | 41.0523 | 0 | 172.186 | 0 | 98.9908 | 0 | 25.335 | 24.0198 | 0 | 0 | 0 | 0 | 361.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65822 | 0 | 65822 | 1650030 | -25451.2 | 73 | 81 | 1650030 | -1025451.2
7 | 14 | 10 | 5 | 41.5378 | 0 | 163.102 | 0 | 96.3171 | 0 | 25.335 | 24.0219 | 0 | 0 | 0 | 0 | 350.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67295.5 | 0 | 67295.5 | 1601500 | -22421.2 | 72 | 78 | 1601500 | -1022421.2
7 | 14 | 11 | 5 | 40.8048 | 0 | 149.692 | 0 | 87.4197 | 0 | 25.335 | 23.3674 | 0 | 0 | 0 | 0 | 326.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.6 | 0 | 67296.6 | 1456730 | -24681.7 | 72 | 76 | 1456730 | -1024681.7
7 | 14 | 12 | 5 | 39.7813 | 0 | 150.207 | 0 | 83.1167 | 0 | 25.335 | 23.5387 | 0 | 0 | 0 | 0 | 321.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.4 | 0 | 67297.4 | 1408170 | -18180.7 | 71 | 73 | 1408170 | -1018180.7
7 | 14 | 13 | 5 | 41.3763 | 0 | 165.698 | 0 | 92.7222 | 0 | 25.335 | 23.6938 | 0 | 0 | 0 | 0 | 348.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.3 | 0 | 67298.3 | 1518050 | -21855 | 71 | 75 | 1518050 | -1021855
7 | 14 | 14 | 5 | 40.8876 | 0 | 172.702 | 0 | 94.5484 | 0 | 25.335 | 23.6259 | 0 | 0 | 0 | 0 | 357.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65826.2 | 0 | 65826.2 | 1559030 | -26116.2 | 72 | 76 | 1559030 | -1026116.2
7 | 14 | 15 | 5 | 40.8175 | 0 | 173.986 | 0 | 96.0919 | 0 | 25.335 | 23.7762 | 0 | 0 | 0 | 0 | 360.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59936.8 | 0 | 59936.8 | 1597060 | -27172.9 | 72 | 78 | 1597060 | -1027172.9
7 | 14 | 16 | 5 | 40.7629 | 0 | 169.782 | 0 | 97.28 | 0 | 25.335 | 23.8379 | 0 | 0 | 0 | 0 | 356.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49629.4 | 0 | 49629.4 | 1647010 | -25768 | 73 | 79 | 1647010 | -1025768
7 | 14 | 17 | 5 | 35.7803 | 0 | 152.497 | 0 | 93.3797 | 0 | 25.335 | 23.8337 | 0 | 0 | 0 | 0 | 330.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37849.9 | 0 | 37849.9 | 1591970 | -21209.7 | 74 | 79 | 1591970 | -1021209.7
7 | 14 | 18 | 5 | 24.8535 | 0 | 93.4203 | 0 | 69.0839 | 0 | 25.335 | 22.1813 | 0 | 0 | 0 | 0 | 234.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23125.8 | 0 | 23125.8 | 1199860 | -18598.4 | 75 | 80 | 1199860 | -1018598.4
7 | 14 | 19 | 5 | 18.1203 | 0 | 62.7906 | 0 | 12.3792 | 0 | 13.1737 | 8.818 | 0 | 0 | 0 | 1.2 | 116.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16500.1 | 0 | 16500.1 | 197740 | 0 | 75 | 80 | 197740 | -1000000
7 | 14 | 20 | 5 | 17.8007 | 0 | 54.6418 | 0 | 10.2953 | 0 | 9.9455 | 8.818 | 0 | 0 | 0 | 4 | 105.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15764.6 | 0 | 15764.6 | 176667 | 0 | 75 | 80 | 176667 | -1000000
7 | 14 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.841 | 0 | 8.7544 | 8.818 | 0 | 0 | 0 | 7.2 | 96.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.73 | 0 | 9860.73 | 163399 | 0 | 75 | 80 | 163399 | -1000000
7 | 14 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 8.24 | 0 | 5.4872 | 8.818 | 0 | 0 | 0 | 6.4 | 84.4757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9621.65 | 0 | 9621.65 | 152439 | 0 | 75 | 80 | 152439 | -1000000
7 | 14 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.9723 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 5.6 | 80.7322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.67 | 0 | 8381.67 | 147155 | 0 | 74 | 79 | 147155 | -1000000
7 | 14 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.8782 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 4.8 | 76.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.26 | 0 | 8380.26 | 145323 | 0 | 74 | 79 | 145323 | -1000000
7 | 15 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.8245 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 4.8 | 76.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.9 | 0 | 8378.9 | 144256 | 0 | 73 | 78 | 144256 | -1000000
7 | 15 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.7815 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 76.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.3 | 0 | 8378.3 | 143396 | 0 | 73 | 76 | 143396 | -1000000
7 | 15 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.7366 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 75.9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8377.36 | 0 | 8377.36 | 142493 | 0 | 72 | 75 | 142493 | -1000000
7 | 15 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.6983 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 3.2 | 74.3247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376.53 | 0 | 8376.53 | 141727 | 0 | 72 | 75 | 141727 | -1000000
7 | 15 | 5 | 6 | 6.3304 | 0 | 42.7453 | 0 | 7.6619 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 1.6 | 72.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8375.77 | 0 | 8375.77 | 140995 | 0 | 72 | 75 | 140995 | -1000000
7 | 15 | 6 | 6 | 4.8755 | 0 | 42.7453 | 0 | 8.3812 | 0 | 7.8257 | 8.818 | 0 | 0 | 0 | 0 | 72.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8375.09 | 0 | 8375.09 | 140293 | 0 | 72 | 75 | 140293 | -1000000
7 | 15 | 7 | 6 | 4.5949 | 0 | 42.7453 | 0 | 56.6733 | 0 | 24.9169 | 20.8829 | 0 | 0 | 0 | 0 | 149.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8374.42 | 0 | 8374.42 | 993830 | 0 | 73 | 77 | 993830 | -1000000
7 | 15 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 52.6587 | 0 | 25.335 | 20.3593 | 0 | 0 | 0 | 0 | 146.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8373.67 | 0 | 8373.67 | 907610 | -18043.3 | 73 | 79 | 907610 | -1018043.3
7 | 15 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 49.1258 | 0 | 25.335 | 20.3216 | 0 | 0 | 0 | 0 | 142.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.44 | 0 | 8396.44 | 846999 | -9773.08 | 74 | 81 | 846999 | -1009773.08
7 | 15 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 54.6 | 0 | 25.335 | 19.8243 | 0 | 0 | 0 | 0 | 147.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8399.73 | 0 | 8399.73 | 915392 | -27390.5 | 75 | 83 | 915392 | -1027390.5
7 | 15 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 58.7813 | 0 | 25.335 | 19.7864 | 0 | 0 | 0 | 0 | 152.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8401.38 | 0 | 8401.38 | 944970 | -32248.6 | 76 | 84 | 944970 | -1032248.6
7 | 15 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 69.8633 | 0 | 6.332 | 19.6507 | 0 | 0 | 0 | 0 | 144.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8402.32 | 0 | 8402.32 | 1005400 | -46295.2 | 76 | 86 | 1005400 | -1046295.2
7 | 15 | 13 | 6 | 5.4722 | 0 | 42.7453 | 0 | 71.1538 | 0 | 6.332 | 19.5769 | 0 | 0 | 0 | 0 | 145.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8403.11 | 0 | 8403.11 | 991061 | -49528.9 | 76 | 87 | 991061 | -1049528.9
7 | 15 | 14 | 6 | 5.4706 | 0 | 42.7453 | 0 | 14.1153 | 0 | 16.1113 | 12.8287 | 0 | 0 | 0 | 0 | 91.2711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8404.01 | 0 | 8404.01 | 223962 | 0 | 76 | 87 | 223962 | -1000000
7 | 15 | 15 | 6 | 5.47 | 0 | 42.7453 | 0 | 13.6578 | 0 | 15.1939 | 12.8287 | 0 | 0 | 0 | 0 | 89.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8404.46 | 0 | 8404.46 | 229845 | 0 | 76 | 88 | 229845 | -1000000
7 | 15 | 16 | 6 | 5.4725 | 0 | 42.7453 | 0 | 16.9471 | 0 | 24.2798 | 14.8767 | 0 | 0 | 0 | 0 | 104.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.31 | 0 | 8395.31 | 292479 | 0 | 76 | 87 | 292479 | -1000000
7 | 15 | 17 | 6 | 5.4733 | 0 | 42.7453 | 0 | 16.9506 | 0 | 24.7548 | 14.8767 | 0 | 0 | 0 | 0 | 104.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8390.04 | 0 | 8390.04 | 295720 | 0 | 76 | 87 | 295720 | -1000000
7 | 15 | 18 | 6 | 5.4752 | 0 | 42.7453 | 0 | 16.8317 | 0 | 24.6673 | 14.8767 | 0 | 0 | 0 | 0 | 104.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8386.16 | 0 | 8386.16 | 296304 | 0 | 76 | 86 | 296304 | -1000000
7 | 15 | 19 | 6 | 6.5531 | 0 | 42.7453 | 0 | 13.519 | 0 | 15.5357 | 12.8287 | 0 | 0 | 0 | 1.2 | 92.3817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.01 | 0 | 8383.01 | 235125 | 0 | 76 | 83 | 235125 | -1000000
7 | 15 | 20 | 6 | 8.3206 | 0 | 42.7453 | 0 | 7.4269 | 0 | 7.4101 | 8.818 | 0 | 0 | 0 | 4 | 78.7208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.6 | 0 | 8380.6 | 134386 | 0 | 75 | 81 | 134386 | -1000000
7 | 15 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.3195 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 7.2 | 80.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.54 | 0 | 8378.54 | 134125 | 0 | 74 | 78 | 134125 | -1000000
7 | 15 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.3027 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 79.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376.96 | 0 | 8376.96 | 133787 | 0 | 73 | 78 | 133787 | -1000000
7 | 15 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.2902 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 5.6 | 78.7299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8375.56 | 0 | 8375.56 | 133536 | 0 | 73 | 77 | 133536 | -1000000
7 | 15 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 7.2732 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 74.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3221.17 | 0 | 3221.17 | 133193 | 0 | 73 | 77 | 133193 | -1000000
7 | 16 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.2534 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 74.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.11 | 0 | 3220.11 | 132794 | 0 | 72 | 77 | 132794 | -1000000
7 | 16 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.2393 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 74.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3219.33 | 0 | 3219.33 | 132513 | 0 | 72 | 76 | 132513 | -1000000
7 | 16 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.2254 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 74.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3218.5 | 0 | 3218.5 | 132235 | 0 | 72 | 76 | 132235 | -1000000
7 | 16 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.2123 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 3.2 | 72.5598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3217.69 | 0 | 3217.69 | 131971 | 0 | 72 | 76 | 131971 | -1000000
7 | 16 | 5 | 7 | 5.0869 | 0 | 42.7453 | 0 | 7.1996 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 1.6 | 70.9286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.91 | 0 | 3216.91 | 131716 | 0 | 72 | 77 | 131716 | -1000000
7 | 16 | 6 | 7 | 3.9963 | 0 | 42.7453 | 0 | 7.1928 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.14 | 0 | 3216.14 | 131582 | 0 | 73 | 77 | 131582 | -1000000
7 | 16 | 7 | 7 | 3.6966 | 0 | 42.7453 | 0 | 7.1817 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 67.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.38 | 0 | 3215.38 | 131357 | 0 | 73 | 79 | 131357 | -1000000
7 | 16 | 8 | 7 | 3.799 | 0 | 42.7453 | 0 | 14.7827 | 0 | 5.8061 | 15.3158 | 0 | 0 | 0 | 0 | 82.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.5 | 0 | 3214.5 | 286744 | 0 | 74 | 81 | 286744 | -1000000
7 | 16 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 15.2909 | 0 | 5.8501 | 15.3158 | 0 | 0 | 0 | 0 | 83.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213.06 | 0 | 3213.06 | 294506 | 0 | 74 | 83 | 294506 | -1000000
7 | 16 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 15.6921 | 0 | 5.8868 | 15.3158 | 0 | 0 | 0 | 0 | 83.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3211.45 | 0 | 3211.45 | 302582 | 0 | 75 | 86 | 302582 | -1000000
7 | 16 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 16.2506 | 0 | 5.9138 | 15.3158 | 0 | 0 | 0 | 0 | 84.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3211.57 | 0 | 3211.57 | 313801 | 0 | 76 | 88 | 313801 | -1000000
7 | 16 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 16.7601 | 0 | 5.9138 | 14.8767 | 0 | 0 | 0 | 0 | 84.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3210.08 | 0 | 3210.08 | 323897 | 0 | 76 | 91 | 323897 | -1000000
7 | 16 | 13 | 7 | 4.144 | 0 | 42.7453 | 0 | 17.0003 | 0 | 5.9138 | 14.8767 | 0 | 0 | 0 | 0 | 84.6801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3209 | 0 | 3209 | 328573 | 0 | 75 | 85 | 328573 | -1000000
7 | 16 | 14 | 7 | 4.1462 | 0 | 42.7453 | 0 | 16.6655 | 0 | 24.9169 | 14.8767 | 0 | 0 | 0 | 0 | 103.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3207.07 | 0 | 3207.07 | 313573 | 0 | 73 | 80 | 313573 | -1000000
7 | 16 | 15 | 7 | 4.8004 | 0 | 42.7453 | 0 | 7.406 | 0 | 7.1383 | 8.818 | 0 | 0 | 0 | 0 | 70.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.13 | 0 | 3203.13 | 130047 | 0 | 71 | 74 | 130047 | -1000000
7 | 16 | 16 | 7 | 4.1484 | 0 | 42.7453 | 0 | 13.0193 | 0 | 15.3727 | 12.8287 | 0 | 0 | 0 | 0 | 88.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3201.11 | 0 | 3201.11 | 235805 | 0 | 71 | 75 | 235805 | -1000000
7 | 16 | 17 | 7 | 4.1522 | 0 | 42.7453 | 0 | 10.568 | 0 | 11.1063 | 10.866 | 0 | 0 | 0 | 0 | 79.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3199.17 | 0 | 3199.17 | 197808 | 0 | 73 | 77 | 197808 | -1000000
7 | 16 | 18 | 7 | 4.5501 | 0 | 42.7453 | 0 | 7.1781 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3198.41 | 0 | 3198.41 | 130162 | 0 | 74 | 78 | 130162 | -1000000
7 | 16 | 19 | 7 | 5.2657 | 0 | 42.7453 | 0 | 7.1104 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 1.2 | 70.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3197.36 | 0 | 3197.36 | 129925 | 0 | 73 | 76 | 129925 | -1000000
7 | 16 | 20 | 7 | 6.5534 | 0 | 42.7453 | 0 | 12.1023 | 0 | 5.62 | 12.8287 | 0 | 0 | 0 | 4 | 83.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3196.25 | 0 | 3196.25 | 231949 | 0 | 72 | 75 | 231949 | -1000000
7 | 16 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.5363 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 7.2 | 77.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3195.21 | 0 | 3195.21 | 129533 | 0 | 72 | 73 | 129533 | -1000000
7 | 16 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.9954 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 77.1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3194.4 | 0 | 3194.4 | 129342 | 0 | 71 | 73 | 129342 | -1000000
7 | 16 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.991 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 76.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3193.92 | 0 | 3193.92 | 129254 | 0 | 71 | 73 | 129254 | -1000000
7 | 16 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 7.0058 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8346.68 | 0 | 8346.68 | 129563 | 0 | 72 | 73 | 129563 | -1000000
7 | 17 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.6813 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8346.23 | 0 | 8346.23 | 129390 | 0 | 71 | 72 | 129390 | -1000000
7 | 17 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.9499 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8344.92 | 0 | 8344.92 | 129273 | 0 | 71 | 72 | 129273 | -1000000
7 | 17 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.6257 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 78.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8344.05 | 0 | 8344.05 | 129065 | 0 | 70 | 71 | 129065 | -1000000
7 | 17 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 7.1056 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9256.12 | 0 | 9256.12 | 133402 | 0 | 71 | 71 | 133402 | -1000000
7 | 17 | 5 | 1 | 24.2496 | 0 | 69.9783 | 0 | 14.7907 | 0 | 5.7869 | 12.8287 | 0 | 0 | 0 | 1.6 | 129.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11287.3 | 0 | 11287.3 | 286723 | 0 | 70 | 72 | 286723 | -1000000
7 | 17 | 6 | 1 | 45.7951 | 0 | 140.608 | 0 | 91.1239 | 0 | 5.9138 | 26.1265 | 0 | 0 | 0 | 0 | 309.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30427.8 | 0 | 30427.8 | 1790970 | 0 | 71 | 72 | 1790970 | -1000000
7 | 17 | 7 | 1 | 42.5949 | 0 | 168.222 | 0 | 91.5122 | 0 | 6.332 | 24.6692 | 0 | 0 | 0 | 0 | 333.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33368.2 | 0 | 33368.2 | 1755390 | -26830.2 | 71 | 73 | 1755390 | -1026830.2
7 | 17 | 8 | 1 | 40.0395 | 0 | 173.795 | 0 | 90.636 | 0 | 6.332 | 24.0857 | 0 | 0 | 0 | 0 | 334.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42242 | 0 | 42242 | 1611620 | -29158.7 | 71 | 73 | 1611620 | -1029158.7
7 | 17 | 9 | 1 | 41.3104 | 0 | 172.186 | 0 | 82.1144 | 0 | 6.332 | 24.7495 | 0 | 0 | 0 | 0 | 326.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65805.7 | 0 | 65805.7 | 1570770 | -20774.1 | 71 | 74 | 1570770 | -1020774.1
7 | 17 | 10 | 1 | 41.5619 | 0 | 163.102 | 0 | 83.9636 | 0 | 6.332 | 24.2688 | 0 | 0 | 0 | 0 | 319.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67279.7 | 0 | 67279.7 | 1613700 | -18342.8 | 72 | 75 | 1613700 | -1018342.8
7 | 17 | 11 | 1 | 40.9253 | 0 | 149.692 | 0 | 74.0036 | 0 | 6.3927 | 24.3426 | 0 | 0 | 0 | 0 | 295.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67281 | 0 | 67281 | 1452820 | -14704.8 | 72 | 77 | 1452820 | -1014704.8
7 | 17 | 12 | 1 | 39.7954 | 0 | 150.207 | 0 | 78.162 | 0 | 18.2107 | 24.1124 | 0 | 0 | 0 | 0 | 310.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67283.1 | 0 | 67283.1 | 1533820 | -13783.8 | 73 | 78 | 1533820 | -1013783.8
7 | 17 | 13 | 1 | 41.4377 | 0 | 165.698 | 0 | 86.6086 | 0 | 25.335 | 24.1726 | 0 | 0 | 0 | 0 | 343.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67284.7 | 0 | 67284.7 | 1649290 | -17123.3 | 73 | 78 | 1649290 | -1017123.3
7 | 17 | 14 | 1 | 40.7489 | 0 | 172.702 | 0 | 93.3337 | 0 | 25.335 | 23.9362 | 0 | 0 | 0 | 0 | 356.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65813.7 | 0 | 65813.7 | 1697190 | -20740 | 74 | 79 | 1697190 | -1020740
7 | 17 | 15 | 1 | 40.5745 | 0 | 173.986 | 0 | 98.1451 | 0 | 25.335 | 24.1866 | 0 | 0 | 0 | 0 | 362.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59924.9 | 0 | 59924.9 | 1732900 | -22084.1 | 74 | 79 | 1732900 | -1022084.1
7 | 17 | 16 | 1 | 40.3008 | 0 | 169.782 | 0 | 100.626 | 0 | 25.335 | 24.1143 | 0 | 0 | 0 | 0 | 360.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49618.2 | 0 | 49618.2 | 1747960 | -20914.6 | 74 | 80 | 1747960 | -1020914.6
7 | 17 | 17 | 1 | 35.4895 | 0 | 152.497 | 0 | 93.7214 | 0 | 25.335 | 23.8437 | 0 | 0 | 0 | 0 | 330.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37838.8 | 0 | 37838.8 | 1656840 | -19567.6 | 74 | 80 | 1656840 | -1019567.6
7 | 17 | 18 | 1 | 24.602 | 0 | 93.4203 | 0 | 72.5852 | 0 | 14.2987 | 22.018 | 0 | 0 | 0 | 0 | 226.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23115.4 | 0 | 23115.4 | 1251230 | -25284.9 | 74 | 81 | 1251230 | -1025284.9
7 | 17 | 19 | 1 | 18.8248 | 0 | 62.7906 | 0 | 11.0607 | 0 | 5.5684 | 8.818 | 0 | 0 | 0 | 1.2 | 108.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16490.5 | 0 | 16490.5 | 191646 | 0 | 74 | 79 | 191646 | -1000000
7 | 17 | 20 | 1 | 18.1773 | 0 | 54.6418 | 0 | 9.1649 | 0 | 5.5044 | 8.818 | 0 | 0 | 0 | 4 | 100.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15755.3 | 0 | 15755.3 | 170859 | 0 | 73 | 77 | 170859 | -1000000
7 | 17 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 8.5124 | 0 | 5.4913 | 8.818 | 0 | 0 | 0 | 7.2 | 92.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.64 | 0 | 9849.64 | 157879 | 0 | 73 | 75 | 157879 | -1000000
7 | 17 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.9774 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 6.4 | 84.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9610.08 | 0 | 9610.08 | 147167 | 0 | 73 | 75 | 147167 | -1000000
7 | 17 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.4035 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 5.6 | 80.1588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8369.93 | 0 | 8369.93 | 142264 | 0 | 73 | 74 | 142264 | -1000000
7 | 17 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.6108 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8368.61 | 0 | 8368.61 | 140899 | 0 | 73 | 74 | 140899 | -1000000
7 | 18 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.5683 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8367.51 | 0 | 8367.51 | 140048 | 0 | 72 | 74 | 140048 | -1000000
7 | 18 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.5305 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8366.56 | 0 | 8366.56 | 139285 | 0 | 71 | 74 | 139285 | -1000000
7 | 18 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.5003 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8365.65 | 0 | 8365.65 | 138678 | 0 | 71 | 74 | 138678 | -1000000
7 | 18 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 7.6828 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 3.2 | 81.8262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9277.64 | 0 | 9277.64 | 142439 | 0 | 71 | 74 | 142439 | -1000000
7 | 18 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.7992 | 0 | 5.7941 | 12.8287 | 0 | 0 | 0 | 1.6 | 129.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11308.7 | 0 | 11308.7 | 296324 | 0 | 70 | 73 | 296324 | -1000000
7 | 18 | 6 | 2 | 44.746 | 0 | 140.608 | 0 | 81.7852 | 0 | 5.9138 | 24.783 | 0 | 0 | 0 | 0 | 297.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30448.9 | 0 | 30448.9 | 1604070 | 0 | 70 | 73 | 1604070 | -1000000
7 | 18 | 7 | 2 | 39.0412 | 0 | 168.222 | 0 | 89.9376 | 0 | 25.335 | 24.7755 | 0 | 0 | 0 | 0 | 347.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33389.1 | 0 | 33389.1 | 1642070 | -24170.7 | 71 | 75 | 1642070 | -1024170.7
7 | 18 | 8 | 2 | 39.6631 | 0 | 173.795 | 0 | 94.8277 | 0 | 25.335 | 23.0262 | 0 | 0 | 0 | 0 | 356.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42252.2 | 0 | 42252.2 | 1620710 | -23760.7 | 72 | 77 | 1620710 | -1023760.7
7 | 18 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 98.8384 | 0 | 25.335 | 23.0849 | 0 | 0 | 0 | 0 | 360.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65815.2 | 0 | 65815.2 | 1671970 | -23468.6 | 73 | 79 | 1671970 | -1023468.6
7 | 18 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 100.189 | 0 | 25.335 | 23.4646 | 0 | 0 | 0 | 0 | 353.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67291.3 | 0 | 67291.3 | 1690530 | -19840.1 | 73 | 81 | 1690530 | -1019840.1
7 | 18 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 91.3925 | 0 | 25.335 | 23.4869 | 0 | 0 | 0 | 0 | 330.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67293 | 0 | 67293 | 1542240 | -17922.7 | 73 | 83 | 1542240 | -1017922.7
7 | 18 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 101.3 | 0 | 25.335 | 23.245 | 0 | 0 | 0 | 0 | 339.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67294.2 | 0 | 67294.2 | 1667720 | -27998.9 | 74 | 85 | 1667720 | -1027998.9
7 | 18 | 13 | 2 | 41.233 | 0 | 165.698 | 0 | 112.962 | 0 | 25.335 | 23.5079 | 0 | 0 | 0 | 0 | 368.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67294.8 | 0 | 67294.8 | 1792850 | -33033.6 | 74 | 86 | 1792850 | -1033033.6
7 | 18 | 14 | 2 | 40.6372 | 0 | 172.702 | 0 | 111.713 | 0 | 25.335 | 23.3855 | 0 | 0 | 0 | 0 | 373.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65822.6 | 0 | 65822.6 | 1793270 | -33129.3 | 74 | 86 | 1793270 | -1033129.3
7 | 18 | 15 | 2 | 40.5352 | 0 | 173.986 | 0 | 112.953 | 0 | 25.335 | 23.5687 | 0 | 0 | 0 | 0 | 376.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59933.2 | 0 | 59933.2 | 1798200 | -33432.8 | 73 | 87 | 1798200 | -1033432.8
7 | 18 | 16 | 2 | 40.2862 | 0 | 169.782 | 0 | 113.456 | 0 | 25.335 | 23.7887 | 0 | 0 | 0 | 0 | 372.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49626.2 | 0 | 49626.2 | 1800350 | -33394.7 | 73 | 86 | 1800350 | -1033394.7
7 | 18 | 17 | 2 | 35.469 | 0 | 152.497 | 0 | 108.209 | 0 | 14.8052 | 23.3625 | 0 | 0 | 0 | 0 | 334.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37846.8 | 0 | 37846.8 | 1672730 | -36699.1 | 72 | 84 | 1672730 | -1036699.1
7 | 18 | 18 | 2 | 24.5877 | 0 | 93.4203 | 0 | 83.7222 | 0 | 6.7504 | 21.762 | 0 | 0 | 0 | 0 | 230.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23122.6 | 0 | 23122.6 | 1248050 | -42511.3 | 72 | 83 | 1248050 | -1042511.3
7 | 18 | 19 | 2 | 18.141 | 0 | 62.7906 | 0 | 12.2579 | 0 | 12.9923 | 8.818 | 0 | 0 | 0 | 1.2 | 116.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16496.9 | 0 | 16496.9 | 195351 | 0 | 70 | 81 | 195351 | -1000000
7 | 18 | 20 | 2 | 18.0987 | 0 | 54.6418 | 0 | 9.9935 | 0 | 9.7146 | 8.818 | 0 | 0 | 0 | 4 | 105.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15761.4 | 0 | 15761.4 | 174777 | 0 | 69 | 78 | 174777 | -1000000
7 | 18 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.6829 | 0 | 5.6101 | 8.818 | 0 | 0 | 0 | 7.2 | 93.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.2 | 0 | 9856.2 | 161297 | 0 | 67 | 76 | 161297 | -1000000
7 | 18 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.4809 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9616.63 | 0 | 9616.63 | 150264 | 0 | 66 | 73 | 150264 | -1000000
7 | 18 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1409 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376.53 | 0 | 8376.53 | 145199 | 0 | 65 | 71 | 145199 | -1000000
7 | 18 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.6725 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 78.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8375.27 | 0 | 8375.27 | 143665 | 0 | 64 | 68 | 143665 | -1000000
7 | 19 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1227 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8374.36 | 0 | 8374.36 | 142734 | 0 | 64 | 67 | 142734 | -1000000
7 | 19 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0306 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8373.69 | 0 | 8373.69 | 141632 | 0 | 63 | 66 | 141632 | -1000000
7 | 19 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9617 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8373.2 | 0 | 8373.2 | 141010 | 0 | 63 | 65 | 141010 | -1000000
7 | 19 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.3645 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 3.2 | 81.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9285.73 | 0 | 9285.73 | 144037 | 0 | 63 | 65 | 144037 | -1000000
7 | 19 | 5 | 3 | 24.2276 | 0 | 69.9783 | 0 | 13.7255 | 0 | 5.678 | 12.8287 | 0 | 0 | 0 | 1.6 | 128.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11317.3 | 0 | 11317.3 | 274502 | 0 | 63 | 66 | 274502 | -1000000
7 | 19 | 6 | 3 | 39.4753 | 0 | 140.608 | 0 | 56.348 | 0 | 7.4488 | 23.2635 | 0 | 0 | 0 | 0 | 267.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30458.2 | 0 | 30458.2 | 1166400 | -4962.68 | 63 | 66 | 1166400 | -1004962.68
7 | 19 | 7 | 3 | 39.0994 | 0 | 168.222 | 0 | 72.06 | 0 | 25.335 | 22.3614 | 0 | 0 | 0 | 0 | 327.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33399 | 0 | 33399 | 1281090 | -28176.5 | 64 | 69 | 1281090 | -1028176.5
7 | 19 | 8 | 3 | 39.7625 | 0 | 173.795 | 0 | 74.2843 | 0 | 25.335 | 21.7433 | 0 | 0 | 0 | 0 | 334.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42257.5 | 0 | 42257.5 | 1283790 | -26667.7 | 65 | 72 | 1283790 | -1026667.7
7 | 19 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 77.2215 | 0 | 25.335 | 22.024 | 0 | 0 | 0 | 0 | 337.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65821.7 | 0 | 65821.7 | 1300490 | -25774.1 | 65 | 75 | 1300490 | -1025774.1
7 | 19 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 76.6742 | 0 | 25.335 | 22.3917 | 0 | 0 | 0 | 0 | 328.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67296.7 | 0 | 67296.7 | 1306350 | -21845.9 | 65 | 77 | 1306350 | -1021845.9
7 | 19 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 70.4243 | 0 | 25.335 | 22.9998 | 0 | 0 | 0 | 0 | 309.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298 | 0 | 67298 | 1196510 | -17369.1 | 65 | 78 | 1196510 | -1017369.1
7 | 19 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 71.7808 | 0 | 25.335 | 22.936 | 0 | 0 | 0 | 0 | 310.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.6 | 0 | 67298.6 | 1213670 | -25544.3 | 64 | 80 | 1213670 | -1025544.3
7 | 19 | 13 | 3 | 41.2562 | 0 | 165.698 | 0 | 77.214 | 0 | 25.335 | 23.6375 | 0 | 0 | 0 | 0 | 333.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.7 | 0 | 67298.7 | 1295260 | -18981.8 | 64 | 81 | 1295260 | -1018981.8
7 | 19 | 14 | 3 | 40.6703 | 0 | 172.702 | 0 | 79.5634 | 0 | 25.335 | 23.2493 | 0 | 0 | 0 | 0 | 341.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65826.1 | 0 | 65826.1 | 1330250 | -23384 | 64 | 81 | 1330250 | -1023384
7 | 19 | 15 | 3 | 40.5663 | 0 | 173.986 | 0 | 81.9616 | 0 | 25.335 | 23.4136 | 0 | 0 | 0 | 0 | 345.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59936.7 | 0 | 59936.7 | 1374810 | -24879.7 | 64 | 82 | 1374810 | -1024879.7
7 | 19 | 16 | 3 | 40.307 | 0 | 169.782 | 0 | 80.6522 | 0 | 25.335 | 23.4444 | 0 | 0 | 0 | 0 | 339.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49629.5 | 0 | 49629.5 | 1366960 | -28407.9 | 64 | 82 | 1366960 | -1028407.9
7 | 19 | 17 | 3 | 35.4764 | 0 | 152.497 | 0 | 79.4166 | 0 | 25.335 | 22.9646 | 0 | 0 | 0 | 0 | 315.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37849.8 | 0 | 37849.8 | 1295980 | -35853 | 64 | 81 | 1295980 | -1035853
7 | 19 | 18 | 3 | 24.5871 | 0 | 93.4203 | 0 | 60.0709 | 0 | 15.5415 | 21.5821 | 0 | 0 | 0 | 0 | 215.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23125.4 | 0 | 23125.4 | 957911 | -37980.5 | 64 | 81 | 957911 | -1037980.5
7 | 19 | 19 | 3 | 18.5266 | 0 | 62.7906 | 0 | 12.0891 | 0 | 12.6281 | 8.818 | 0 | 0 | 0 | 1.2 | 116.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16499.6 | 0 | 16499.6 | 196080 | 0 | 65 | 77 | 196080 | -1000000
7 | 19 | 20 | 3 | 17.6781 | 0 | 54.6418 | 0 | 9.1833 | 0 | 8.4631 | 8.818 | 0 | 0 | 0 | 4 | 102.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15763.9 | 0 | 15763.9 | 175542 | 0 | 64 | 72 | 175542 | -1000000
7 | 19 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.7173 | 0 | 7.2058 | 8.818 | 0 | 0 | 0 | 7.2 | 93.6614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860 | 0 | 9860 | 162031 | 0 | 63 | 68 | 162031 | -1000000
7 | 19 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.351 | 0 | 7.0183 | 8.818 | 0 | 0 | 0 | 6.4 | 85.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9621.06 | 0 | 9621.06 | 150764 | 0 | 62 | 66 | 150764 | -1000000
7 | 19 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.0223 | 0 | 6.7605 | 8.818 | 0 | 0 | 0 | 5.6 | 81.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.6 | 0 | 8381.6 | 145669 | 0 | 61 | 64 | 145669 | -1000000
7 | 19 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8631 | 0 | 6.6251 | 8.818 | 0 | 0 | 0 | 4.8 | 80.1666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.98 | 0 | 8380.98 | 143954 | 0 | 60 | 62 | 143954 | -1000000
7 | 20 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0446 | 0 | 6.7054 | 8.818 | 0 | 0 | 0 | 4.8 | 80.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.64 | 0 | 8380.64 | 143003 | 0 | 60 | 61 | 143003 | -1000000
7 | 20 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.253 | 0 | 6.8279 | 8.818 | 0 | 0 | 0 | 4.8 | 80.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.41 | 0 | 8380.41 | 141833 | 0 | 59 | 61 | 141833 | -1000000
7 | 20 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9174 | 0 | 6.613 | 8.818 | 0 | 0 | 0 | 4.8 | 80.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.22 | 0 | 8380.22 | 141069 | 0 | 59 | 60 | 141069 | -1000000
7 | 20 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.3129 | 0 | 6.8395 | 8.818 | 0 | 0 | 0 | 3.2 | 82.8149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9292.69 | 0 | 9292.69 | 144001 | 0 | 59 | 60 | 144001 | -1000000
7 | 20 | 5 | 4 | 24.2485 | 0 | 69.9783 | 0 | 12.6304 | 0 | 12.7485 | 12.8287 | 0 | 0 | 0 | 1.6 | 134.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11324.6 | 0 | 11324.6 | 259989 | 0 | 59 | 60 | 259989 | -1000000
7 | 20 | 6 | 4 | 46.1978 | 0 | 140.608 | 0 | 45.1177 | 0 | 25.335 | 21.4691 | 0 | 0 | 0 | 0 | 278.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30465.8 | 0 | 30465.8 | 905181 | -7446.92 | 59 | 60 | 905181 | -1007446.92
7 | 20 | 7 | 4 | 38.9976 | 0 | 168.222 | 0 | 60.3429 | 0 | 25.335 | 22.0101 | 0 | 0 | 0 | 0 | 314.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33406.9 | 0 | 33406.9 | 1077340 | -29421.1 | 62 | 65 | 1077340 | -1029421.1
7 | 20 | 8 | 4 | 39.6782 | 0 | 173.795 | 0 | 66.8714 | 0 | 25.335 | 22.129 | 0 | 0 | 0 | 0 | 327.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42261.5 | 0 | 42261.5 | 1148630 | -27358.3 | 64 | 70 | 1148630 | -1027358.3
7 | 20 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 74.6363 | 0 | 25.335 | 22.0967 | 0 | 0 | 0 | 0 | 334.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65822.8 | 0 | 65822.8 | 1234880 | -25829.2 | 65 | 75 | 1234880 | -1025829.2
7 | 20 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 75.9839 | 0 | 25.335 | 22.3774 | 0 | 0 | 0 | 0 | 327.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.2 | 0 | 67297.2 | 1282440 | -21729.2 | 66 | 77 | 1282440 | -1021729.2
7 | 20 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 72.3419 | 0 | 25.335 | 22.7352 | 0 | 0 | 0 | 0 | 310.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.6 | 0 | 67299.6 | 1215990 | -17006.8 | 67 | 78 | 1215990 | -1017006.8
7 | 20 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 77.0315 | 0 | 25.335 | 23.105 | 0 | 0 | 0 | 0 | 315.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300 | 0 | 67300 | 1284510 | -15546.5 | 68 | 80 | 1284510 | -1015546.5
7 | 20 | 13 | 4 | 41.252 | 0 | 165.698 | 0 | 84.2005 | 0 | 25.335 | 23.7762 | 0 | 0 | 0 | 0 | 340.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.4 | 0 | 67300.4 | 1397380 | -19179.7 | 68 | 80 | 1397380 | -1019179.7
7 | 20 | 14 | 4 | 40.6307 | 0 | 172.702 | 0 | 86.9593 | 0 | 25.335 | 23.4186 | 0 | 0 | 0 | 0 | 349.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65828 | 0 | 65828 | 1437660 | -23408.9 | 68 | 81 | 1437660 | -1023408.9
7 | 20 | 15 | 4 | 40.506 | 0 | 173.986 | 0 | 89.1861 | 0 | 25.335 | 23.5325 | 0 | 0 | 0 | 0 | 352.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59938 | 0 | 59938 | 1477020 | -24942.9 | 68 | 81 | 1477020 | -1024942.9
7 | 20 | 16 | 4 | 40.2778 | 0 | 169.782 | 0 | 89.4258 | 0 | 25.335 | 23.6419 | 0 | 0 | 0 | 0 | 348.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49630.9 | 0 | 49630.9 | 1511460 | -24648.4 | 69 | 81 | 1511460 | -1024648.4
7 | 20 | 17 | 4 | 35.49 | 0 | 152.497 | 0 | 81.574 | 0 | 25.335 | 23.6303 | 0 | 0 | 0 | 0 | 318.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37851.3 | 0 | 37851.3 | 1402840 | -19731.6 | 69 | 80 | 1402840 | -1019731.6
7 | 20 | 18 | 4 | 24.7072 | 0 | 93.4203 | 0 | 60.0507 | 0 | 25.335 | 21.9388 | 0 | 0 | 0 | 0 | 225.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127 | 0 | 23127 | 1045910 | -19444.6 | 70 | 80 | 1045910 | -1019444.6
7 | 20 | 19 | 4 | 18.6373 | 0 | 62.7906 | 0 | 12.1248 | 0 | 12.7312 | 8.818 | 0 | 0 | 0 | 1.2 | 116.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16501 | 0 | 16501 | 195940 | 0 | 69 | 78 | 195940 | -1000000
7 | 20 | 20 | 4 | 17.8578 | 0 | 54.6418 | 0 | 10.2403 | 0 | 9.8617 | 8.818 | 0 | 0 | 0 | 4 | 105.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15765.5 | 0 | 15765.5 | 175375 | 0 | 68 | 77 | 175375 | -1000000
7 | 20 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 9.3906 | 0 | 8.9284 | 8.818 | 0 | 0 | 0 | 7.2 | 97.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.87 | 0 | 9861.87 | 161947 | 0 | 67 | 75 | 161947 | -1000000
7 | 20 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 8.1634 | 0 | 6.0709 | 8.818 | 0 | 0 | 0 | 6.4 | 84.9829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9622.98 | 0 | 9622.98 | 150899 | 0 | 67 | 75 | 150899 | -1000000
7 | 20 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.5858 | 0 | 5.9328 | 8.818 | 0 | 0 | 0 | 5.6 | 80.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.31 | 0 | 8383.31 | 145949 | 0 | 67 | 74 | 145949 | -1000000
7 | 20 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.7801 | 0 | 5.9746 | 8.818 | 0 | 0 | 0 | 4.8 | 80.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.28 | 0 | 8382.28 | 144315 | 0 | 67 | 74 | 144315 | -1000000
7 | 21 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.4019 | 0 | 5.8941 | 8.818 | 0 | 0 | 0 | 4.8 | 80.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.37 | 0 | 8381.37 | 143208 | 0 | 66 | 73 | 143208 | -1000000
7 | 21 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.6417 | 0 | 5.9438 | 8.818 | 0 | 0 | 0 | 4.8 | 80.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.56 | 0 | 8380.56 | 142476 | 0 | 66 | 73 | 142476 | -1000000
7 | 21 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2747 | 0 | 5.8681 | 8.818 | 0 | 0 | 0 | 4.8 | 79.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.74 | 0 | 8379.74 | 141517 | 0 | 65 | 72 | 141517 | -1000000
7 | 21 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.7134 | 0 | 5.9583 | 8.818 | 0 | 0 | 0 | 3.2 | 82.3341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9291.85 | 0 | 9291.85 | 144950 | 0 | 65 | 72 | 144950 | -1000000
7 | 21 | 5 | 5 | 24.2359 | 0 | 69.9783 | 0 | 14.4975 | 0 | 9.2881 | 12.8287 | 0 | 0 | 0 | 1.6 | 132.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11323 | 0 | 11323 | 286132 | 0 | 65 | 72 | 286132 | -1000000
7 | 21 | 6 | 5 | 39.9288 | 0 | 140.608 | 0 | 71.2182 | 0 | 25.335 | 23.8757 | 0 | 0 | 0 | 0 | 300.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30463.4 | 0 | 30463.4 | 1274870 | -3722.53 | 65 | 72 | 1274870 | -1003722.53
7 | 21 | 7 | 5 | 39.0929 | 0 | 168.222 | 0 | 85.1071 | 0 | 25.335 | 22.652 | 0 | 0 | 0 | 0 | 340.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33403.8 | 0 | 33403.8 | 1431210 | -26793.6 | 67 | 75 | 1431210 | -1026793.6
7 | 21 | 8 | 5 | 39.7612 | 0 | 173.795 | 0 | 86.7081 | 0 | 25.335 | 22.0197 | 0 | 0 | 0 | 0 | 347.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42261 | 0 | 42261 | 1469930 | -26031.2 | 69 | 79 | 1469930 | -1026031.2
7 | 21 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 92.9956 | 0 | 25.335 | 22.4979 | 0 | 0 | 0 | 0 | 353.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65825.2 | 0 | 65825.2 | 1569820 | -25313 | 71 | 82 | 1569820 | -1025313
7 | 21 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 97.7679 | 0 | 25.335 | 23.0924 | 0 | 0 | 0 | 0 | 350.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.9 | 0 | 67299.9 | 1635820 | -21066.5 | 72 | 85 | 1635820 | -1021066.5
7 | 21 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 93.5276 | 0 | 25.335 | 23.0918 | 0 | 0 | 0 | 0 | 332.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.9 | 0 | 67300.9 | 1573290 | -21256.2 | 74 | 87 | 1573290 | -1021256.2
7 | 21 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 113.452 | 0 | 10.5073 | 22.7335 | 0 | 0 | 0 | 0 | 336.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67301.6 | 0 | 67301.6 | 1719410 | -34522.3 | 75 | 90 | 1719410 | -1034522.3
7 | 21 | 13 | 5 | 41.2383 | 0 | 165.698 | 0 | 119.089 | 0 | 25.335 | 23.1753 | 0 | 0 | 0 | 0 | 374.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67301.6 | 0 | 67301.6 | 1836570 | -33075.2 | 75 | 90 | 1836570 | -1033075.2
7 | 21 | 14 | 5 | 40.6433 | 0 | 172.702 | 0 | 117.758 | 0 | 25.335 | 23.0987 | 0 | 0 | 0 | 0 | 379.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65829.2 | 0 | 65829.2 | 1837290 | -33184.6 | 75 | 90 | 1837290 | -1033184.6
7 | 21 | 15 | 5 | 40.6901 | 0 | 173.986 | 0 | 118.266 | 0 | 25.335 | 23.4946 | 0 | 0 | 0 | 0 | 381.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59939.7 | 0 | 59939.7 | 1839980 | -33119.2 | 75 | 90 | 1839980 | -1033119.2
7 | 21 | 16 | 5 | 40.2978 | 0 | 169.782 | 0 | 114.803 | 0 | 25.335 | 23.5839 | 0 | 0 | 0 | 0 | 373.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49632.4 | 0 | 49632.4 | 1841250 | -33669.9 | 75 | 83 | 1841250 | -1033669.9
7 | 21 | 17 | 5 | 35.9046 | 0 | 152.497 | 0 | 97.8069 | 0 | 25.335 | 23.0552 | 0 | 0 | 0 | 0 | 334.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37852.5 | 0 | 37852.5 | 1583300 | -37933.4 | 72 | 77 | 1583300 | -1037933.4
7 | 21 | 18 | 5 | 24.926 | 0 | 93.4203 | 0 | 51.9527 | 0 | 25.335 | 21.6841 | 0 | 0 | 0 | 0 | 217.318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23128 | 0 | 23128 | 967068 | -17587.9 | 69 | 70 | 967068 | -1017587.9
7 | 21 | 19 | 5 | 18.2613 | 0 | 62.7906 | 0 | 11.4224 | 0 | 11.3507 | 8.818 | 0 | 0 | 0 | 1.2 | 113.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16501.9 | 0 | 16501.9 | 196678 | 0 | 69 | 70 | 196678 | -1000000
7 | 21 | 20 | 5 | 18.016 | 0 | 54.6418 | 0 | 9.4754 | 0 | 5.507 | 8.818 | 0 | 0 | 0 | 4 | 100.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15766.1 | 0 | 15766.1 | 176152 | 0 | 69 | 71 | 176152 | -1000000
7 | 21 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.5405 | 0 | 5.4889 | 8.818 | 0 | 0 | 0 | 7.2 | 92.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.61 | 0 | 9862.61 | 162638 | 0 | 68 | 71 | 162638 | -1000000
7 | 21 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.6746 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 6.4 | 83.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9624.4 | 0 | 9624.4 | 151404 | 0 | 67 | 70 | 151404 | -1000000
7 | 21 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.6931 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 5.6 | 80.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.06 | 0 | 8385.06 | 146274 | 0 | 67 | 70 | 146274 | -1000000
7 | 21 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.2793 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8384.32 | 0 | 8384.32 | 144257 | 0 | 66 | 69 | 144257 | -1000000
7 | 22 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8666 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 75.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.67 | 0 | 8383.67 | 142946 | 0 | 64 | 67 | 142946 | -1000000
7 | 22 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.748 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.76 | 0 | 8383.76 | 142068 | 0 | 63 | 65 | 142068 | -1000000
7 | 22 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6231 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.56 | 0 | 8383.56 | 140965 | 0 | 61 | 63 | 140965 | -1000000
7 | 22 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.1132 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 3.2 | 73.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.5 | 0 | 8383.5 | 140300 | 0 | 61 | 63 | 140300 | -1000000
7 | 22 | 5 | 6 | 6.3633 | 0 | 42.7453 | 0 | 6.7728 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.53 | 0 | 8383.53 | 139368 | 0 | 60 | 62 | 139368 | -1000000
7 | 22 | 6 | 6 | 5.1723 | 0 | 42.7453 | 0 | 7.5842 | 0 | 6.8771 | 8.818 | 0 | 0 | 0 | 0 | 71.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.68 | 0 | 8383.68 | 138463 | 0 | 59 | 62 | 138463 | -1000000
7 | 22 | 7 | 6 | 4.6147 | 0 | 42.7453 | 0 | 22.6762 | 0 | 25.335 | 19.2752 | 0 | 0 | 0 | 0 | 114.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.87 | 0 | 8383.87 | 449269 | -4601.37 | 60 | 65 | 449269 | -1004601.37
7 | 22 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 25.5569 | 0 | 25.335 | 19.214 | 0 | 0 | 0 | 0 | 117.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8384.02 | 0 | 8384.02 | 440774 | -6194.64 | 61 | 69 | 440774 | -1006194.64
7 | 22 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 26.2205 | 0 | 25.335 | 19.2077 | 0 | 0 | 0 | 0 | 118.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8400.27 | 0 | 8400.27 | 448786 | -10743.1 | 61 | 72 | 448786 | -1010743.1
7 | 22 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 28.3117 | 0 | 25.335 | 19.3398 | 0 | 0 | 0 | 0 | 121.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8403.11 | 0 | 8403.11 | 486085 | -11997.8 | 62 | 74 | 486085 | -1011997.8
7 | 22 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 30.6927 | 0 | 25.335 | 19.4263 | 0 | 0 | 0 | 0 | 123.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8405 | 0 | 8405 | 526237 | -16450.1 | 63 | 76 | 526237 | -1016450.1
7 | 22 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 31.845 | 0 | 25.335 | 19.5818 | 0 | 0 | 0 | 0 | 124.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8405.95 | 0 | 8405.95 | 548175 | -21988.9 | 63 | 78 | 548175 | -1021988.9
7 | 22 | 13 | 6 | 5.4712 | 0 | 42.7453 | 0 | 32.3312 | 0 | 25.335 | 19.6246 | 0 | 0 | 0 | 0 | 125.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8406.51 | 0 | 8406.51 | 556307 | -21810.4 | 63 | 79 | 556307 | -1021810.4
7 | 22 | 14 | 6 | 5.4718 | 0 | 42.7453 | 0 | 12.2813 | 0 | 12.5576 | 12.8287 | 0 | 0 | 0 | 0 | 85.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8406.79 | 0 | 8406.79 | 199326 | 0 | 63 | 81 | 199326 | -1000000
7 | 22 | 15 | 6 | 5.4711 | 0 | 42.7453 | 0 | 12.0888 | 0 | 12.2853 | 12.8287 | 0 | 0 | 0 | 0 | 85.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8407.3 | 0 | 8407.3 | 202886 | 0 | 63 | 82 | 202886 | -1000000
7 | 22 | 16 | 6 | 5.4711 | 0 | 42.7453 | 0 | 14.5451 | 0 | 17.5776 | 14.8767 | 0 | 0 | 0 | 0 | 95.2157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8399.85 | 0 | 8399.85 | 251045 | 0 | 62 | 80 | 251045 | -1000000
7 | 22 | 17 | 6 | 5.473 | 0 | 42.7453 | 0 | 8.103 | 0 | 7.5922 | 8.818 | 0 | 0 | 0 | 0 | 72.7314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.53 | 0 | 8395.53 | 133255 | 0 | 61 | 78 | 133255 | -1000000
7 | 22 | 18 | 6 | 5.4749 | 0 | 42.7453 | 0 | 7.9227 | 0 | 7.4774 | 8.818 | 0 | 0 | 0 | 0 | 72.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8392.38 | 0 | 8392.38 | 133019 | 0 | 60 | 76 | 133019 | -1000000
7 | 22 | 19 | 6 | 6.7103 | 0 | 42.7453 | 0 | 7.5285 | 0 | 7.1755 | 8.818 | 0 | 0 | 0 | 1.2 | 74.1775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8389.88 | 0 | 8389.88 | 133279 | 0 | 62 | 74 | 133279 | -1000000
7 | 22 | 20 | 6 | 8.5363 | 0 | 42.7453 | 0 | 6.2731 | 0 | 5.6969 | 8.818 | 0 | 0 | 0 | 4 | 76.0696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.07 | 0 | 8388.07 | 133037 | 0 | 63 | 71 | 133037 | -1000000
7 | 22 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4603 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 7.2 | 79.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8386.65 | 0 | 8386.65 | 132849 | 0 | 64 | 69 | 132849 | -1000000
7 | 22 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3607 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.59 | 0 | 8385.59 | 132304 | 0 | 63 | 67 | 132304 | -1000000
7 | 22 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.2707 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 5.6 | 77.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8384.74 | 0 | 8384.74 | 131906 | 0 | 62 | 65 | 131906 | -1000000
7 | 22 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.1851 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3230.66 | 0 | 3230.66 | 131543 | 0 | 62 | 63 | 131543 | -1000000
7 | 23 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6806 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3230.02 | 0 | 3230.02 | 130984 | 0 | 61 | 63 | 130984 | -1000000
7 | 23 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3739 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3229.64 | 0 | 3229.64 | 130742 | 0 | 61 | 62 | 130742 | -1000000
7 | 23 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6163 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3229.28 | 0 | 3229.28 | 130376 | 0 | 61 | 62 | 130376 | -1000000
7 | 23 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6008 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 3.2 | 71.9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.9 | 0 | 3228.9 | 130039 | 0 | 61 | 62 | 130039 | -1000000
7 | 23 | 5 | 7 | 5.097 | 0 | 42.7453 | 0 | 6.5927 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 1.6 | 70.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.56 | 0 | 3228.56 | 129866 | 0 | 62 | 62 | 129866 | -1000000
7 | 23 | 6 | 7 | 4.9414 | 0 | 42.7453 | 0 | 6.5715 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 0 | 68.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.17 | 0 | 3228.17 | 129404 | 0 | 62 | 62 | 129404 | -1000000
7 | 23 | 7 | 7 | 3.7739 | 0 | 42.7453 | 0 | 6.558 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 0 | 67.3777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.86 | 0 | 3227.86 | 129113 | 0 | 62 | 62 | 129113 | -1000000
7 | 23 | 8 | 7 | 4.1122 | 0 | 42.7453 | 0 | 6.5454 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 0 | 67.7036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.98 | 0 | 3227.98 | 128841 | 0 | 62 | 62 | 128841 | -1000000
7 | 23 | 9 | 7 | 4.9288 | 0 | 42.7453 | 0 | 6.5264 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 0 | 68.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.17 | 0 | 3228.17 | 128427 | 0 | 61 | 62 | 128427 | -1000000
7 | 23 | 10 | 7 | 4.4864 | 0 | 42.7453 | 0 | 7.1301 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 0 | 68.6588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.09 | 0 | 3228.09 | 128612 | 0 | 63 | 64 | 128612 | -1000000
7 | 23 | 11 | 7 | 4.3778 | 0 | 42.7453 | 0 | 7.2801 | 0 | 7.0007 | 8.818 | 0 | 0 | 0 | 0 | 70.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228 | 0 | 3228 | 128422 | 0 | 65 | 66 | 128422 | -1000000
7 | 23 | 12 | 7 | 4.2739 | 0 | 42.7453 | 0 | 7.7402 | 0 | 7.2069 | 8.818 | 0 | 0 | 0 | 0 | 70.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.98 | 0 | 3227.98 | 128320 | 0 | 67 | 68 | 128320 | -1000000
7 | 23 | 13 | 7 | 4.2664 | 0 | 42.7453 | 0 | 10.7574 | 0 | 9.9967 | 12.8287 | 0 | 0 | 0 | 0 | 80.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.41 | 0 | 3227.41 | 185859 | 0 | 67 | 69 | 185859 | -1000000
7 | 23 | 14 | 7 | 4.2375 | 0 | 42.7453 | 0 | 7.5103 | 0 | 6.9649 | 8.818 | 0 | 0 | 0 | 0 | 70.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3226.75 | 0 | 3226.75 | 127924 | 0 | 67 | 69 | 127924 | -1000000
7 | 23 | 15 | 7 | 4.3194 | 0 | 42.7453 | 0 | 7.7626 | 0 | 7.1749 | 8.818 | 0 | 0 | 0 | 0 | 70.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3225.77 | 0 | 3225.77 | 127862 | 0 | 67 | 70 | 127862 | -1000000
7 | 23 | 16 | 7 | 4.4304 | 0 | 42.7453 | 0 | 7.3832 | 0 | 6.9548 | 8.818 | 0 | 0 | 0 | 0 | 70.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.86 | 0 | 3224.86 | 127813 | 0 | 67 | 70 | 127813 | -1000000
7 | 23 | 17 | 7 | 4.6288 | 0 | 42.7453 | 0 | 6.7191 | 0 | 6.6542 | 8.818 | 0 | 0 | 0 | 0 | 69.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3223.73 | 0 | 3223.73 | 127763 | 0 | 67 | 69 | 127763 | -1000000
7 | 23 | 18 | 7 | 5.2463 | 0 | 42.7453 | 0 | 6.7534 | 0 | 6.7668 | 8.818 | 0 | 0 | 0 | 0 | 70.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3222.73 | 0 | 3222.73 | 127718 | 0 | 67 | 69 | 127718 | -1000000
7 | 23 | 19 | 7 | 5.4681 | 0 | 42.7453 | 0 | 9.9727 | 0 | 5.5171 | 12.8287 | 0 | 0 | 0 | 1.2 | 77.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3221.85 | 0 | 3221.85 | 195913 | 0 | 67 | 69 | 195913 | -1000000
7 | 23 | 20 | 7 | 6.5477 | 0 | 42.7453 | 0 | 6.4916 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4 | 74.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3221.14 | 0 | 3221.14 | 127534 | 0 | 67 | 68 | 127534 | -1000000
7 | 23 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.7034 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 7.2 | 77.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.71 | 0 | 3220.71 | 127495 | 0 | 67 | 68 | 127495 | -1000000
7 | 23 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0134 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 6.4 | 77.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.31 | 0 | 3220.31 | 127527 | 0 | 68 | 69 | 127527 | -1000000
7 | 23 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.7396 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 5.6 | 76.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3219.93 | 0 | 3219.93 | 127437 | 0 | 68 | 69 | 127437 | -1000000
7 | 23 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 10.0583 | 0 | 5.5212 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.3875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8372.87 | 0 | 8372.87 | 190778 | 0 | 68 | 70 | 190778 | -1000000
7 | 24 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.8368 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8372.44 | 0 | 8372.44 | 127580 | 0 | 68 | 70 | 127580 | -1000000
7 | 24 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.785 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8371.19 | 0 | 8371.19 | 127559 | 0 | 68 | 70 | 127559 | -1000000
7 | 24 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.783 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.45 | 0 | 8370.45 | 127517 | 0 | 68 | 70 | 127517 | -1000000
7 | 24 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.8044 | 0 | 5.5126 | 12.8287 | 0 | 0 | 0 | 3.2 | 87.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9282.45 | 0 | 9282.45 | 198063 | 0 | 68 | 69 | 198063 | -1000000
7 | 24 | 5 | 1 | 24.2727 | 0 | 69.9783 | 0 | 13.8943 | 0 | 5.7037 | 12.8287 | 0 | 0 | 0 | 1.6 | 128.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11313.6 | 0 | 11313.6 | 277838 | 0 | 68 | 69 | 277838 | -1000000
7 | 24 | 6 | 1 | 43.7813 | 0 | 140.608 | 0 | 81.5854 | 0 | 6.332 | 22.9645 | 0 | 0 | 0 | 0 | 295.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30454 | 0 | 30454 | 1427350 | -7852.05 | 68 | 68 | 1427350 | -1007852.05
7 | 24 | 7 | 1 | 39.7882 | 0 | 168.222 | 0 | 82.5943 | 0 | 6.332 | 22.926 | 0 | 0 | 0 | 0 | 319.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33394.5 | 0 | 33394.5 | 1420890 | -26075.9 | 68 | 69 | 1420890 | -1026075.9
7 | 24 | 8 | 1 | 39.9157 | 0 | 173.795 | 0 | 73.0028 | 0 | 6.332 | 23.113 | 0 | 0 | 0 | 0 | 316.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42254.5 | 0 | 42254.5 | 1324460 | -19150.5 | 68 | 69 | 1324460 | -1019150.5
7 | 24 | 9 | 1 | 41.1465 | 0 | 172.186 | 0 | 75.412 | 0 | 6.332 | 23.7114 | 0 | 0 | 0 | 0 | 318.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65817.2 | 0 | 65817.2 | 1363010 | -17737.6 | 69 | 70 | 1363010 | -1017737.6
7 | 24 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 78.9573 | 0 | 6.332 | 22.9651 | 0 | 0 | 0 | 0 | 312.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67290.8 | 0 | 67290.8 | 1437300 | -15790.9 | 70 | 72 | 1437300 | -1015790.9
7 | 24 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 73.7957 | 0 | 7.0185 | 23.5334 | 0 | 0 | 0 | 0 | 294.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67291.4 | 0 | 67291.4 | 1352720 | -12204.9 | 71 | 74 | 1352720 | -1012204.9
7 | 24 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 80.7685 | 0 | 25.335 | 23.2145 | 0 | 0 | 0 | 0 | 319.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67294.1 | 0 | 67294.1 | 1452710 | -19279 | 72 | 76 | 1452710 | -1019279
7 | 24 | 13 | 1 | 41.233 | 0 | 165.698 | 0 | 83.4795 | 0 | 25.335 | 24.0614 | 0 | 0 | 0 | 0 | 339.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67295.1 | 0 | 67295.1 | 1523070 | -13709.3 | 71 | 78 | 1523070 | -1013709.3
7 | 24 | 14 | 1 | 40.6249 | 0 | 172.702 | 0 | 85.7986 | 0 | 25.335 | 23.6122 | 0 | 0 | 0 | 0 | 348.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65823 | 0 | 65823 | 1512210 | -17223.6 | 70 | 79 | 1512210 | -1017223.6
7 | 24 | 15 | 1 | 40.5182 | 0 | 173.986 | 0 | 87.7237 | 0 | 25.335 | 23.7679 | 0 | 0 | 0 | 0 | 351.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59933.9 | 0 | 59933.9 | 1528430 | -18640.1 | 69 | 81 | 1528430 | -1018640.1
7 | 24 | 16 | 1 | 40.2738 | 0 | 169.782 | 0 | 89.8873 | 0 | 25.335 | 23.4866 | 0 | 0 | 0 | 0 | 348.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49626.9 | 0 | 49626.9 | 1580550 | -24902.6 | 70 | 81 | 1580550 | -1024902.6
7 | 24 | 17 | 1 | 35.4687 | 0 | 152.497 | 0 | 88.5616 | 0 | 25.335 | 23.3201 | 0 | 0 | 0 | 0 | 325.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37847.6 | 0 | 37847.6 | 1564410 | -24268.1 | 72 | 81 | 1564410 | -1024268.1
7 | 24 | 18 | 1 | 24.593 | 0 | 93.4203 | 0 | 65.3604 | 0 | 25.335 | 21.9716 | 0 | 0 | 0 | 0 | 230.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23123.4 | 0 | 23123.4 | 1176760 | -21455.8 | 73 | 81 | 1176760 | -1021455.8
7 | 24 | 19 | 1 | 18.2086 | 0 | 62.7906 | 0 | 10.9465 | 0 | 5.5635 | 8.818 | 0 | 0 | 0 | 1.2 | 107.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16497.7 | 0 | 16497.7 | 190575 | 0 | 72 | 78 | 190575 | -1000000
7 | 24 | 20 | 1 | 18.3078 | 0 | 54.6418 | 0 | 9.1252 | 0 | 5.5035 | 8.818 | 0 | 0 | 0 | 4 | 100.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15762.1 | 0 | 15762.1 | 170066 | 0 | 71 | 76 | 170066 | -1000000
7 | 24 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.813 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858 | 0 | 9858 | 156983 | 0 | 70 | 73 | 156983 | -1000000
7 | 24 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.5082 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9618.97 | 0 | 9618.97 | 146129 | 0 | 69 | 72 | 146129 | -1000000
7 | 24 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.9021 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 5.6 | 79.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.26 | 0 | 8379.26 | 141129 | 0 | 67 | 70 | 141129 | -1000000
7 | 24 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.0577 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8378.28 | 0 | 8378.28 | 139653 | 0 | 66 | 69 | 139653 | -1000000
7 | 25 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.981 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8377.53 | 0 | 8377.53 | 138912 | 0 | 66 | 68 | 138912 | -1000000
7 | 25 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.2106 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376.95 | 0 | 8376.95 | 138105 | 0 | 65 | 68 | 138105 | -1000000
7 | 25 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.868 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376.46 | 0 | 8376.46 | 137372 | 0 | 64 | 67 | 137372 | -1000000
7 | 25 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 9.6705 | 0 | 5.5054 | 12.8287 | 0 | 0 | 0 | 3.2 | 87.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9288.89 | 0 | 9288.89 | 198608 | 0 | 64 | 66 | 198608 | -1000000
7 | 25 | 5 | 2 | 24.2601 | 0 | 69.9783 | 0 | 13.5129 | 0 | 5.665 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11320.4 | 0 | 11320.4 | 274705 | 0 | 64 | 66 | 274705 | -1000000
7 | 25 | 6 | 2 | 40.5448 | 0 | 140.608 | 0 | 57.2036 | 0 | 6.332 | 22.6939 | 0 | 0 | 0 | 0 | 267.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30461.1 | 0 | 30461.1 | 1118700 | -6672.64 | 63 | 65 | 1118700 | -1006672.64
7 | 25 | 7 | 2 | 39.1608 | 0 | 168.222 | 0 | 67.1266 | 0 | 25.335 | 22.1502 | 0 | 0 | 0 | 0 | 321.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33402 | 0 | 33402 | 1194860 | -22866.4 | 63 | 67 | 1194860 | -1022866.4
7 | 25 | 8 | 2 | 39.8317 | 0 | 173.795 | 0 | 68.1979 | 0 | 25.335 | 21.4581 | 0 | 0 | 0 | 0 | 328.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42259 | 0 | 42259 | 1203300 | -22431 | 64 | 69 | 1203300 | -1022431
7 | 25 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 70.4209 | 0 | 25.335 | 21.7122 | 0 | 0 | 0 | 0 | 330.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65823.1 | 0 | 65823.1 | 1219190 | -22506.3 | 64 | 71 | 1219190 | -1022506.3
7 | 25 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 71.9586 | 0 | 25.335 | 22.0079 | 0 | 0 | 0 | 0 | 323.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298 | 0 | 67298 | 1225880 | -19392 | 64 | 73 | 1225880 | -1019392
7 | 25 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 67.2078 | 0 | 25.335 | 22.9141 | 0 | 0 | 0 | 0 | 305.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.2 | 0 | 67299.2 | 1125750 | -14860.5 | 64 | 76 | 1125750 | -1014860.5
7 | 25 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 70.8012 | 0 | 25.335 | 22.4619 | 0 | 0 | 0 | 0 | 308.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.7 | 0 | 67299.7 | 1189660 | -27517.2 | 64 | 78 | 1189660 | -1027517.2
7 | 25 | 13 | 2 | 41.2636 | 0 | 165.698 | 0 | 75.4291 | 0 | 25.335 | 23.4518 | 0 | 0 | 0 | 0 | 331.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.7 | 0 | 67299.7 | 1262650 | -15984.2 | 64 | 79 | 1262650 | -1015984.2
7 | 25 | 14 | 2 | 40.6757 | 0 | 172.702 | 0 | 80.0899 | 0 | 25.335 | 23.0557 | 0 | 0 | 0 | 0 | 341.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65827.3 | 0 | 65827.3 | 1331380 | -20101.3 | 65 | 79 | 1331380 | -1020101.3
7 | 25 | 15 | 2 | 40.5734 | 0 | 173.986 | 0 | 84.8009 | 0 | 25.335 | 23.2139 | 0 | 0 | 0 | 0 | 347.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59937.8 | 0 | 59937.8 | 1410450 | -21922.2 | 66 | 80 | 1410450 | -1021922.2
7 | 25 | 16 | 2 | 40.3069 | 0 | 169.782 | 0 | 86.7007 | 0 | 25.335 | 23.1658 | 0 | 0 | 0 | 0 | 345.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49630.5 | 0 | 49630.5 | 1454860 | -27294 | 67 | 80 | 1454860 | -1027294
7 | 25 | 17 | 2 | 35.483 | 0 | 152.497 | 0 | 84.1944 | 0 | 25.335 | 22.7205 | 0 | 0 | 0 | 0 | 320.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37850.8 | 0 | 37850.8 | 1421060 | -33337 | 68 | 80 | 1421060 | -1033337
7 | 25 | 18 | 2 | 24.5879 | 0 | 93.4203 | 0 | 65.2651 | 0 | 25.335 | 21.1835 | 0 | 0 | 0 | 0 | 229.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23126.3 | 0 | 23126.3 | 1059070 | -37459.6 | 68 | 80 | 1059070 | -1037459.6
7 | 25 | 19 | 2 | 18.776 | 0 | 62.7906 | 0 | 12.0567 | 0 | 12.6102 | 8.818 | 0 | 0 | 0 | 1.2 | 116.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16500.4 | 0 | 16500.4 | 194441 | 0 | 68 | 77 | 194441 | -1000000
7 | 25 | 20 | 2 | 17.9851 | 0 | 54.6418 | 0 | 9.8207 | 0 | 9.2657 | 8.818 | 0 | 0 | 0 | 4 | 104.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15764.9 | 0 | 15764.9 | 174078 | 0 | 68 | 74 | 174078 | -1000000
7 | 25 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.239 | 0 | 7.6276 | 8.818 | 0 | 0 | 0 | 7.2 | 94.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.43 | 0 | 9861.43 | 160788 | 0 | 67 | 71 | 160788 | -1000000
7 | 25 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 8.1497 | 0 | 7.5448 | 8.818 | 0 | 0 | 0 | 6.4 | 86.4431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9622.6 | 0 | 9622.6 | 149760 | 0 | 66 | 70 | 149760 | -1000000
7 | 25 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.5055 | 0 | 7.0168 | 8.818 | 0 | 0 | 0 | 5.6 | 81.7982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.98 | 0 | 8382.98 | 144722 | 0 | 65 | 68 | 144722 | -1000000
7 | 25 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.6624 | 0 | 7.093 | 8.818 | 0 | 0 | 0 | 4.8 | 81.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.97 | 0 | 8381.97 | 143078 | 0 | 64 | 67 | 143078 | -1000000
7 | 26 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.5788 | 0 | 7.01 | 8.818 | 0 | 0 | 0 | 4.8 | 81.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.06 | 0 | 8381.06 | 142288 | 0 | 64 | 66 | 142288 | -1000000
7 | 26 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.8156 | 0 | 7.1679 | 8.818 | 0 | 0 | 0 | 4.8 | 81.7809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.29 | 0 | 8380.29 | 141347 | 0 | 64 | 66 | 141347 | -1000000
7 | 26 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.4415 | 0 | 6.8972 | 8.818 | 0 | 0 | 0 | 4.8 | 81.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8379.53 | 0 | 8379.53 | 140395 | 0 | 63 | 65 | 140395 | -1000000
7 | 26 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 8.2212 | 0 | 7.4597 | 8.818 | 0 | 0 | 0 | 3.2 | 84.3434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9291.72 | 0 | 9291.72 | 143811 | 0 | 64 | 66 | 143811 | -1000000
7 | 26 | 5 | 3 | 24.2619 | 0 | 69.9783 | 0 | 14.9625 | 0 | 17.7587 | 12.8287 | 0 | 0 | 0 | 1.6 | 141.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11323.3 | 0 | 11323.3 | 277468 | 0 | 64 | 67 | 277468 | -1000000
7 | 26 | 6 | 3 | 39.8906 | 0 | 140.608 | 0 | 65.4694 | 0 | 25.335 | 22.9474 | 0 | 0 | 0 | 0 | 294.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30464.1 | 0 | 30464.1 | 1187530 | -5418.55 | 65 | 68 | 1187530 | -1005418.55
7 | 26 | 7 | 3 | 38.9463 | 0 | 168.222 | 0 | 71.7782 | 0 | 25.335 | 23.0275 | 0 | 0 | 0 | 0 | 327.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33404.9 | 0 | 33404.9 | 1260100 | -24794.2 | 65 | 69 | 1260100 | -1024794.2
7 | 26 | 8 | 3 | 39.6631 | 0 | 173.795 | 0 | 73.3162 | 0 | 25.335 | 22.4775 | 0 | 0 | 0 | 0 | 334.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42260.8 | 0 | 42260.8 | 1267740 | -24252 | 66 | 71 | 1267740 | -1024252
7 | 26 | 9 | 3 | 40.899 | 0 | 172.186 | 0 | 73.5575 | 0 | 25.335 | 23.0003 | 0 | 0 | 0 | 0 | 334.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65823.2 | 0 | 65823.2 | 1259900 | -24251 | 66 | 72 | 1259900 | -1024251
7 | 26 | 10 | 3 | 42.1359 | 0 | 163.102 | 0 | 75.5315 | 0 | 25.335 | 23.1728 | 0 | 0 | 0 | 0 | 329.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.6 | 0 | 67297.6 | 1281230 | -21038.5 | 67 | 73 | 1281230 | -1021038.5
7 | 26 | 11 | 3 | 41.0505 | 0 | 149.692 | 0 | 69.8522 | 0 | 25.335 | 23.1164 | 0 | 0 | 0 | 0 | 309.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.6 | 0 | 67297.6 | 1189930 | -17303.7 | 68 | 73 | 1189930 | -1017303.7
7 | 26 | 12 | 3 | 39.829 | 0 | 150.207 | 0 | 74.3643 | 0 | 25.335 | 23.3662 | 0 | 0 | 0 | 0 | 313.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67297.5 | 0 | 67297.5 | 1253090 | -16050.3 | 69 | 74 | 1253090 | -1016050.3
7 | 26 | 13 | 3 | 41.3034 | 0 | 165.698 | 0 | 85.6474 | 0 | 25.335 | 23.3862 | 0 | 0 | 0 | 0 | 341.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67298.2 | 0 | 67298.2 | 1423950 | -19382.9 | 70 | 76 | 1423950 | -1019382.9
7 | 26 | 14 | 3 | 40.7349 | 0 | 172.702 | 0 | 90.1202 | 0 | 25.335 | 23.2971 | 0 | 0 | 0 | 0 | 352.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65826.4 | 0 | 65826.4 | 1496680 | -22829.2 | 71 | 79 | 1496680 | -1022829.2
7 | 26 | 15 | 3 | 40.8055 | 0 | 173.986 | 0 | 94.7199 | 0 | 25.335 | 23.6558 | 0 | 0 | 0 | 0 | 358.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59937.4 | 0 | 59937.4 | 1573790 | -23870.1 | 72 | 81 | 1573790 | -1023870.1
7 | 26 | 16 | 3 | 40.9128 | 0 | 169.782 | 0 | 93.8719 | 0 | 25.335 | 23.8421 | 0 | 0 | 0 | 0 | 353.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49630.4 | 0 | 49630.4 | 1587040 | -22419.9 | 72 | 81 | 1587040 | -1022419.9
7 | 26 | 17 | 3 | 35.9986 | 0 | 152.497 | 0 | 89.8606 | 0 | 25.335 | 23.7222 | 0 | 0 | 0 | 0 | 327.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37850.7 | 0 | 37850.7 | 1539570 | -19455.1 | 73 | 81 | 1539570 | -1019455.1
7 | 26 | 18 | 3 | 25.1003 | 0 | 93.4203 | 0 | 63.9192 | 0 | 25.335 | 22.022 | 0 | 0 | 0 | 0 | 229.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23126.5 | 0 | 23126.5 | 1110330 | -16546.8 | 73 | 81 | 1110330 | -1016546.8
7 | 26 | 19 | 3 | 20.0385 | 0 | 62.7906 | 0 | 12.1945 | 0 | 12.8564 | 8.818 | 0 | 0 | 0 | 1.2 | 117.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16500.9 | 0 | 16500.9 | 196151 | 0 | 72 | 77 | 196151 | -1000000
7 | 26 | 20 | 3 | 18.3998 | 0 | 54.6418 | 0 | 9.8874 | 0 | 9.344 | 8.818 | 0 | 0 | 0 | 4 | 105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15765.3 | 0 | 15765.3 | 175304 | 0 | 71 | 74 | 175304 | -1000000
7 | 26 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.9755 | 0 | 7.3752 | 8.818 | 0 | 0 | 0 | 7.2 | 94.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.6 | 0 | 9861.6 | 161800 | 0 | 69 | 70 | 161800 | -1000000
7 | 26 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 8.9375 | 0 | 8.2184 | 8.818 | 0 | 0 | 0 | 6.4 | 87.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9622.81 | 0 | 9622.81 | 150911 | 0 | 70 | 71 | 150911 | -1000000
7 | 26 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 8.7208 | 0 | 8.0633 | 8.818 | 0 | 0 | 0 | 5.6 | 84.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8383.34 | 0 | 8383.34 | 145926 | 0 | 71 | 72 | 145926 | -1000000
7 | 26 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 8.6898 | 0 | 8.0795 | 8.818 | 0 | 0 | 0 | 4.8 | 83.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8382.58 | 0 | 8382.58 | 144429 | 0 | 72 | 73 | 144429 | -1000000
7 | 27 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.9867 | 0 | 7.4459 | 8.818 | 0 | 0 | 0 | 4.8 | 82.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.9 | 0 | 8381.9 | 143369 | 0 | 71 | 72 | 143369 | -1000000
7 | 27 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.2325 | 0 | 7.6413 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.2 | 0 | 8381.2 | 142394 | 0 | 70 | 72 | 142394 | -1000000
7 | 27 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.8467 | 0 | 7.3074 | 8.818 | 0 | 0 | 0 | 4.8 | 81.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.41 | 0 | 8380.41 | 141607 | 0 | 70 | 71 | 141607 | -1000000
7 | 27 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 8.3149 | 0 | 7.6709 | 8.818 | 0 | 0 | 0 | 3.2 | 84.6484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9292.56 | 0 | 9292.56 | 144947 | 0 | 69 | 71 | 144947 | -1000000
7 | 27 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.6164 | 0 | 19.8449 | 12.8287 | 0 | 0 | 0 | 1.6 | 144.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11323.8 | 0 | 11323.8 | 293372 | 0 | 69 | 70 | 293372 | -1000000
7 | 27 | 6 | 4 | 40.4986 | 0 | 140.608 | 0 | 76.6184 | 0 | 25.335 | 23.5817 | 0 | 0 | 0 | 0 | 306.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30464.2 | 0 | 30464.2 | 1372470 | -4169.85 | 69 | 70 | 1372470 | -1004169.85
7 | 27 | 7 | 4 | 39.0828 | 0 | 168.222 | 0 | 85.3929 | 0 | 25.335 | 22.6535 | 0 | 0 | 0 | 0 | 340.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33404.5 | 0 | 33404.5 | 1461280 | -25344.2 | 69 | 72 | 1461280 | -1025344.2
7 | 27 | 8 | 4 | 39.6631 | 0 | 173.795 | 0 | 85.324 | 0 | 25.335 | 21.9638 | 0 | 0 | 0 | 0 | 346.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42260.9 | 0 | 42260.9 | 1425110 | -24883.6 | 69 | 75 | 1425110 | -1024883.6
7 | 27 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 84.724 | 0 | 25.335 | 22.5155 | 0 | 0 | 0 | 0 | 345.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65824.5 | 0 | 65824.5 | 1430970 | -24563 | 69 | 77 | 1430970 | -1024563
7 | 27 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 85.3133 | 0 | 25.335 | 22.6966 | 0 | 0 | 0 | 0 | 337.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.4 | 0 | 67299.4 | 1438370 | -21056.6 | 69 | 78 | 1438370 | -1021056.6
7 | 27 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 74.0086 | 0 | 25.335 | 23.2528 | 0 | 0 | 0 | 0 | 312.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67299.9 | 0 | 67299.9 | 1246390 | -17042.5 | 67 | 78 | 1246390 | -1017042.5
7 | 27 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 75.3544 | 0 | 25.335 | 22.8323 | 0 | 0 | 0 | 0 | 313.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.5 | 0 | 67300.5 | 1275690 | -24784.1 | 66 | 79 | 1275690 | -1024784.1
7 | 27 | 13 | 4 | 41.2515 | 0 | 165.698 | 0 | 80.2926 | 0 | 25.335 | 23.4305 | 0 | 0 | 0 | 0 | 336.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67300.9 | 0 | 67300.9 | 1356600 | -19302.2 | 66 | 79 | 1356600 | -1019302.2
7 | 27 | 14 | 4 | 40.6412 | 0 | 172.702 | 0 | 82.4447 | 0 | 25.335 | 23.0761 | 0 | 0 | 0 | 0 | 344.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65828.6 | 0 | 65828.6 | 1382240 | -23812.3 | 66 | 78 | 1382240 | -1023812.3
7 | 27 | 15 | 4 | 40.5419 | 0 | 173.986 | 0 | 83.448 | 0 | 25.335 | 23.2019 | 0 | 0 | 0 | 0 | 346.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59939.1 | 0 | 59939.1 | 1404440 | -25467.8 | 66 | 78 | 1404440 | -1025467.8
7 | 27 | 16 | 4 | 40.2922 | 0 | 169.782 | 0 | 79.3898 | 0 | 25.335 | 23.3029 | 0 | 0 | 0 | 0 | 338.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49631.9 | 0 | 49631.9 | 1357800 | -24738.7 | 65 | 77 | 1357800 | -1024738.7
7 | 27 | 17 | 4 | 35.4704 | 0 | 152.497 | 0 | 70.4098 | 0 | 25.335 | 23.2545 | 0 | 0 | 0 | 0 | 306.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37852 | 0 | 37852 | 1211770 | -20951.1 | 64 | 76 | 1211770 | -1020951.1
7 | 27 | 18 | 4 | 24.5902 | 0 | 93.4203 | 0 | 48.7149 | 0 | 25.335 | 21.1873 | 0 | 0 | 0 | 0 | 213.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23127.5 | 0 | 23127.5 | 850312 | -23098.8 | 63 | 75 | 850312 | -1023098.8
7 | 27 | 19 | 4 | 18.5147 | 0 | 62.7906 | 0 | 10.4211 | 0 | 9.7966 | 8.818 | 0 | 0 | 0 | 1.2 | 111.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16501.5 | 0 | 16501.5 | 195214 | 0 | 62 | 71 | 195214 | -1000000
7 | 27 | 20 | 4 | 18.2154 | 0 | 54.6418 | 0 | 8.6348 | 0 | 7.9387 | 8.818 | 0 | 0 | 0 | 4 | 102.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15766.1 | 0 | 15766.1 | 174718 | 0 | 60 | 68 | 174718 | -1000000
7 | 27 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.0912 | 0 | 6.8588 | 8.818 | 0 | 0 | 0 | 7.2 | 92.6883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863 | 0 | 9863 | 161215 | 0 | 58 | 64 | 161215 | -1000000
7 | 27 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.0134 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9624.8 | 0 | 9624.8 | 150023 | 0 | 57 | 62 | 150023 | -1000000
7 | 27 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.9955 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.84 | 0 | 8385.84 | 144933 | 0 | 56 | 61 | 144933 | -1000000
7 | 27 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.8805 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.66 | 0 | 8385.66 | 143278 | 0 | 55 | 59 | 143278 | -1000000
7 | 28 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0925 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.72 | 0 | 8385.72 | 142314 | 0 | 55 | 58 | 142314 | -1000000
7 | 28 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0416 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8385.88 | 0 | 8385.88 | 141199 | 0 | 54 | 56 | 141199 | -1000000
7 | 28 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0037 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8386.1 | 0 | 8386.1 | 140375 | 0 | 54 | 55 | 140375 | -1000000
7 | 28 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.1357 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 3.2 | 81.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9299.25 | 0 | 9299.25 | 143325 | 0 | 55 | 56 | 143325 | -1000000
7 | 28 | 5 | 5 | 24.2734 | 0 | 69.9783 | 0 | 11.4478 | 0 | 5.5471 | 12.8287 | 0 | 0 | 0 | 1.6 | 125.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11331.5 | 0 | 11331.5 | 239290 | 0 | 55 | 56 | 239290 | -1000000
7 | 28 | 6 | 5 | 41.3279 | 0 | 140.608 | 0 | 35.8717 | 0 | 25.335 | 20.332 | 0 | 0 | 0 | 0 | 263.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30473.1 | 0 | 30473.1 | 691108 | -9682.63 | 56 | 57 | 691108 | -1009682.63
7 | 28 | 7 | 5 | 39.1353 | 0 | 168.222 | 0 | 45.1314 | 0 | 25.335 | 20.4736 | 0 | 0 | 0 | 0 | 298.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33414.5 | 0 | 33414.5 | 831375 | -30887 | 57 | 60 | 831375 | -1030887
7 | 28 | 8 | 5 | 39.7853 | 0 | 173.795 | 0 | 50.0541 | 0 | 25.335 | 20.4936 | 0 | 0 | 0 | 0 | 309.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42265 | 0 | 42265 | 906488 | -28112.7 | 58 | 64 | 906488 | -1028112.7
7 | 28 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 54.1286 | 0 | 25.335 | 20.8333 | 0 | 0 | 0 | 0 | 313.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65827.1 | 0 | 65827.1 | 964440 | -27361.8 | 59 | 67 | 964440 | -1027361.8
7 | 28 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 55.2905 | 0 | 25.335 | 21.0801 | 0 | 0 | 0 | 0 | 305.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67302 | 0 | 67302 | 976576 | -23204.8 | 59 | 69 | 976576 | -1023204.8
7 | 28 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 53.0006 | 0 | 25.335 | 22.0372 | 0 | 0 | 0 | 0 | 290.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67303.1 | 0 | 67303.1 | 908390 | -18137.2 | 59 | 72 | 908390 | -1018137.2
7 | 28 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 56.0379 | 0 | 25.335 | 22.3368 | 0 | 0 | 0 | 0 | 293.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67303.3 | 0 | 67303.3 | 949890 | -22019.4 | 59 | 74 | 949890 | -1022019.4
7 | 28 | 13 | 5 | 41.233 | 0 | 165.698 | 0 | 60.7564 | 0 | 25.335 | 22.8592 | 0 | 0 | 0 | 0 | 315.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67303.1 | 0 | 67303.1 | 1035910 | -19836.4 | 59 | 74 | 1035910 | -1019836.4
7 | 28 | 14 | 5 | 40.6518 | 0 | 172.702 | 0 | 66.5059 | 0 | 25.335 | 22.5757 | 0 | 0 | 0 | 0 | 327.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65830.4 | 0 | 65830.4 | 1114560 | -23293.8 | 60 | 75 | 1114560 | -1023293.8
7 | 28 | 15 | 5 | 40.5485 | 0 | 173.986 | 0 | 68.1591 | 0 | 25.335 | 22.7216 | 0 | 0 | 0 | 0 | 330.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59940.7 | 0 | 59940.7 | 1148010 | -24760.1 | 60 | 75 | 1148010 | -1024760.1
7 | 28 | 16 | 5 | 40.2913 | 0 | 169.782 | 0 | 66.3109 | 0 | 25.335 | 22.8968 | 0 | 0 | 0 | 0 | 324.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49633.4 | 0 | 49633.4 | 1135540 | -23820.3 | 60 | 75 | 1135540 | -1023820.3
7 | 28 | 17 | 5 | 35.4761 | 0 | 152.497 | 0 | 58.9012 | 0 | 25.335 | 22.8134 | 0 | 0 | 0 | 0 | 295.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37853.5 | 0 | 37853.5 | 1035040 | -20360.2 | 60 | 74 | 1035040 | -1020360.2
7 | 28 | 18 | 5 | 24.5905 | 0 | 93.4203 | 0 | 42.1093 | 0 | 25.335 | 20.6691 | 0 | 0 | 0 | 0 | 206.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23128.8 | 0 | 23128.8 | 739447 | -21386.6 | 60 | 74 | 739447 | -1021386.6
7 | 28 | 19 | 5 | 18.819 | 0 | 62.7906 | 0 | 9.8715 | 0 | 9.0323 | 8.818 | 0 | 0 | 0 | 1.2 | 110.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16502.7 | 0 | 16502.7 | 194758 | 0 | 60 | 69 | 194758 | -1000000
7 | 28 | 20 | 5 | 18.2538 | 0 | 54.6418 | 0 | 8.1356 | 0 | 7.4438 | 8.818 | 0 | 0 | 0 | 4 | 101.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15767.9 | 0 | 15767.9 | 174192 | 0 | 58 | 65 | 174192 | -1000000
7 | 28 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 6.6595 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 90.8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9865.32 | 0 | 9865.32 | 160698 | 0 | 56 | 60 | 160698 | -1000000
7 | 28 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.4329 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9627.52 | 0 | 9627.52 | 149596 | 0 | 56 | 58 | 149596 | -1000000
7 | 28 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1933 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.9 | 0 | 8388.9 | 144451 | 0 | 55 | 57 | 144451 | -1000000
7 | 28 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.1012 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8389.07 | 0 | 8389.07 | 142489 | 0 | 54 | 55 | 142489 | -1000000
7 | 29 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0479 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8389.39 | 0 | 8389.39 | 141335 | 0 | 53 | 53 | 141335 | -1000000
7 | 29 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9917 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8390.48 | 0 | 8390.48 | 140103 | 0 | 51 | 52 | 140103 | -1000000
7 | 29 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9529 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8391.34 | 0 | 8391.34 | 139262 | 0 | 50 | 50 | 139262 | -1000000
7 | 29 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9177 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 3.2 | 73.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8392.34 | 0 | 8392.34 | 138493 | 0 | 51 | 51 | 138493 | -1000000
7 | 29 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8808 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 1.6 | 71.9066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8393.33 | 0 | 8393.33 | 137684 | 0 | 52 | 53 | 137684 | -1000000
7 | 29 | 6 | 6 | 5.4045 | 0 | 42.7453 | 0 | 7.2945 | 0 | 6.7123 | 8.818 | 0 | 0 | 0 | 0 | 70.9747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.37 | 0 | 8394.37 | 136962 | 0 | 53 | 54 | 136962 | -1000000
7 | 29 | 7 | 6 | 4.6155 | 0 | 42.7453 | 0 | 18.2812 | 0 | 6.0682 | 18.8896 | 0 | 0 | 0 | 0 | 90.5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.39 | 0 | 8395.39 | 220450 | -26046.2 | 56 | 59 | 220450 | -1026046.2
7 | 29 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 14.3743 | 0 | 16.1872 | 18.8896 | 0 | 0 | 0 | 0 | 97.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.16 | 0 | 8396.16 | 260764 | -19306 | 59 | 63 | 260764 | -1019306
7 | 29 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 19.57 | 0 | 25.335 | 18.8896 | 0 | 0 | 0 | 0 | 112.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8406.73 | 0 | 8406.73 | 328570 | -19174.5 | 61 | 68 | 328570 | -1019174.5
7 | 29 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 21.3302 | 0 | 25.335 | 18.8896 | 0 | 0 | 0 | 0 | 113.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8408.05 | 0 | 8408.05 | 371811 | -16812.5 | 62 | 70 | 371811 | -1016812.5
7 | 29 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 25.1374 | 0 | 25.335 | 18.9998 | 0 | 0 | 0 | 0 | 117.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8409.23 | 0 | 8409.23 | 422601 | -16424.6 | 63 | 73 | 422601 | -1016424.6
7 | 29 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 26.996 | 0 | 25.335 | 19.1841 | 0 | 0 | 0 | 0 | 119.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8409.85 | 0 | 8409.85 | 451918 | -16842.1 | 63 | 75 | 451918 | -1016842.1
7 | 29 | 13 | 6 | 5.4689 | 0 | 42.7453 | 0 | 28.2577 | 0 | 25.335 | 19.2791 | 0 | 0 | 0 | 0 | 121.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8410.21 | 0 | 8410.21 | 483497 | -16527.8 | 64 | 75 | 483497 | -1016527.8
7 | 29 | 14 | 6 | 5.47 | 0 | 42.7453 | 0 | 11.9486 | 0 | 11.9653 | 12.8287 | 0 | 0 | 0 | 0 | 84.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8410.6 | 0 | 8410.6 | 193898 | 0 | 65 | 76 | 193898 | -1000000
7 | 29 | 15 | 6 | 5.6986 | 0 | 42.7453 | 0 | 8.3218 | 0 | 7.6311 | 8.818 | 0 | 0 | 0 | 0 | 73.2149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8411 | 0 | 8411 | 133020 | 0 | 66 | 76 | 133020 | -1000000
7 | 29 | 16 | 6 | 5.554 | 0 | 42.7453 | 0 | 8.1753 | 0 | 7.5494 | 8.818 | 0 | 0 | 0 | 0 | 72.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8404.96 | 0 | 8404.96 | 132750 | 0 | 66 | 76 | 132750 | -1000000
7 | 29 | 17 | 6 | 6.3001 | 0 | 42.7453 | 0 | 8.0304 | 0 | 7.4987 | 8.818 | 0 | 0 | 0 | 0 | 73.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8401.55 | 0 | 8401.55 | 132563 | 0 | 66 | 75 | 132563 | -1000000
7 | 29 | 18 | 6 | 7.3068 | 0 | 42.7453 | 0 | 7.9857 | 0 | 7.4809 | 8.818 | 0 | 0 | 0 | 0 | 74.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8399.41 | 0 | 8399.41 | 132412 | 0 | 67 | 75 | 132412 | -1000000
7 | 29 | 19 | 6 | 7.9949 | 0 | 42.7453 | 0 | 7.4977 | 0 | 7.1338 | 8.818 | 0 | 0 | 0 | 1.2 | 75.3897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8397.3 | 0 | 8397.3 | 131843 | 0 | 66 | 74 | 131843 | -1000000
7 | 29 | 20 | 6 | 8.7042 | 0 | 42.7453 | 0 | 7.1509 | 0 | 6.9909 | 8.818 | 0 | 0 | 0 | 4 | 78.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396.07 | 0 | 8396.07 | 131597 | 0 | 65 | 73 | 131597 | -1000000
7 | 29 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.786 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 79.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8395.01 | 0 | 8395.01 | 131535 | 0 | 65 | 72 | 131535 | -1000000
7 | 29 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.7225 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 78.9625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.17 | 0 | 8394.17 | 131052 | 0 | 64 | 71 | 131052 | -1000000
7 | 29 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.9871 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 5.6 | 78.4264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8393.46 | 0 | 8393.46 | 130888 | 0 | 64 | 71 | 130888 | -1000000
7 | 29 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.9629 | 0 | 6.7982 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.52 | 0 | 3239.52 | 130576 | 0 | 64 | 70 | 130576 | -1000000
7 | 30 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.2321 | 0 | 6.9702 | 8.818 | 0 | 0 | 0 | 4.8 | 75.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.98 | 0 | 3238.98 | 130293 | 0 | 64 | 70 | 130293 | -1000000
7 | 30 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8975 | 0 | 6.7354 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.65 | 0 | 3238.65 | 130078 | 0 | 64 | 69 | 130078 | -1000000
7 | 30 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.1552 | 0 | 6.8944 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3238.29 | 0 | 3238.29 | 129592 | 0 | 63 | 69 | 129592 | -1000000
7 | 30 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.1486 | 0 | 6.8902 | 8.818 | 0 | 0 | 0 | 3.2 | 73.9075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.99 | 0 | 3237.99 | 129466 | 0 | 63 | 69 | 129466 | -1000000
7 | 30 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.817 | 0 | 6.6662 | 8.818 | 0 | 0 | 0 | 1.6 | 71.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.71 | 0 | 3237.71 | 129259 | 0 | 63 | 68 | 129259 | -1000000
7 | 30 | 6 | 7 | 4.5659 | 0 | 42.7453 | 0 | 7.3308 | 0 | 6.879 | 8.818 | 0 | 0 | 0 | 0 | 70.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.49 | 0 | 3237.49 | 128857 | 0 | 62 | 68 | 128857 | -1000000
7 | 30 | 7 | 7 | 3.6927 | 0 | 42.7453 | 0 | 7.3897 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.25 | 0 | 3237.25 | 128849 | 0 | 63 | 70 | 128849 | -1000000
7 | 30 | 8 | 7 | 3.7847 | 0 | 42.7453 | 0 | 7.7926 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 0 | 68.6221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3237.06 | 0 | 3237.06 | 128711 | 0 | 64 | 73 | 128711 | -1000000
7 | 30 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.5214 | 0 | 5.5463 | 12.8287 | 0 | 0 | 0 | 0 | 75.7857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3236.47 | 0 | 3236.47 | 188228 | 0 | 65 | 75 | 188228 | -1000000
7 | 30 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.3459 | 0 | 10.7906 | 12.8287 | 0 | 0 | 0 | 0 | 80.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3234.92 | 0 | 3234.92 | 194741 | 0 | 66 | 77 | 194741 | -1000000
7 | 30 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.2758 | 0 | 11.7225 | 12.8287 | 0 | 0 | 0 | 0 | 82.7162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3233.08 | 0 | 3233.08 | 202305 | 0 | 67 | 78 | 202305 | -1000000
7 | 30 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 12.1928 | 0 | 12.7314 | 12.8287 | 0 | 0 | 0 | 0 | 84.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3230.87 | 0 | 3230.87 | 209450 | 0 | 68 | 80 | 209450 | -1000000
7 | 30 | 13 | 7 | 4.1444 | 0 | 42.7453 | 0 | 12.4586 | 0 | 13.1713 | 12.8287 | 0 | 0 | 0 | 0 | 85.3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3228.66 | 0 | 3228.66 | 213562 | 0 | 69 | 81 | 213562 | -1000000
7 | 30 | 14 | 7 | 4.1463 | 0 | 42.7453 | 0 | 12.6909 | 0 | 13.5849 | 12.8287 | 0 | 0 | 0 | 0 | 85.9962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3226.61 | 0 | 3226.61 | 217434 | 0 | 70 | 81 | 217434 | -1000000
7 | 30 | 15 | 7 | 4.1476 | 0 | 42.7453 | 0 | 16.0892 | 0 | 21.8976 | 14.8767 | 0 | 0 | 0 | 0 | 99.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224.73 | 0 | 3224.73 | 280131 | 0 | 71 | 82 | 280131 | -1000000
7 | 30 | 16 | 7 | 4.1474 | 0 | 42.7453 | 0 | 15.6244 | 0 | 20.6511 | 14.8767 | 0 | 0 | 0 | 0 | 98.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3222.78 | 0 | 3222.78 | 271792 | 0 | 70 | 81 | 271792 | -1000000
7 | 30 | 17 | 7 | 4.1482 | 0 | 42.7453 | 0 | 12.549 | 0 | 13.4692 | 12.8287 | 0 | 0 | 0 | 0 | 85.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3220.97 | 0 | 3220.97 | 216291 | 0 | 71 | 80 | 216291 | -1000000
7 | 30 | 18 | 7 | 4.7733 | 0 | 42.7453 | 0 | 7.7037 | 0 | 7.3252 | 8.818 | 0 | 0 | 0 | 0 | 71.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3219.26 | 0 | 3219.26 | 128167 | 0 | 70 | 79 | 128167 | -1000000
7 | 30 | 19 | 7 | 5.5469 | 0 | 42.7453 | 0 | 7.2884 | 0 | 7.1742 | 8.818 | 0 | 0 | 0 | 1.2 | 72.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3217.73 | 0 | 3217.73 | 128242 | 0 | 70 | 78 | 128242 | -1000000
7 | 30 | 20 | 7 | 6.618 | 0 | 42.7453 | 0 | 7.0265 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4 | 74.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.37 | 0 | 3216.37 | 128243 | 0 | 70 | 78 | 128243 | -1000000
7 | 30 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0202 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 77.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.21 | 0 | 3215.21 | 128115 | 0 | 69 | 77 | 128115 | -1000000
7 | 30 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0188 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 77.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.25 | 0 | 3214.25 | 128089 | 0 | 69 | 76 | 128089 | -1000000
7 | 30 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 7.0159 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 76.3211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3213.38 | 0 | 3213.38 | 128030 | 0 | 69 | 76 | 128030 | -1000000
7 | 30 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 7.0291 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8365.86 | 0 | 8365.86 | 128300 | 0 | 69 | 75 | 128300 | -1000000
7 | 31 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.0627 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8365.08 | 0 | 8365.08 | 127963 | 0 | 66 | 72 | 127963 | -1000000
7 | 31 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 5.6349 | 0 | 5.4915 | 8.818 | 0 | 0 | 0 | 4.8 | 77.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8363.52 | 0 | 8363.52 | 127567 | 0 | 63 | 68 | 127567 | -1000000
7 | 31 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 5.7955 | 0 | 5.4904 | 8.818 | 0 | 0 | 0 | 4.8 | 78.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8362.46 | 0 | 8362.46 | 127404 | 0 | 60 | 65 | 127404 | -1000000
7 | 31 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.3285 | 0 | 5.4972 | 12.8287 | 0 | 0 | 0 | 3.2 | 87.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9274.49 | 0 | 9274.49 | 186825 | 0 | 60 | 65 | 186825 | -1000000
7 | 31 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.8567 | 0 | 5.6238 | 12.8287 | 0 | 0 | 0 | 1.6 | 127.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11305.9 | 0 | 11305.9 | 262308 | 0 | 61 | 65 | 262308 | -1000000
7 | 31 | 6 | 1 | 42.9045 | 0 | 140.608 | 0 | 62.2183 | 0 | 6.332 | 22.8186 | 0 | 0 | 0 | 0 | 274.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30446.7 | 0 | 30446.7 | 1183500 | -7043.51 | 61 | 65 | 1183500 | -1007043.51
7 | 31 | 7 | 1 | 38.9714 | 0 | 168.222 | 0 | 66.0143 | 0 | 6.332 | 22.62 | 0 | 0 | 0 | 0 | 302.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33387.7 | 0 | 33387.7 | 1185430 | -31259 | 61 | 67 | 1185430 | -1031259
7 | 31 | 8 | 1 | 39.6631 | 0 | 173.795 | 0 | 61.513 | 0 | 6.332 | 22.4975 | 0 | 0 | 0 | 0 | 303.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42252.4 | 0 | 42252.4 | 1152940 | -21899.9 | 62 | 68 | 1152940 | -1021899.9
7 | 31 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 62.5229 | 0 | 6.332 | 22.7199 | 0 | 0 | 0 | 0 | 304.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65815.1 | 0 | 65815.1 | 1160090 | -17531.4 | 62 | 70 | 1160090 | -1017531.4
7 | 31 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 59.8448 | 0 | 8.8936 | 22.8 | 0 | 0 | 0 | 0 | 295.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67290.1 | 0 | 67290.1 | 1153090 | -15848.4 | 62 | 70 | 1153090 | -1015848.4
7 | 31 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 52.6158 | 0 | 25.335 | 23.1891 | 0 | 0 | 0 | 0 | 291.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67292.1 | 0 | 67292.1 | 1032410 | -12862.8 | 62 | 69 | 1032410 | -1012862.8
7 | 31 | 12 | 1 | 39.8074 | 0 | 150.207 | 0 | 53.2822 | 0 | 25.335 | 23.3303 | 0 | 0 | 0 | 0 | 291.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67293 | 0 | 67293 | 996116 | -12447.5 | 61 | 69 | 996116 | -1012447.5
7 | 31 | 13 | 1 | 41.7384 | 0 | 165.698 | 0 | 58.514 | 0 | 25.335 | 23.2595 | 0 | 0 | 0 | 0 | 314.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67293.3 | 0 | 67293.3 | 1063850 | -16095.9 | 61 | 69 | 1063850 | -1016095.9
7 | 31 | 14 | 1 | 40.945 | 0 | 172.702 | 0 | 59.0678 | 0 | 25.335 | 23.5237 | 0 | 0 | 0 | 0 | 321.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65821.1 | 0 | 65821.1 | 1081600 | -19373.3 | 61 | 68 | 1081600 | -1019373.3
7 | 31 | 15 | 1 | 40.856 | 0 | 173.986 | 0 | 58.7643 | 0 | 25.335 | 23.6542 | 0 | 0 | 0 | 0 | 322.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59931.1 | 0 | 59931.1 | 1073380 | -20833.3 | 60 | 68 | 1073380 | -1020833.3
7 | 31 | 16 | 1 | 40.2857 | 0 | 169.782 | 0 | 57.7757 | 0 | 25.335 | 23.2144 | 0 | 0 | 0 | 0 | 316.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49624 | 0 | 49624 | 1069380 | -20711.3 | 60 | 67 | 1069380 | -1020711.3
7 | 31 | 17 | 1 | 36.0036 | 0 | 152.497 | 0 | 51.07 | 0 | 25.335 | 23.1378 | 0 | 0 | 0 | 0 | 288.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37844.6 | 0 | 37844.6 | 951186 | -17501.9 | 60 | 67 | 951186 | -1017501.9
7 | 31 | 18 | 1 | 24.9184 | 0 | 93.4203 | 0 | 31.6269 | 0 | 25.335 | 20.4557 | 0 | 0 | 0 | 0 | 195.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23120.6 | 0 | 23120.6 | 619543 | -14181 | 59 | 66 | 619543 | -1014181
7 | 31 | 19 | 1 | 20.8875 | 0 | 62.7906 | 0 | 9.2826 | 0 | 8.621 | 8.818 | 0 | 0 | 0 | 1.2 | 111.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16494.8 | 0 | 16494.8 | 188139 | 0 | 59 | 64 | 188139 | -1000000
7 | 31 | 20 | 1 | 18.4719 | 0 | 54.6418 | 0 | 7.8694 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4 | 99.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15760.8 | 0 | 15760.8 | 168420 | 0 | 59 | 62 | 168420 | -1000000
7 | 31 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.1784 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 91.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.74 | 0 | 9857.74 | 155219 | 0 | 59 | 60 | 155219 | -1000000
7 | 31 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.1879 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9620.28 | 0 | 9620.28 | 144237 | 0 | 59 | 60 | 144237 | -1000000
7 | 31 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.9654 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.62 | 0 | 8381.62 | 139471 | 0 | 59 | 59 | 139471 | -1000000
7 | 31 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.8957 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8381.67 | 0 | 8381.67 | 137999 | 0 | 59 | 60 | 137999 | -1000000
8 | 1 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.175 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.03 | 0 | 7929.03 | 137693 | 0 | 61 | 61 | 137693 | -1000000
8 | 1 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.1838 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.26 | 0 | 7929.26 | 137045 | 0 | 62 | 62 | 137045 | -1000000
8 | 1 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8884 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.39 | 0 | 7929.39 | 136261 | 0 | 62 | 62 | 136261 | -1000000
8 | 1 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 7.3331 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 83.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8786.21 | 0 | 8786.21 | 139486 | 0 | 62 | 63 | 139486 | -1000000
8 | 1 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.0848 | 0 | 5.58 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10693.2 | 0 | 10693.2 | 249271 | 0 | 63 | 63 | 249271 | -1000000
8 | 1 | 6 | 2 | 47.8464 | 0 | 140.608 | 0 | 52.067 | 0 | 6.332 | 21.5356 | 0 | 0 | 0 | 2.4 | 270.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28657.2 | 0 | 28657.2 | 964161 | -8333 | 64 | 64 | 964161 | -1008333
8 | 1 | 7 | 2 | 39.1432 | 0 | 168.222 | 0 | 64.3879 | 0 | 6.332 | 21.9968 | 0 | 0 | 0 | 0.8 | 300.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31417.1 | 0 | 31417.1 | 1130150 | -21423.1 | 66 | 66 | 1130150 | -1021423.1
8 | 1 | 8 | 2 | 39.7986 | 0 | 173.795 | 0 | 74.1649 | 0 | 25.335 | 21.1883 | 0 | 0 | 0 | 0 | 334.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39725.8 | 0 | 39725.8 | 1281730 | -20492.8 | 69 | 70 | 1281730 | -1020492.8
8 | 1 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 84.0547 | 0 | 25.335 | 21.6749 | 0 | 0 | 0 | 0 | 343.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61838.1 | 0 | 61838.1 | 1383970 | -19120.8 | 70 | 77 | 1383970 | -1019120.8
8 | 1 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 88.3834 | 0 | 25.335 | 22.1092 | 0 | 0 | 0 | 0 | 340.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.1 | 0 | 63224.1 | 1507210 | -15580.4 | 72 | 80 | 1507210 | -1015580.4
8 | 1 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 81.5775 | 0 | 25.335 | 22.7203 | 0 | 0 | 0 | 0 | 320.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.6 | 0 | 63225.6 | 1388280 | -12542.9 | 72 | 83 | 1388280 | -1012542.9
8 | 1 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 84.7801 | 0 | 25.335 | 22.5855 | 0 | 0 | 0 | 0 | 322.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.4 | 0 | 63226.4 | 1436810 | -22418.1 | 71 | 86 | 1436810 | -1022418.1
8 | 1 | 13 | 2 | 41.2473 | 0 | 165.698 | 0 | 94.6165 | 0 | 25.335 | 23.8978 | 0 | 0 | 0 | 0 | 350.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.4 | 0 | 63226.4 | 1596740 | -13611.4 | 72 | 89 | 1596740 | -1013611.4
8 | 1 | 14 | 2 | 40.6668 | 0 | 172.702 | 0 | 98.1867 | 0 | 25.335 | 23.1103 | 0 | 0 | 0 | 0 | 360.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61844.3 | 0 | 61844.3 | 1654370 | -24397.2 | 72 | 90 | 1654370 | -1024397.2
8 | 1 | 15 | 2 | 40.5604 | 0 | 173.986 | 0 | 110.56 | 0 | 25.335 | 22.9444 | 0 | 0 | 0 | 0 | 373.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56317.1 | 0 | 56317.1 | 1763190 | -33597.5 | 73 | 89 | 1763190 | -1033597.5
8 | 1 | 16 | 2 | 40.3045 | 0 | 169.782 | 0 | 107.857 | 0 | 25.335 | 23.1534 | 0 | 0 | 0 | 1.2 | 367.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.8 | 0 | 46643.8 | 1717790 | -33853.1 | 72 | 87 | 1717790 | -1033853.1
8 | 1 | 17 | 2 | 35.4825 | 0 | 152.497 | 0 | 115.887 | 0 | 7.1758 | 22.7801 | 0 | 0 | 0 | 4.8 | 338.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588.6 | 0 | 35588.6 | 1738120 | -38182.7 | 74 | 88 | 1738120 | -1038182.7
8 | 1 | 18 | 2 | 24.5902 | 0 | 93.4203 | 0 | 83.328 | 0 | 6.4995 | 21.4265 | 0 | 0 | 0 | 7.2 | 236.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.5 | 0 | 21769.5 | 1259460 | -38747.5 | 73 | 86 | 1259460 | -1038747.5
8 | 1 | 19 | 2 | 18.6459 | 0 | 62.7906 | 0 | 11.7042 | 0 | 12.6012 | 8.818 | 0 | 0 | 0 | 7.2 | 121.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15551.2 | 0 | 15551.2 | 195006 | 0 | 72 | 83 | 195006 | -1000000
8 | 1 | 20 | 2 | 18.3208 | 0 | 54.6418 | 0 | 9.3424 | 0 | 5.5088 | 8.818 | 0 | 0 | 0 | 7.2 | 103.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14860.6 | 0 | 14860.6 | 174431 | 0 | 72 | 78 | 174431 | -1000000
8 | 1 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.676 | 0 | 5.4942 | 8.818 | 0 | 0 | 0 | 7.2 | 92.9084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9318.39 | 0 | 9318.39 | 161161 | 0 | 71 | 77 | 161161 | -1000000
8 | 1 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.4775 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.37 | 0 | 9093.37 | 150195 | 0 | 70 | 73 | 150195 | -1000000
8 | 1 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1353 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.54 | 0 | 7929.54 | 145085 | 0 | 69 | 71 | 145085 | -1000000
8 | 1 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.2874 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.3 | 0 | 7928.3 | 143549 | 0 | 69 | 70 | 143549 | -1000000
8 | 2 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.831 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 80.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.4 | 0 | 7927.4 | 142628 | 0 | 69 | 71 | 142628 | -1000000
8 | 2 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8858 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.67 | 0 | 7926.67 | 141695 | 0 | 68 | 69 | 141695 | -1000000
8 | 2 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0708 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.04 | 0 | 7926.04 | 140790 | 0 | 67 | 68 | 140790 | -1000000
8 | 2 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.1782 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 82.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8782.18 | 0 | 8782.18 | 143970 | 0 | 66 | 67 | 143970 | -1000000
8 | 2 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.2295 | 0 | 5.7213 | 12.8287 | 0 | 0 | 0 | 4.8 | 131.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10688.6 | 0 | 10688.6 | 281899 | 0 | 65 | 68 | 281899 | -1000000
8 | 2 | 6 | 3 | 42.1433 | 0 | 140.608 | 0 | 63.0321 | 0 | 6.6985 | 23.4051 | 0 | 0 | 0 | 2.4 | 278.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28652.2 | 0 | 28652.2 | 1272390 | -4935.78 | 66 | 69 | 1272390 | -1004935.78
8 | 2 | 7 | 3 | 39.1049 | 0 | 168.222 | 0 | 81.3776 | 0 | 25.335 | 22.5973 | 0 | 0 | 0 | 0.8 | 337.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31411.7 | 0 | 31411.7 | 1385920 | -24532.3 | 67 | 73 | 1385920 | -1024532.3
8 | 2 | 8 | 3 | 39.7464 | 0 | 173.795 | 0 | 82.8097 | 0 | 25.335 | 21.8592 | 0 | 0 | 0 | 0 | 343.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39725.4 | 0 | 39725.4 | 1392930 | -23834.6 | 68 | 76 | 1392930 | -1023834.6
8 | 2 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 86.8881 | 0 | 25.335 | 22.266 | 0 | 0 | 0 | 0 | 347.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61840.4 | 0 | 61840.4 | 1458200 | -23228.6 | 69 | 79 | 1458200 | -1023228.6
8 | 2 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 93.2996 | 0 | 25.335 | 22.8407 | 0 | 0 | 0 | 0 | 345.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.9 | 0 | 63224.9 | 1556300 | -19438.7 | 71 | 81 | 1556300 | -1019438.7
8 | 2 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 87.997 | 0 | 25.335 | 23.2409 | 0 | 0 | 0 | 0 | 326.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.1 | 0 | 63226.1 | 1460280 | -14945 | 72 | 83 | 1460280 | -1014945
8 | 2 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 92.5579 | 0 | 25.335 | 22.5062 | 0 | 0 | 0 | 0 | 330.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.7 | 0 | 63226.7 | 1514850 | -31111.3 | 71 | 84 | 1514850 | -1031111.3
8 | 2 | 13 | 3 | 41.2615 | 0 | 165.698 | 0 | 101.522 | 0 | 25.335 | 23.094 | 0 | 0 | 0 | 0 | 356.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.7 | 0 | 63226.7 | 1667120 | -27923.2 | 72 | 87 | 1667120 | -1027923.2
8 | 2 | 14 | 3 | 40.6451 | 0 | 172.702 | 0 | 105.607 | 0 | 25.335 | 22.9149 | 0 | 0 | 0 | 0 | 367.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61844.9 | 0 | 61844.9 | 1698640 | -32172.2 | 72 | 89 | 1698640 | -1032172.2
8 | 2 | 15 | 3 | 40.5437 | 0 | 173.986 | 0 | 112.338 | 0 | 25.335 | 23.1483 | 0 | 0 | 0 | 0 | 375.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56317.7 | 0 | 56317.7 | 1754570 | -34379.4 | 72 | 90 | 1754570 | -1034379.4
8 | 2 | 16 | 3 | 40.2927 | 0 | 169.782 | 0 | 112.358 | 0 | 25.335 | 23.4091 | 0 | 0 | 0 | 1.2 | 372.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46644.5 | 0 | 46644.5 | 1751420 | -33624.8 | 72 | 89 | 1751420 | -1033624.8
8 | 2 | 17 | 3 | 35.4762 | 0 | 152.497 | 0 | 111.425 | 0 | 9.0109 | 23.0739 | 0 | 0 | 0 | 4.8 | 336.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35589.2 | 0 | 35589.2 | 1676180 | -36584.3 | 72 | 88 | 1676180 | -1036584.3
8 | 2 | 18 | 3 | 24.591 | 0 | 93.4203 | 0 | 82.2077 | 0 | 6.7363 | 21.4042 | 0 | 0 | 0 | 7.2 | 235.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21770.2 | 0 | 21770.2 | 1214910 | -43444.3 | 71 | 83 | 1214910 | -1043444.3
8 | 2 | 19 | 3 | 18.4583 | 0 | 62.7906 | 0 | 12.3918 | 0 | 13.1337 | 8.818 | 0 | 0 | 0 | 7.2 | 122.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15551.8 | 0 | 15551.8 | 196671 | 0 | 71 | 83 | 196671 | -1000000
8 | 2 | 20 | 3 | 18.4355 | 0 | 54.6418 | 0 | 10.3117 | 0 | 9.9296 | 8.818 | 0 | 0 | 0 | 7.2 | 109.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14861.1 | 0 | 14861.1 | 176117 | 0 | 71 | 81 | 176117 | -1000000
8 | 2 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 9.5755 | 0 | 9.047 | 8.818 | 0 | 0 | 0 | 7.2 | 97.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9318.7 | 0 | 9318.7 | 162983 | 0 | 72 | 80 | 162983 | -1000000
8 | 2 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 8.958 | 0 | 8.3998 | 8.818 | 0 | 0 | 0 | 6.4 | 88.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.67 | 0 | 9093.67 | 151909 | 0 | 71 | 79 | 151909 | -1000000
8 | 2 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 8.6766 | 0 | 8.1275 | 8.818 | 0 | 0 | 0 | 5.6 | 84.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.55 | 0 | 7929.55 | 146824 | 0 | 71 | 79 | 146824 | -1000000
8 | 2 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 8.5936 | 0 | 8.0504 | 8.818 | 0 | 0 | 0 | 4.8 | 83.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.97 | 0 | 7927.97 | 145356 | 0 | 72 | 79 | 145356 | -1000000
8 | 3 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.5424 | 0 | 8.0035 | 8.818 | 0 | 0 | 0 | 4.8 | 83.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.62 | 0 | 7926.62 | 144421 | 0 | 72 | 79 | 144421 | -1000000
8 | 3 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.5024 | 0 | 7.9672 | 8.818 | 0 | 0 | 0 | 4.8 | 83.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.35 | 0 | 7925.35 | 143687 | 0 | 73 | 78 | 143687 | -1000000
8 | 3 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.4598 | 0 | 7.9289 | 8.818 | 0 | 0 | 0 | 4.8 | 83.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7923.99 | 0 | 7923.99 | 142901 | 0 | 73 | 79 | 142901 | -1000000
8 | 3 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 13.3983 | 0 | 15.2704 | 12.8287 | 0 | 0 | 0 | 4.8 | 102.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8779.41 | 0 | 8779.41 | 235463 | 0 | 74 | 78 | 235463 | -1000000
8 | 3 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 17.6689 | 0 | 24.9169 | 12.8287 | 0 | 0 | 0 | 4.8 | 154.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10685.1 | 0 | 10685.1 | 313768 | 0 | 74 | 78 | 313768 | -1000000
8 | 3 | 6 | 4 | 46.2009 | 0 | 140.608 | 0 | 107.759 | 0 | 24.9169 | 24.5621 | 0 | 0 | 0 | 2.4 | 346.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28647.9 | 0 | 28647.9 | 1863040 | 0 | 75 | 79 | 1863040 | -1000000
8 | 3 | 7 | 4 | 39.3031 | 0 | 168.222 | 0 | 113.936 | 0 | 25.335 | 24.5106 | 0 | 0 | 0 | 0.8 | 372.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31406.7 | 0 | 31406.7 | 1860770 | -26122.9 | 75 | 80 | 1860770 | -1026122.9
8 | 3 | 8 | 4 | 39.6858 | 0 | 173.795 | 0 | 106.625 | 0 | 25.335 | 23.8039 | 0 | 0 | 0 | 0 | 369.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39725.1 | 0 | 39725.1 | 1759590 | -25630.9 | 75 | 81 | 1759590 | -1025630.9
8 | 3 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 111.442 | 0 | 25.335 | 23.251 | 0 | 0 | 0 | 0 | 372.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61838.6 | 0 | 61838.6 | 1831910 | -25288.6 | 76 | 83 | 1831910 | -1025288.6
8 | 3 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 118.728 | 0 | 25.335 | 23.2939 | 0 | 0 | 0 | 0 | 371.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.2 | 0 | 63222.2 | 1932350 | -27075.6 | 77 | 87 | 1932350 | -1027075.6
8 | 3 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 119.293 | 0 | 25.335 | 22.8601 | 0 | 0 | 0 | 0 | 357.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.4 | 0 | 63224.4 | 1809640 | -34671.1 | 78 | 89 | 1809640 | -1034671.1
8 | 3 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 129.779 | 0 | 12.2387 | 23.0394 | 0 | 0 | 0 | 0 | 355.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.5 | 0 | 63225.5 | 1910270 | -34532.9 | 78 | 92 | 1910270 | -1034532.9
8 | 3 | 13 | 4 | 41.2509 | 0 | 165.698 | 0 | 131.171 | 0 | 25.335 | 23.6931 | 0 | 0 | 0 | 0 | 387.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.7 | 0 | 63225.7 | 1994660 | -31071.6 | 78 | 92 | 1994660 | -1031071.6
8 | 3 | 14 | 4 | 40.6306 | 0 | 172.702 | 0 | 131.536 | 0 | 25.335 | 23.6686 | 0 | 0 | 0 | 0 | 393.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61844.3 | 0 | 61844.3 | 2028890 | -31195.2 | 78 | 92 | 2028890 | -1031195.2
8 | 3 | 15 | 4 | 40.5242 | 0 | 173.986 | 0 | 136.426 | 0 | 25.335 | 24.0433 | 0 | 0 | 0 | 0 | 400.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56316.8 | 0 | 56316.8 | 2074510 | -31420.9 | 78 | 94 | 2074510 | -1031420.9
8 | 3 | 16 | 4 | 41.4087 | 0 | 169.782 | 0 | 129.533 | 0 | 25.335 | 24.0932 | 0 | 0 | 0 | 1.2 | 391.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.7 | 0 | 46643.7 | 1979480 | -31084.8 | 77 | 91 | 1979480 | -1031084.8
8 | 3 | 17 | 4 | 36.2157 | 0 | 152.497 | 0 | 124.777 | 0 | 12.1005 | 23.6063 | 0 | 0 | 0 | 4.8 | 353.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588.6 | 0 | 35588.6 | 1877810 | -34472.4 | 77 | 87 | 1877810 | -1034472.4
8 | 3 | 18 | 4 | 29.6397 | 0 | 93.4203 | 0 | 99.6902 | 0 | 6.7972 | 21.6349 | 0 | 0 | 0 | 7.2 | 258.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.3 | 0 | 21769.3 | 1439210 | -47290.5 | 78 | 80 | 1439210 | -1047290.5
8 | 3 | 19 | 4 | 18.44 | 0 | 62.7906 | 0 | 12.7591 | 0 | 13.7851 | 8.818 | 0 | 0 | 0 | 7.2 | 123.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15550.9 | 0 | 15550.9 | 198986 | 0 | 77 | 82 | 198986 | -1000000
8 | 3 | 20 | 4 | 18.5326 | 0 | 54.6418 | 0 | 10.4229 | 0 | 10.0502 | 8.818 | 0 | 0 | 0 | 7.2 | 109.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14860.3 | 0 | 14860.3 | 177566 | 0 | 76 | 80 | 177566 | -1000000
8 | 3 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 9.6524 | 0 | 9.1244 | 8.818 | 0 | 0 | 0 | 7.2 | 97.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9317.62 | 0 | 9317.62 | 164124 | 0 | 75 | 78 | 164124 | -1000000
8 | 3 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 9.0235 | 0 | 8.4655 | 8.818 | 0 | 0 | 0 | 6.4 | 88.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9092.76 | 0 | 9092.76 | 153116 | 0 | 75 | 79 | 153116 | -1000000
8 | 3 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 8.7348 | 0 | 8.1825 | 8.818 | 0 | 0 | 0 | 5.6 | 84.1932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.59 | 0 | 7928.59 | 147894 | 0 | 75 | 79 | 147894 | -1000000
8 | 3 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 8.651 | 0 | 8.1036 | 8.818 | 0 | 0 | 0 | 4.8 | 83.5519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.09 | 0 | 7927.09 | 146412 | 0 | 76 | 78 | 146412 | -1000000
8 | 4 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.593 | 0 | 8.0498 | 8.818 | 0 | 0 | 0 | 4.8 | 83.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.72 | 0 | 7925.72 | 145351 | 0 | 75 | 77 | 145351 | -1000000
8 | 4 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.5451 | 0 | 8.006 | 8.818 | 0 | 0 | 0 | 4.8 | 83.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.4 | 0 | 7924.4 | 144472 | 0 | 75 | 77 | 144472 | -1000000
8 | 4 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.5017 | 0 | 7.9665 | 8.818 | 0 | 0 | 0 | 4.8 | 83.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7923.12 | 0 | 7923.12 | 143673 | 0 | 75 | 77 | 143673 | -1000000
8 | 4 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.7063 | 0 | 8.1554 | 8.818 | 0 | 0 | 0 | 4.8 | 87.1242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8778.7 | 0 | 8778.7 | 147519 | 0 | 75 | 77 | 147519 | -1000000
8 | 4 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 18.0137 | 0 | 24.9169 | 12.8287 | 0 | 0 | 0 | 4.8 | 154.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10684.4 | 0 | 10684.4 | 321627 | 0 | 75 | 77 | 321627 | -1000000
8 | 4 | 6 | 5 | 42.4623 | 0 | 140.608 | 0 | 112.673 | 0 | 24.9169 | 25.0224 | 0 | 0 | 0 | 2.4 | 348.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28647.3 | 0 | 28647.3 | 1908950 | 0 | 76 | 77 | 1908950 | -1000000
8 | 4 | 7 | 5 | 39.1384 | 0 | 168.222 | 0 | 119.209 | 0 | 25.335 | 24.4426 | 0 | 0 | 0 | 0.8 | 377.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31406.1 | 0 | 31406.1 | 1915050 | -25770.5 | 76 | 79 | 1915050 | -1025770.5
8 | 4 | 8 | 5 | 39.6738 | 0 | 173.795 | 0 | 115.186 | 0 | 25.335 | 22.6522 | 0 | 0 | 0 | 0 | 376.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39724.5 | 0 | 39724.5 | 1887900 | -27400.9 | 77 | 82 | 1887900 | -1027400.9
8 | 4 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 121.611 | 0 | 25.335 | 23.0709 | 0 | 0 | 0 | 0 | 382.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61838.3 | 0 | 61838.3 | 1985490 | -26615.6 | 79 | 84 | 1985490 | -1026615.6
8 | 4 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 124.224 | 0 | 25.335 | 23.6569 | 0 | 0 | 0 | 0 | 377.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.5 | 0 | 63223.5 | 2021280 | -22426.2 | 79 | 87 | 2021280 | -1022426.2
8 | 4 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 128.822 | 0 | 25.335 | 22.7864 | 0 | 0 | 0 | 0 | 367.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.6 | 0 | 63224.6 | 1935970 | -33198.7 | 80 | 91 | 1935970 | -1033198.7
8 | 4 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 129.327 | 0 | 25.335 | 23.1289 | 0 | 0 | 0 | 0 | 367.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.4 | 0 | 63225.4 | 1945350 | -33630.8 | 79 | 89 | 1945350 | -1033630.8
8 | 4 | 13 | 5 | 41.2656 | 0 | 165.698 | 0 | 136.39 | 0 | 25.335 | 23.7779 | 0 | 0 | 0 | 0 | 392.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226 | 0 | 63226 | 2097060 | -31070.6 | 80 | 90 | 2097060 | -1031070.6
8 | 4 | 14 | 5 | 40.6358 | 0 | 172.702 | 0 | 139.292 | 0 | 25.335 | 23.7138 | 0 | 0 | 0 | 0 | 401.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61844.1 | 0 | 61844.1 | 2134090 | -31167 | 81 | 93 | 2134090 | -1031167
8 | 4 | 15 | 5 | 40.5567 | 0 | 173.986 | 0 | 141.865 | 0 | 25.335 | 24.0459 | 0 | 0 | 0 | 0 | 405.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56316.5 | 0 | 56316.5 | 2157490 | -30932.8 | 80 | 94 | 2157490 | -1030932.8
8 | 4 | 16 | 5 | 40.3015 | 0 | 169.782 | 0 | 151.252 | 0 | 10.5775 | 24.6461 | 0 | 0 | 0 | 1.2 | 397.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.2 | 0 | 46643.2 | 2250700 | -30169.8 | 81 | 96 | 2250700 | -1030169.8
8 | 4 | 17 | 5 | 36.2991 | 0 | 152.497 | 0 | 135.148 | 0 | 7.9372 | 23.8472 | 0 | 0 | 0 | 4.8 | 360.529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588.1 | 0 | 35588.1 | 2004290 | -33380.4 | 79 | 89 | 2004290 | -1033380.4
8 | 4 | 18 | 5 | 28.2991 | 0 | 93.4203 | 0 | 68.5298 | 0 | 7.8712 | 21.6038 | 0 | 0 | 0 | 7.2 | 226.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.4 | 0 | 21769.4 | 1055160 | -47531.6 | 67 | 73 | 1055160 | -1047531.6
8 | 4 | 19 | 5 | 22.2704 | 0 | 62.7906 | 0 | 10.6301 | 0 | 9.8739 | 8.818 | 0 | 0 | 0 | 7.2 | 121.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15550.9 | 0 | 15550.9 | 197191 | 0 | 66 | 69 | 197191 | -1000000
8 | 4 | 20 | 5 | 18.5987 | 0 | 54.6418 | 0 | 10.3692 | 0 | 9.6266 | 8.818 | 0 | 0 | 0 | 7.2 | 109.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14860 | 0 | 14860 | 176984 | 0 | 67 | 70 | 176984 | -1000000
8 | 4 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 9.5513 | 0 | 8.8729 | 8.818 | 0 | 0 | 0 | 7.2 | 97.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9317.59 | 0 | 9317.59 | 163628 | 0 | 68 | 71 | 163628 | -1000000
8 | 4 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 8.3965 | 0 | 7.9117 | 8.818 | 0 | 0 | 0 | 6.4 | 87.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.61 | 0 | 9093.61 | 152448 | 0 | 68 | 71 | 152448 | -1000000
8 | 4 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.7919 | 0 | 7.3738 | 8.818 | 0 | 0 | 0 | 5.6 | 82.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.25 | 0 | 7930.25 | 147143 | 0 | 67 | 70 | 147143 | -1000000
8 | 4 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.6407 | 0 | 7.2297 | 8.818 | 0 | 0 | 0 | 4.8 | 77.6154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.35 | 0 | 7929.35 | 145082 | 0 | 66 | 69 | 145082 | -1000000
8 | 5 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2173 | 0 | 6.8877 | 8.818 | 0 | 0 | 0 | 4.8 | 76.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.53 | 0 | 7928.53 | 143923 | 0 | 65 | 67 | 143923 | -1000000
8 | 5 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0858 | 0 | 6.7594 | 8.818 | 0 | 0 | 0 | 4.8 | 76.5902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.49 | 0 | 7928.49 | 142883 | 0 | 64 | 65 | 142883 | -1000000
8 | 5 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.5926 | 0 | 7.0788 | 8.818 | 0 | 0 | 0 | 4.8 | 77.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.21 | 0 | 7928.21 | 141997 | 0 | 64 | 65 | 141997 | -1000000
8 | 5 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.5546 | 0 | 7.0534 | 8.818 | 0 | 0 | 0 | 4.8 | 77.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.08 | 0 | 7928.08 | 141224 | 0 | 65 | 65 | 141224 | -1000000
8 | 5 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.8334 | 0 | 7.2766 | 8.818 | 0 | 0 | 0 | 4.8 | 77.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.97 | 0 | 7927.97 | 140408 | 0 | 65 | 66 | 140408 | -1000000
8 | 5 | 6 | 6 | 5.6889 | 0 | 42.7453 | 0 | 8.343 | 0 | 7.4565 | 8.818 | 0 | 0 | 0 | 2.4 | 75.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.62 | 0 | 7927.62 | 139820 | 0 | 67 | 67 | 139820 | -1000000
8 | 5 | 7 | 6 | 4.6219 | 0 | 42.7453 | 0 | 39.0858 | 0 | 25.335 | 20 | 0 | 0 | 0 | 0.8 | 132.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.33 | 0 | 7927.33 | 680309 | -2876.44 | 68 | 71 | 680309 | -1002876.44
8 | 5 | 8 | 6 | 4.9311 | 0 | 42.7453 | 0 | 41.2301 | 0 | 25.335 | 19.7969 | 0 | 0 | 0 | 0 | 134.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.23 | 0 | 7927.23 | 686920 | -5442.71 | 70 | 75 | 686920 | -1005442.71
8 | 5 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 38.587 | 0 | 25.335 | 19.6344 | 0 | 0 | 0 | 0 | 131.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.48 | 0 | 7945.48 | 663896 | -8413.91 | 70 | 76 | 663896 | -1008413.91
8 | 5 | 10 | 6 | 5.6113 | 0 | 42.7453 | 0 | 40.0903 | 0 | 25.335 | 19.821 | 0 | 0 | 0 | 0 | 133.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.78 | 0 | 7948.78 | 689304 | -9513.58 | 71 | 79 | 689304 | -1009513.58
8 | 5 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 42.5378 | 0 | 25.335 | 20.0006 | 0 | 0 | 0 | 0 | 136.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7950.46 | 0 | 7950.46 | 728917 | -10251 | 72 | 81 | 728917 | -1010251
8 | 5 | 12 | 6 | 5.4693 | 0 | 42.7453 | 0 | 42.3711 | 0 | 25.335 | 19.765 | 0 | 0 | 0 | 0 | 135.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7951.05 | 0 | 7951.05 | 720950 | -20238.2 | 70 | 82 | 720950 | -1020238.2
8 | 5 | 13 | 6 | 5.4719 | 0 | 42.7453 | 0 | 44.2408 | 0 | 25.335 | 19.9505 | 0 | 0 | 0 | 0 | 137.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7951.96 | 0 | 7951.96 | 748434 | -26253.7 | 69 | 83 | 748434 | -1026253.7
8 | 5 | 14 | 6 | 5.4749 | 0 | 42.7453 | 0 | 13.2256 | 0 | 14.0549 | 12.8287 | 0 | 0 | 0 | 0 | 88.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7952.61 | 0 | 7952.61 | 209220 | 0 | 68 | 83 | 209220 | -1000000
8 | 5 | 15 | 6 | 5.4761 | 0 | 42.7453 | 0 | 13.0588 | 0 | 13.7574 | 12.8287 | 0 | 0 | 0 | 0 | 87.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7953.19 | 0 | 7953.19 | 215743 | 0 | 68 | 84 | 215743 | -1000000
8 | 5 | 16 | 6 | 5.4749 | 0 | 42.7453 | 0 | 15.8938 | 0 | 20.6878 | 14.8767 | 0 | 0 | 0 | 1.2 | 100.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7944.92 | 0 | 7944.92 | 269985 | 0 | 67 | 83 | 269985 | -1000000
8 | 5 | 17 | 6 | 5.4757 | 0 | 42.7453 | 0 | 15.6453 | 0 | 20.3051 | 14.8767 | 0 | 0 | 0 | 4.8 | 103.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7940.3 | 0 | 7940.3 | 268002 | 0 | 67 | 82 | 268002 | -1000000
8 | 5 | 18 | 6 | 5.4764 | 0 | 42.7453 | 0 | 10.932 | 0 | 10.6824 | 10.866 | 0 | 0 | 0 | 7.2 | 87.9021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.92 | 0 | 7936.92 | 184345 | 0 | 65 | 81 | 184345 | -1000000
8 | 5 | 19 | 6 | 6.7351 | 0 | 42.7453 | 0 | 8.0268 | 0 | 7.5545 | 8.818 | 0 | 0 | 0 | 7.2 | 81.0797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.19 | 0 | 7934.19 | 133875 | 0 | 65 | 78 | 133875 | -1000000
8 | 5 | 20 | 6 | 8.7054 | 0 | 42.7453 | 0 | 7.9909 | 0 | 7.5139 | 8.818 | 0 | 0 | 0 | 7.2 | 82.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.24 | 0 | 7932.24 | 133607 | 0 | 65 | 76 | 133607 | -1000000
8 | 5 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.2634 | 0 | 6.9302 | 8.818 | 0 | 0 | 0 | 7.2 | 81.7542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.5 | 0 | 7930.5 | 133099 | 0 | 63 | 73 | 133099 | -1000000
8 | 5 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5092 | 0 | 6.5353 | 8.818 | 0 | 0 | 0 | 6.4 | 79.8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.24 | 0 | 7929.24 | 132821 | 0 | 62 | 70 | 132821 | -1000000
8 | 5 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.7033 | 0 | 6.602 | 8.818 | 0 | 0 | 0 | 5.6 | 79.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.27 | 0 | 7928.27 | 132594 | 0 | 62 | 68 | 132594 | -1000000
8 | 5 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 7.5472 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 74.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.12 | 0 | 3091.12 | 132101 | 0 | 62 | 70 | 132101 | -1000000
8 | 6 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6751 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.61 | 0 | 3090.61 | 131703 | 0 | 61 | 69 | 131703 | -1000000
8 | 6 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.6239 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.44 | 0 | 3090.44 | 131441 | 0 | 61 | 68 | 131441 | -1000000
8 | 6 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5726 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.11 | 0 | 3090.11 | 131156 | 0 | 61 | 67 | 131156 | -1000000
8 | 6 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2151 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.83 | 0 | 3089.83 | 130723 | 0 | 60 | 65 | 130723 | -1000000
8 | 6 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 5.2662 | 0 | 5.5028 | 8.818 | 0 | 0 | 0 | 4.8 | 72.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.61 | 0 | 3089.61 | 130427 | 0 | 59 | 60 | 130427 | -1000000
8 | 6 | 6 | 7 | 4.7651 | 0 | 42.7453 | 0 | 6.7866 | 0 | 6.4949 | 8.818 | 0 | 0 | 0 | 2.4 | 72.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.54 | 0 | 3089.54 | 129553 | 0 | 55 | 57 | 129553 | -1000000
8 | 6 | 7 | 7 | 3.7784 | 0 | 42.7453 | 0 | 6.4999 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 0.8 | 68.1254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.6 | 0 | 3089.6 | 129358 | 0 | 54 | 57 | 129358 | -1000000
8 | 6 | 8 | 7 | 4.1475 | 0 | 42.7453 | 0 | 6.4769 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 0 | 67.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.94 | 0 | 3089.94 | 128850 | 0 | 52 | 57 | 128850 | -1000000
8 | 6 | 9 | 7 | 4.6708 | 0 | 42.7453 | 0 | 6.4689 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 0 | 68.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.51 | 0 | 3090.51 | 128680 | 0 | 51 | 57 | 128680 | -1000000
8 | 6 | 10 | 7 | 4.6201 | 0 | 42.7453 | 0 | 6.4611 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 0 | 68.1287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.86 | 0 | 3090.86 | 128509 | 0 | 51 | 57 | 128509 | -1000000
8 | 6 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.4528 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 0 | 67.6444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.31 | 0 | 3091.31 | 128328 | 0 | 52 | 59 | 128328 | -1000000
8 | 6 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.2719 | 0 | 5.4961 | 12.8287 | 0 | 0 | 0 | 0 | 74.486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.49 | 0 | 3091.49 | 157030 | 0 | 54 | 65 | 157030 | -1000000
8 | 6 | 13 | 7 | 4.145 | 0 | 42.7453 | 0 | 8.8807 | 0 | 5.4897 | 12.8287 | 0 | 0 | 0 | 0 | 74.0893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.63 | 0 | 3091.63 | 176619 | 0 | 54 | 65 | 176619 | -1000000
8 | 6 | 14 | 7 | 4.1474 | 0 | 42.7453 | 0 | 9.8262 | 0 | 5.5118 | 12.8287 | 0 | 0 | 0 | 0 | 75.0593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.64 | 0 | 3090.64 | 176056 | 0 | 55 | 68 | 176056 | -1000000
8 | 6 | 15 | 7 | 4.1485 | 0 | 42.7453 | 0 | 8.7665 | 0 | 5.4894 | 12.8287 | 0 | 0 | 0 | 0 | 73.9784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.88 | 0 | 3089.88 | 177403 | 0 | 54 | 67 | 177403 | -1000000
8 | 6 | 16 | 7 | 4.1476 | 0 | 42.7453 | 0 | 6.7103 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 1.2 | 69.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.77 | 0 | 3088.77 | 127618 | 0 | 55 | 67 | 127618 | -1000000
8 | 6 | 17 | 7 | 4.2115 | 0 | 42.7453 | 0 | 6.3559 | 0 | 5.4831 | 8.818 | 0 | 0 | 0 | 4.8 | 72.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.05 | 0 | 3088.05 | 127354 | 0 | 54 | 66 | 127354 | -1000000
8 | 6 | 18 | 7 | 4.4348 | 0 | 42.7453 | 0 | 6.627 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 7.2 | 75.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3087.35 | 0 | 3087.35 | 127489 | 0 | 55 | 66 | 127489 | -1000000
8 | 6 | 19 | 7 | 5.1699 | 0 | 42.7453 | 0 | 6.0177 | 0 | 5.4877 | 8.818 | 0 | 0 | 0 | 7.2 | 75.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.7 | 0 | 3086.7 | 127233 | 0 | 54 | 64 | 127233 | -1000000
8 | 6 | 20 | 7 | 6.5893 | 0 | 42.7453 | 0 | 5.3745 | 0 | 5.5006 | 8.818 | 0 | 0 | 0 | 7.2 | 76.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.36 | 0 | 3086.36 | 127188 | 0 | 53 | 59 | 127188 | -1000000
8 | 6 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.387 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.28 | 0 | 3086.28 | 126886 | 0 | 52 | 57 | 126886 | -1000000
8 | 6 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3891 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 6.4 | 76.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.41 | 0 | 3086.41 | 126937 | 0 | 53 | 57 | 126937 | -1000000
8 | 6 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3829 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 5.6 | 75.6945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.88 | 0 | 3086.88 | 126799 | 0 | 54 | 57 | 126799 | -1000000
8 | 6 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.3937 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 4.8 | 78.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7923.97 | 0 | 7923.97 | 127042 | 0 | 55 | 57 | 127042 | -1000000
8 | 7 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.6082 | 0 | 5.4786 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.55 | 0 | 7924.55 | 154068 | 0 | 55 | 57 | 154068 | -1000000
8 | 7 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3945 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.33 | 0 | 7924.33 | 126598 | 0 | 55 | 57 | 126598 | -1000000
8 | 7 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3636 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.42 | 0 | 7924.42 | 126374 | 0 | 54 | 56 | 126374 | -1000000
8 | 7 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.5174 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 4.8 | 82.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8781.18 | 0 | 8781.18 | 129801 | 0 | 52 | 54 | 129801 | -1000000
8 | 7 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 11.1407 | 0 | 5.5367 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10688.2 | 0 | 10688.2 | 232678 | 0 | 52 | 53 | 232678 | -1000000
8 | 7 | 6 | 1 | 43.2978 | 0 | 140.608 | 0 | 41.6234 | 0 | 6.332 | 21.2023 | 0 | 0 | 0 | 2.4 | 255.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28652.3 | 0 | 28652.3 | 702537 | -13316.5 | 53 | 54 | 702537 | -1013316.5
8 | 7 | 7 | 1 | 39.2591 | 0 | 168.222 | 0 | 45.8462 | 0 | 6.332 | 21.0275 | 0 | 0 | 0 | 0.8 | 281.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31412.4 | 0 | 31412.4 | 789448 | -25023.1 | 55 | 58 | 789448 | -1025023.1
8 | 7 | 8 | 1 | 39.8902 | 0 | 173.795 | 0 | 45.8734 | 0 | 6.332 | 20.9519 | 0 | 0 | 0 | 0 | 286.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39722.3 | 0 | 39722.3 | 826049 | -22691.7 | 55 | 61 | 826049 | -1022691.7
8 | 7 | 9 | 1 | 40.6566 | 0 | 172.186 | 0 | 51.9917 | 0 | 6.332 | 21.0586 | 0 | 0 | 0 | 0 | 292.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61836.7 | 0 | 61836.7 | 910671 | -22040.5 | 57 | 64 | 910671 | -1022040.5
8 | 7 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 53.1311 | 0 | 6.332 | 21.4278 | 0 | 0 | 0 | 0 | 285.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.5 | 0 | 63221.5 | 940487 | -18808.9 | 58 | 66 | 940487 | -1018808.9
8 | 7 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 46.7122 | 0 | 6.332 | 22.3334 | 0 | 0 | 0 | 0 | 265.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.8 | 0 | 63222.8 | 825284 | -14630.1 | 56 | 69 | 825284 | -1014630.1
8 | 7 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 54.0919 | 0 | 7.1844 | 21.8386 | 0 | 0 | 0 | 0 | 273.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.2 | 0 | 63223.2 | 931590 | -26477.9 | 58 | 71 | 931590 | -1026477.9
8 | 7 | 13 | 1 | 41.2627 | 0 | 165.698 | 0 | 54.3455 | 0 | 25.335 | 22.9043 | 0 | 0 | 0 | 0 | 309.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.2 | 0 | 63223.2 | 964486 | -15286.3 | 57 | 72 | 964486 | -1015286.3
8 | 7 | 14 | 1 | 40.6645 | 0 | 172.702 | 0 | 61.6747 | 0 | 25.335 | 22.7225 | 0 | 0 | 0 | 0 | 323.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.5 | 0 | 61841.5 | 1057370 | -18153.2 | 58 | 74 | 1057370 | -1018153.2
8 | 7 | 15 | 1 | 40.5558 | 0 | 173.986 | 0 | 64.916 | 0 | 25.335 | 22.8923 | 0 | 0 | 0 | 0 | 327.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56314.3 | 0 | 56314.3 | 1124980 | -20049.9 | 59 | 74 | 1124980 | -1020049.9
8 | 7 | 16 | 1 | 40.2978 | 0 | 169.782 | 0 | 61.0891 | 0 | 25.335 | 23.0241 | 0 | 0 | 0 | 1.2 | 320.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46641.2 | 0 | 46641.2 | 1079580 | -20406.5 | 58 | 74 | 1079580 | -1020406.5
8 | 7 | 17 | 1 | 35.4803 | 0 | 152.497 | 0 | 55.8639 | 0 | 23.369 | 22.4994 | 0 | 0 | 0 | 4.8 | 294.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35585.9 | 0 | 35585.9 | 1002240 | -26822.2 | 58 | 74 | 1002240 | -1026822.2
8 | 7 | 18 | 1 | 24.6484 | 0 | 93.4203 | 0 | 36.3337 | 0 | 25.335 | 20.5273 | 0 | 0 | 0 | 7.2 | 207.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21766.9 | 0 | 21766.9 | 698822 | -27097.2 | 57 | 72 | 698822 | -1027097.2
8 | 7 | 19 | 1 | 19.0325 | 0 | 62.7906 | 0 | 8.9501 | 0 | 5.4931 | 8.818 | 0 | 0 | 0 | 7.2 | 112.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15548.4 | 0 | 15548.4 | 188514 | 0 | 57 | 68 | 188514 | -1000000
8 | 7 | 20 | 1 | 18.5249 | 0 | 54.6418 | 0 | 7.7374 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 102.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14858.7 | 0 | 14858.7 | 168441 | 0 | 56 | 65 | 168441 | -1000000
8 | 7 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 6.7118 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 7.2 | 90.9316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9317.98 | 0 | 9317.98 | 155466 | 0 | 56 | 61 | 155466 | -1000000
8 | 7 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.9321 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.59 | 0 | 9094.59 | 144247 | 0 | 54 | 57 | 144247 | -1000000
8 | 7 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.9675 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.92 | 0 | 7931.92 | 139517 | 0 | 53 | 55 | 139517 | -1000000
8 | 7 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.9068 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.64 | 0 | 7931.64 | 138246 | 0 | 54 | 55 | 138246 | -1000000
8 | 8 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8666 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.56 | 0 | 7931.56 | 137371 | 0 | 54 | 55 | 137371 | -1000000
8 | 8 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8352 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.53 | 0 | 7931.53 | 136688 | 0 | 55 | 57 | 136688 | -1000000
8 | 8 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8056 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.06 | 0 | 7932.06 | 136040 | 0 | 55 | 56 | 136040 | -1000000
8 | 8 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.9404 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8788.61 | 0 | 8788.61 | 139053 | 0 | 55 | 57 | 139053 | -1000000
8 | 8 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 11.6563 | 0 | 5.5546 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10695.6 | 0 | 10695.6 | 244006 | 0 | 54 | 58 | 244006 | -1000000
8 | 8 | 6 | 2 | 47.0955 | 0 | 140.608 | 0 | 37.9035 | 0 | 6.332 | 20.7883 | 0 | 0 | 0 | 2.4 | 255.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28660 | 0 | 28660 | 686645 | -10801.7 | 55 | 58 | 686645 | -1010801.7
8 | 8 | 7 | 2 | 40.8294 | 0 | 168.222 | 0 | 42.2484 | 0 | 12.843 | 20.6992 | 0 | 0 | 0 | 0.8 | 285.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31419.7 | 0 | 31419.7 | 753765 | -26164.3 | 55 | 59 | 753765 | -1026164.3
8 | 8 | 8 | 2 | 39.9004 | 0 | 173.795 | 0 | 44.8722 | 0 | 25.335 | 21.0716 | 0 | 0 | 0 | 0 | 304.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39728.1 | 0 | 39728.1 | 817972 | -24836.2 | 57 | 62 | 817972 | -1024836.2
8 | 8 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 56.3757 | 0 | 25.335 | 21.3007 | 0 | 0 | 0 | 0 | 315.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61840.2 | 0 | 61840.2 | 954548 | -23044.1 | 59 | 68 | 954548 | -1023044.1
8 | 8 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 60.2732 | 0 | 25.335 | 21.4964 | 0 | 0 | 0 | 0 | 311.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.1 | 0 | 63223.1 | 1040860 | -19281 | 61 | 71 | 1040860 | -1019281
8 | 8 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 59.5255 | 0 | 25.335 | 22.3399 | 0 | 0 | 0 | 0 | 297.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.9 | 0 | 63225.9 | 1001060 | -14586.7 | 62 | 74 | 1001060 | -1014586.7
8 | 8 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 66.3105 | 0 | 25.335 | 21.9323 | 0 | 0 | 0 | 0 | 303.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.7 | 0 | 63226.7 | 1115280 | -28430.3 | 63 | 77 | 1115280 | -1028430.3
8 | 8 | 13 | 2 | 41.2787 | 0 | 165.698 | 0 | 70.5607 | 0 | 25.335 | 23.095 | 0 | 0 | 0 | 0 | 325.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.9 | 0 | 63226.9 | 1185880 | -14837.5 | 63 | 78 | 1185880 | -1014837.5
8 | 8 | 14 | 2 | 40.6621 | 0 | 172.702 | 0 | 74.1669 | 0 | 25.335 | 22.8043 | 0 | 0 | 0 | 0 | 335.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61845.2 | 0 | 61845.2 | 1242070 | -19162.7 | 63 | 79 | 1242070 | -1019162.7
8 | 8 | 15 | 2 | 40.5665 | 0 | 173.986 | 0 | 75.842 | 0 | 25.335 | 22.9749 | 0 | 0 | 0 | 0 | 338.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56317.9 | 0 | 56317.9 | 1272310 | -20806.7 | 63 | 80 | 1272310 | -1020806.7
8 | 8 | 16 | 2 | 40.2937 | 0 | 169.782 | 0 | 75.0813 | 0 | 25.335 | 23.0771 | 0 | 0 | 0 | 1.2 | 334.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46644.6 | 0 | 46644.6 | 1276480 | -22713 | 63 | 80 | 1276480 | -1022713
8 | 8 | 17 | 2 | 35.4867 | 0 | 152.497 | 0 | 70.3629 | 0 | 25.335 | 22.4526 | 0 | 0 | 0 | 4.8 | 310.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35589.1 | 0 | 35589.1 | 1212360 | -32128.9 | 63 | 79 | 1212360 | -1032128.9
8 | 8 | 18 | 2 | 24.5968 | 0 | 93.4203 | 0 | 50.7092 | 0 | 25.335 | 20.9919 | 0 | 0 | 0 | 7.2 | 222.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21770.2 | 0 | 21770.2 | 885219 | -26184.7 | 64 | 78 | 885219 | -1026184.7
8 | 8 | 19 | 2 | 19.0651 | 0 | 62.7906 | 0 | 11.4252 | 0 | 11.4825 | 8.818 | 0 | 0 | 0 | 7.2 | 120.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15551.5 | 0 | 15551.5 | 193225 | 0 | 63 | 74 | 193225 | -1000000
8 | 8 | 20 | 2 | 18.532 | 0 | 54.6418 | 0 | 7.695 | 0 | 7.383 | 8.818 | 0 | 0 | 0 | 7.2 | 104.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14861.3 | 0 | 14861.3 | 173102 | 0 | 62 | 69 | 173102 | -1000000
8 | 8 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.0585 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 91.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.37 | 0 | 9320.37 | 159701 | 0 | 61 | 65 | 159701 | -1000000
8 | 8 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 6.9817 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.52 | 0 | 9096.52 | 148522 | 0 | 60 | 63 | 148522 | -1000000
8 | 8 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9735 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.37 | 0 | 7933.37 | 143649 | 0 | 60 | 62 | 143649 | -1000000
8 | 8 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8622 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.78 | 0 | 7932.78 | 142090 | 0 | 60 | 61 | 142090 | -1000000
8 | 9 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0749 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.29 | 0 | 7932.29 | 141115 | 0 | 60 | 61 | 141115 | -1000000
8 | 9 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7254 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.42 | 0 | 7932.42 | 139890 | 0 | 57 | 58 | 139890 | -1000000
8 | 9 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9508 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.43 | 0 | 7932.43 | 139217 | 0 | 57 | 57 | 139217 | -1000000
8 | 9 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.0887 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8789.3 | 0 | 8789.3 | 142298 | 0 | 58 | 59 | 142298 | -1000000
8 | 9 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 12.268 | 0 | 5.5791 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10696.5 | 0 | 10696.5 | 257577 | 0 | 58 | 59 | 257577 | -1000000
8 | 9 | 6 | 3 | 43.4626 | 0 | 140.608 | 0 | 41.4296 | 0 | 8.2722 | 20.9312 | 0 | 0 | 0 | 2.4 | 257.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28660.4 | 0 | 28660.4 | 792277 | -9157.02 | 58 | 59 | 792277 | -1009157.02
8 | 9 | 7 | 3 | 39.1221 | 0 | 168.222 | 0 | 52.5932 | 0 | 6.332 | 21.2077 | 0 | 0 | 0 | 0.8 | 288.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31420.2 | 0 | 31420.2 | 943973 | -27138.4 | 60 | 62 | 943973 | -1027138.4
8 | 9 | 8 | 3 | 39.7521 | 0 | 173.795 | 0 | 56.8484 | 0 | 25.335 | 20.9737 | 0 | 0 | 0 | 0 | 316.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39729 | 0 | 39729 | 1009700 | -25506 | 61 | 66 | 1009700 | -1025506
8 | 9 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 65.3339 | 0 | 25.335 | 21.4305 | 0 | 0 | 0 | 0 | 324.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.7 | 0 | 61841.7 | 1092670 | -23657.7 | 62 | 72 | 1092670 | -1023657.7
8 | 9 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 72.5183 | 0 | 25.335 | 21.8881 | 0 | 0 | 0 | 0 | 323.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.6 | 0 | 63226.6 | 1225270 | -19497.4 | 65 | 76 | 1225270 | -1019497.4
8 | 9 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 68.923 | 0 | 25.335 | 22.5824 | 0 | 0 | 0 | 0 | 307.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228 | 0 | 63228 | 1176370 | -14328.7 | 66 | 80 | 1176370 | -1014328.7
8 | 9 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 71.0487 | 0 | 25.335 | 22.0244 | 0 | 0 | 0 | 0 | 308.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.6 | 0 | 63228.6 | 1202660 | -31640.9 | 64 | 83 | 1202660 | -1031640.9
8 | 9 | 13 | 3 | 41.2531 | 0 | 165.698 | 0 | 74.2066 | 0 | 25.335 | 23.4204 | 0 | 0 | 0 | 0 | 329.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.6 | 0 | 63228.6 | 1248040 | -14920.3 | 63 | 85 | 1248040 | -1014920.3
8 | 9 | 14 | 3 | 40.6357 | 0 | 172.702 | 0 | 79.2079 | 0 | 25.335 | 23.1064 | 0 | 0 | 0 | 0 | 340.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61846.8 | 0 | 61846.8 | 1327250 | -19563.5 | 64 | 85 | 1327250 | -1019563.5
8 | 9 | 15 | 3 | 40.5539 | 0 | 173.986 | 0 | 84.3298 | 0 | 25.335 | 23.0328 | 0 | 0 | 0 | 0 | 347.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56319.6 | 0 | 56319.6 | 1409210 | -24301.6 | 65 | 84 | 1409210 | -1024301.6
8 | 9 | 16 | 3 | 40.2946 | 0 | 169.782 | 0 | 82.3214 | 0 | 25.335 | 23.0318 | 0 | 0 | 0 | 1.2 | 341.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46646.2 | 0 | 46646.2 | 1393880 | -26827 | 65 | 84 | 1393880 | -1026827
8 | 9 | 17 | 3 | 35.4777 | 0 | 152.497 | 0 | 78.7275 | 0 | 25.335 | 22.5391 | 0 | 0 | 0 | 4.8 | 319.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35590.7 | 0 | 35590.7 | 1284380 | -33946.2 | 64 | 84 | 1284380 | -1033946.2
8 | 9 | 18 | 3 | 24.6005 | 0 | 93.4203 | 0 | 55.2224 | 0 | 25.335 | 21.3881 | 0 | 0 | 0 | 7.2 | 227.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21771.7 | 0 | 21771.7 | 928962 | -29293.8 | 64 | 83 | 928962 | -1029293.8
8 | 9 | 19 | 3 | 18.987 | 0 | 62.7906 | 0 | 11.9736 | 0 | 12.4836 | 8.818 | 0 | 0 | 0 | 7.2 | 122.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15553.1 | 0 | 15553.1 | 195431 | 0 | 64 | 78 | 195431 | -1000000
8 | 9 | 20 | 3 | 18.6031 | 0 | 54.6418 | 0 | 8.07 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 7.2 | 102.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14862.5 | 0 | 14862.5 | 175302 | 0 | 64 | 71 | 175302 | -1000000
8 | 9 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.5378 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9321.18 | 0 | 9321.18 | 161588 | 0 | 63 | 68 | 161588 | -1000000
8 | 9 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 6.8835 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.75 | 0 | 9096.75 | 150397 | 0 | 62 | 65 | 150397 | -1000000
8 | 9 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8184 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 5.6 | 79.5747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.56 | 0 | 7933.56 | 145100 | 0 | 60 | 63 | 145100 | -1000000
8 | 9 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.9682 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.98 | 0 | 7932.98 | 143590 | 0 | 60 | 62 | 143590 | -1000000
8 | 10 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.1792 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.71 | 0 | 7932.71 | 142553 | 0 | 60 | 62 | 142553 | -1000000
8 | 10 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8416 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.62 | 0 | 7932.62 | 141653 | 0 | 60 | 61 | 141653 | -1000000
8 | 10 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0575 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.56 | 0 | 7932.56 | 140738 | 0 | 60 | 61 | 140738 | -1000000
8 | 10 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.8921 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8789.28 | 0 | 8789.28 | 143608 | 0 | 59 | 60 | 143608 | -1000000
8 | 10 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.1311 | 0 | 5.5733 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10696.3 | 0 | 10696.3 | 254505 | 0 | 57 | 58 | 254505 | -1000000
8 | 10 | 6 | 4 | 43.7534 | 0 | 140.608 | 0 | 41.4339 | 0 | 6.332 | 21.0338 | 0 | 0 | 0 | 2.4 | 255.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28660.4 | 0 | 28660.4 | 817993 | -8428.13 | 58 | 59 | 817993 | -1008428.13
8 | 10 | 7 | 4 | 39.1147 | 0 | 168.222 | 0 | 56.0038 | 0 | 6.332 | 21.6681 | 0 | 0 | 0 | 0.8 | 292.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31420.4 | 0 | 31420.4 | 996917 | -28625.8 | 61 | 64 | 996917 | -1028625.8
8 | 10 | 8 | 4 | 39.7152 | 0 | 173.795 | 0 | 61.884 | 0 | 12.6152 | 21.1676 | 0 | 0 | 0 | 0 | 309.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39729.3 | 0 | 39729.3 | 1092110 | -26853.9 | 63 | 68 | 1092110 | -1026853.9
8 | 10 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 70.6611 | 0 | 25.335 | 21.5907 | 0 | 0 | 0 | 0 | 330.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.7 | 0 | 61841.7 | 1175940 | -25007.6 | 64 | 74 | 1175940 | -1025007.6
8 | 10 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 75.0292 | 0 | 25.335 | 22.0774 | 0 | 0 | 0 | 0 | 326.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.8 | 0 | 63226.8 | 1279220 | -20719.1 | 66 | 78 | 1279220 | -1020719.1
8 | 10 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 73.8633 | 0 | 25.335 | 22.6775 | 0 | 0 | 0 | 0 | 312.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.2 | 0 | 63228.2 | 1258010 | -15682.8 | 68 | 80 | 1258010 | -1015682.8
8 | 10 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 82.8761 | 0 | 25.335 | 22.2189 | 0 | 0 | 0 | 0 | 320.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.8 | 0 | 63228.8 | 1392070 | -31535.5 | 69 | 84 | 1392070 | -1031535.5
8 | 10 | 13 | 4 | 41.2374 | 0 | 165.698 | 0 | 85.1047 | 0 | 25.335 | 23.5591 | 0 | 0 | 0 | 0 | 340.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.8 | 0 | 63228.8 | 1442080 | -16022.6 | 68 | 86 | 1442080 | -1016022.6
8 | 10 | 14 | 4 | 40.6324 | 0 | 172.702 | 0 | 93.5274 | 0 | 25.335 | 22.8472 | 0 | 0 | 0 | 0 | 355.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61847 | 0 | 61847 | 1576600 | -27440 | 70 | 86 | 1576600 | -1027440
8 | 10 | 15 | 4 | 40.5496 | 0 | 173.986 | 0 | 94.6281 | 0 | 25.335 | 22.9383 | 0 | 0 | 0 | 0 | 357.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56319.7 | 0 | 56319.7 | 1585350 | -30660.6 | 69 | 86 | 1585350 | -1030660.6
8 | 10 | 16 | 4 | 40.2879 | 0 | 169.782 | 0 | 96.7641 | 0 | 25.335 | 23.0271 | 0 | 0 | 0 | 1.2 | 356.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46646.4 | 0 | 46646.4 | 1551560 | -33490.3 | 68 | 88 | 1551560 | -1033490.3
8 | 10 | 17 | 4 | 35.4815 | 0 | 152.497 | 0 | 84.8958 | 0 | 25.335 | 22.8801 | 0 | 0 | 0 | 4.8 | 325.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35591 | 0 | 35591 | 1398470 | -29873.2 | 67 | 85 | 1398470 | -1029873.2
8 | 10 | 18 | 4 | 24.6025 | 0 | 93.4203 | 0 | 62.0779 | 0 | 14.6976 | 21.3769 | 0 | 0 | 0 | 7.2 | 223.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21772.1 | 0 | 21772.1 | 1016450 | -32616.5 | 67 | 82 | 1016450 | -1032616.5
8 | 10 | 19 | 4 | 19.2107 | 0 | 62.7906 | 0 | 11.3074 | 0 | 12.15 | 8.818 | 0 | 0 | 0 | 7.2 | 121.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15553.5 | 0 | 15553.5 | 195783 | 0 | 65 | 77 | 195783 | -1000000
8 | 10 | 20 | 4 | 18.6682 | 0 | 54.6418 | 0 | 8.7409 | 0 | 5.4936 | 8.818 | 0 | 0 | 0 | 7.2 | 103.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14862.8 | 0 | 14862.8 | 175740 | 0 | 65 | 73 | 175740 | -1000000
8 | 10 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.3371 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9321.25 | 0 | 9321.25 | 162111 | 0 | 64 | 69 | 162111 | -1000000
8 | 10 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.5576 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.8 | 0 | 9096.8 | 150813 | 0 | 63 | 68 | 150813 | -1000000
8 | 10 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.2707 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 80.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.51 | 0 | 7933.51 | 145782 | 0 | 62 | 67 | 145782 | -1000000
8 | 10 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.5443 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.8 | 0 | 7932.8 | 144103 | 0 | 61 | 64 | 144103 | -1000000
8 | 11 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9759 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.34 | 0 | 7932.34 | 142949 | 0 | 60 | 63 | 142949 | -1000000
8 | 11 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9068 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.58 | 0 | 7931.58 | 142276 | 0 | 61 | 62 | 142276 | -1000000
8 | 11 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.5206 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.47 | 0 | 7931.47 | 141022 | 0 | 59 | 60 | 141022 | -1000000
8 | 11 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.4735 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 83.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8788.06 | 0 | 8788.06 | 144250 | 0 | 60 | 61 | 144250 | -1000000
8 | 11 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.2096 | 0 | 5.6351 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10695 | 0 | 10695 | 262427 | 0 | 61 | 63 | 262427 | -1000000
8 | 11 | 6 | 5 | 44.948 | 0 | 140.608 | 0 | 47.1277 | 0 | 6.332 | 21.723 | 0 | 0 | 0 | 2.4 | 263.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28659.1 | 0 | 28659.1 | 995629 | -7293.54 | 62 | 63 | 995629 | -1007293.54
8 | 11 | 7 | 5 | 39.1397 | 0 | 168.222 | 0 | 73.5455 | 0 | 6.332 | 22.6332 | 0 | 0 | 0 | 0.8 | 310.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31419 | 0 | 31419 | 1209540 | -27467.1 | 65 | 72 | 1209540 | -1027467.1
8 | 11 | 8 | 5 | 39.6961 | 0 | 173.795 | 0 | 68.6803 | 0 | 14.1938 | 21.9439 | 0 | 0 | 0 | 0 | 318.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39728.7 | 0 | 39728.7 | 1206330 | -26514.8 | 65 | 72 | 1206330 | -1026514.8
8 | 11 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 74.7333 | 0 | 25.335 | 21.9345 | 0 | 0 | 0 | 0 | 334.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.3 | 0 | 61841.3 | 1280100 | -25767.3 | 66 | 74 | 1280100 | -1025767.3
8 | 11 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 80.8468 | 0 | 25.335 | 22.4717 | 0 | 0 | 0 | 0 | 332.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.6 | 0 | 63225.6 | 1372220 | -21249.6 | 68 | 79 | 1372220 | -1021249.6
8 | 11 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 77.6373 | 0 | 25.335 | 22.8836 | 0 | 0 | 0 | 0 | 316.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63227.5 | 0 | 63227.5 | 1311240 | -16253.7 | 69 | 83 | 1311240 | -1016253.7
8 | 11 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 85.947 | 0 | 25.335 | 22.3356 | 0 | 0 | 0 | 0 | 323.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63227.9 | 0 | 63227.9 | 1383970 | -33385.9 | 68 | 87 | 1383970 | -1033385.9
8 | 11 | 13 | 5 | 41.2418 | 0 | 165.698 | 0 | 84.3776 | 0 | 25.335 | 23.2749 | 0 | 0 | 0 | 0 | 339.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.3 | 0 | 63228.3 | 1411130 | -22467.4 | 67 | 84 | 1411130 | -1022467.4
8 | 11 | 14 | 5 | 40.6507 | 0 | 172.702 | 0 | 84.6979 | 0 | 25.335 | 22.8706 | 0 | 0 | 0 | 0 | 346.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61846.7 | 0 | 61846.7 | 1413750 | -28765.8 | 66 | 84 | 1413750 | -1028765.8
8 | 11 | 15 | 5 | 40.5431 | 0 | 173.986 | 0 | 87.0688 | 0 | 25.335 | 23.2069 | 0 | 0 | 0 | 0 | 350.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56319.1 | 0 | 56319.1 | 1456430 | -25400.9 | 66 | 83 | 1456430 | -1025400.9
8 | 11 | 16 | 5 | 40.302 | 0 | 169.782 | 0 | 88.0254 | 0 | 25.335 | 23.1789 | 0 | 0 | 0 | 1.2 | 347.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46645.8 | 0 | 46645.8 | 1487730 | -29390.8 | 67 | 85 | 1487730 | -1029390.8
8 | 11 | 17 | 5 | 35.4785 | 0 | 152.497 | 0 | 89.238 | 0 | 25.335 | 22.76 | 0 | 0 | 0 | 4.8 | 330.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35590.5 | 0 | 35590.5 | 1421100 | -34835.3 | 67 | 85 | 1421100 | -1034835.3
8 | 11 | 18 | 5 | 24.5987 | 0 | 93.4203 | 0 | 61.229 | 0 | 25.335 | 21.5245 | 0 | 0 | 0 | 7.2 | 233.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21771.4 | 0 | 21771.4 | 1004950 | -31493.8 | 66 | 83 | 1004950 | -1031493.8
8 | 11 | 19 | 5 | 19.4058 | 0 | 62.7906 | 0 | 12.1306 | 0 | 12.7216 | 8.818 | 0 | 0 | 0 | 7.2 | 123.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15553 | 0 | 15553 | 196400 | 0 | 66 | 79 | 196400 | -1000000
8 | 11 | 20 | 5 | 18.6422 | 0 | 54.6418 | 0 | 10.3124 | 0 | 9.9304 | 8.818 | 0 | 0 | 0 | 7.2 | 109.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14862.3 | 0 | 14862.3 | 176133 | 0 | 66 | 75 | 176133 | -1000000
8 | 11 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.6848 | 0 | 7.3645 | 8.818 | 0 | 0 | 0 | 7.2 | 93.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.76 | 0 | 9320.76 | 162464 | 0 | 65 | 71 | 162464 | -1000000
8 | 11 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.0482 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.19 | 0 | 9096.19 | 151376 | 0 | 65 | 68 | 151376 | -1000000
8 | 11 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 6.9464 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.73 | 0 | 7932.73 | 145381 | 0 | 60 | 66 | 145381 | -1000000
8 | 11 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.13 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.65 | 0 | 7931.65 | 144593 | 0 | 63 | 65 | 144593 | -1000000
8 | 12 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.03 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.83 | 0 | 7930.83 | 143284 | 0 | 63 | 64 | 143284 | -1000000
8 | 12 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2419 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 75.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.27 | 0 | 7931.27 | 142214 | 0 | 63 | 64 | 142214 | -1000000
8 | 12 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8916 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.29 | 0 | 7931.29 | 141133 | 0 | 62 | 63 | 141133 | -1000000
8 | 12 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.522 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 4.8 | 74.7503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.42 | 0 | 7931.42 | 140310 | 0 | 61 | 61 | 140310 | -1000000
8 | 12 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9945 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.15 | 0 | 7931.15 | 139367 | 0 | 60 | 61 | 139367 | -1000000
8 | 12 | 6 | 6 | 5.7131 | 0 | 42.7453 | 0 | 6.9614 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 2.4 | 72.1178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.41 | 0 | 7931.41 | 138649 | 0 | 60 | 61 | 138649 | -1000000
8 | 12 | 7 | 6 | 4.6142 | 0 | 42.7453 | 0 | 28.0211 | 0 | 25.335 | 19.2625 | 0 | 0 | 0 | 0.8 | 120.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.25 | 0 | 7931.25 | 498418 | -4746.37 | 63 | 65 | 498418 | -1004746.37
8 | 12 | 8 | 6 | 4.936 | 0 | 42.7453 | 0 | 29.0423 | 0 | 25.335 | 19.3003 | 0 | 0 | 0 | 0 | 121.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.54 | 0 | 7931.54 | 500522 | -6181.77 | 65 | 69 | 500522 | -1006181.77
8 | 12 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 32.8688 | 0 | 25.335 | 19.3057 | 0 | 0 | 0 | 0 | 125.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.08 | 0 | 7948.08 | 542389 | -10750.9 | 66 | 74 | 542389 | -1010750.9
8 | 12 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 34.6944 | 0 | 25.335 | 19.3652 | 0 | 0 | 0 | 0 | 127.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7950.61 | 0 | 7950.61 | 590104 | -11596 | 68 | 78 | 590104 | -1011596
8 | 12 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 39.1756 | 0 | 25.335 | 19.6117 | 0 | 0 | 0 | 0 | 132.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7952.54 | 0 | 7952.54 | 676794 | -18906.4 | 69 | 82 | 676794 | -1018906.4
8 | 12 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 40.6948 | 0 | 25.335 | 19.8007 | 0 | 0 | 0 | 0 | 134.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7953 | 0 | 7953 | 702767 | -20774.8 | 69 | 84 | 702767 | -1020774.8
8 | 12 | 13 | 6 | 5.4712 | 0 | 42.7453 | 0 | 42.6102 | 0 | 25.335 | 19.718 | 0 | 0 | 0 | 0 | 135.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7953.94 | 0 | 7953.94 | 722807 | -28438.4 | 68 | 84 | 722807 | -1028438.4
8 | 12 | 14 | 6 | 5.4727 | 0 | 42.7453 | 0 | 12.8771 | 0 | 13.72 | 12.8287 | 0 | 0 | 0 | 0 | 87.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.38 | 0 | 7954.38 | 208680 | 0 | 68 | 86 | 208680 | -1000000
8 | 12 | 15 | 6 | 5.4725 | 0 | 42.7453 | 0 | 12.6737 | 0 | 13.4006 | 12.8287 | 0 | 0 | 0 | 0 | 87.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.97 | 0 | 7954.97 | 214740 | 0 | 67 | 85 | 214740 | -1000000
8 | 12 | 16 | 6 | 5.4747 | 0 | 42.7453 | 0 | 12.6832 | 0 | 13.6367 | 12.8287 | 0 | 0 | 0 | 1.2 | 88.5685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7946.99 | 0 | 7946.99 | 218336 | 0 | 69 | 86 | 218336 | -1000000
8 | 12 | 17 | 6 | 5.6119 | 0 | 42.7453 | 0 | 12.3563 | 0 | 13.2146 | 12.8287 | 0 | 0 | 0 | 4.8 | 91.5567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7942.08 | 0 | 7942.08 | 215353 | 0 | 67 | 81 | 215353 | -1000000
8 | 12 | 18 | 6 | 6.4558 | 0 | 42.7453 | 0 | 7.8262 | 0 | 7.4943 | 8.818 | 0 | 0 | 0 | 7.2 | 80.5396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7938.67 | 0 | 7938.67 | 133420 | 0 | 65 | 78 | 133420 | -1000000
8 | 12 | 19 | 6 | 8.1523 | 0 | 42.7453 | 0 | 7.2829 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 7.2 | 79.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935.9 | 0 | 7935.9 | 133393 | 0 | 65 | 75 | 133393 | -1000000
8 | 12 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.9492 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 79.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.97 | 0 | 7933.97 | 133160 | 0 | 65 | 74 | 133160 | -1000000
8 | 12 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.963 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 7.2 | 79.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.54 | 0 | 7932.54 | 132998 | 0 | 65 | 70 | 132998 | -1000000
8 | 12 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4156 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.54 | 0 | 7931.54 | 132692 | 0 | 67 | 68 | 132692 | -1000000
8 | 12 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.6187 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 5.6 | 78.0601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.74 | 0 | 7930.74 | 132124 | 0 | 66 | 67 | 132124 | -1000000
8 | 12 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.5559 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 73.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.68 | 0 | 3093.68 | 131585 | 0 | 65 | 66 | 131585 | -1000000
8 | 13 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.1016 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 74.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.94 | 0 | 3092.94 | 131067 | 0 | 64 | 67 | 131067 | -1000000
8 | 13 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8375 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 73.7857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.89 | 0 | 3092.89 | 131128 | 0 | 66 | 67 | 131128 | -1000000
8 | 13 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.1248 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 74.0721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.75 | 0 | 3092.75 | 130700 | 0 | 66 | 68 | 130700 | -1000000
8 | 13 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.1511 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 74.0984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.63 | 0 | 3092.63 | 130388 | 0 | 66 | 69 | 130388 | -1000000
8 | 13 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8689 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.49 | 0 | 3092.49 | 130127 | 0 | 66 | 69 | 130127 | -1000000
8 | 13 | 6 | 7 | 4.9014 | 0 | 42.7453 | 0 | 6.7293 | 0 | 6.6577 | 8.818 | 0 | 0 | 0 | 2.4 | 72.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.24 | 0 | 3092.24 | 129791 | 0 | 65 | 68 | 129791 | -1000000
8 | 13 | 7 | 7 | 4.2088 | 0 | 42.7453 | 0 | 6.8035 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 0.8 | 68.8552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092 | 0 | 3092 | 129589 | 0 | 65 | 68 | 129589 | -1000000
8 | 13 | 8 | 7 | 4.6267 | 0 | 42.7453 | 0 | 6.4673 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 0 | 68.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.68 | 0 | 3091.68 | 128933 | 0 | 62 | 67 | 128933 | -1000000
8 | 13 | 9 | 7 | 4.9531 | 0 | 42.7453 | 0 | 6.4607 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 0 | 68.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.41 | 0 | 3091.41 | 129590 | 0 | 65 | 66 | 129590 | -1000000
8 | 13 | 10 | 7 | 4.7358 | 0 | 42.7453 | 0 | 7.0046 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 0 | 68.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.99 | 0 | 3090.99 | 129022 | 0 | 66 | 67 | 129022 | -1000000
8 | 13 | 11 | 7 | 4.5785 | 0 | 42.7453 | 0 | 7.0363 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.6 | 0 | 3090.6 | 128850 | 0 | 66 | 68 | 128850 | -1000000
8 | 13 | 12 | 7 | 4.6375 | 0 | 42.7453 | 0 | 9.9047 | 0 | 5.5353 | 12.8287 | 0 | 0 | 0 | 0 | 75.6514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.07 | 0 | 3090.07 | 188743 | 0 | 66 | 69 | 188743 | -1000000
8 | 13 | 13 | 7 | 4.2519 | 0 | 42.7453 | 0 | 8.4422 | 0 | 7.8173 | 8.818 | 0 | 0 | 0 | 0 | 72.0747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.56 | 0 | 3089.56 | 128520 | 0 | 67 | 72 | 128520 | -1000000
8 | 13 | 14 | 7 | 4.1453 | 0 | 42.7453 | 0 | 12.1292 | 0 | 12.7193 | 12.8287 | 0 | 0 | 0 | 0 | 84.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.82 | 0 | 3088.82 | 194095 | 0 | 68 | 75 | 194095 | -1000000
8 | 13 | 15 | 7 | 4.1479 | 0 | 42.7453 | 0 | 14.6023 | 0 | 18.1617 | 14.8767 | 0 | 0 | 0 | 0 | 94.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.24 | 0 | 3088.24 | 257584 | 0 | 68 | 78 | 257584 | -1000000
8 | 13 | 16 | 7 | 4.1482 | 0 | 42.7453 | 0 | 14.4182 | 0 | 17.7598 | 14.8767 | 0 | 0 | 0 | 1.2 | 95.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.76 | 0 | 3086.76 | 253872 | 0 | 68 | 78 | 253872 | -1000000
8 | 13 | 17 | 7 | 4.1486 | 0 | 42.7453 | 0 | 10.2034 | 0 | 10.255 | 10.866 | 0 | 0 | 0 | 4.8 | 83.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3085.34 | 0 | 3085.34 | 183838 | 0 | 69 | 79 | 183838 | -1000000
8 | 13 | 18 | 7 | 4.1511 | 0 | 42.7453 | 0 | 7.2437 | 0 | 7.1828 | 8.818 | 0 | 0 | 0 | 7.2 | 77.3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3083.78 | 0 | 3083.78 | 128168 | 0 | 68 | 77 | 128168 | -1000000
8 | 13 | 19 | 7 | 5.3261 | 0 | 42.7453 | 0 | 7.0242 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 76.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3082.47 | 0 | 3082.47 | 128197 | 0 | 68 | 75 | 128197 | -1000000
8 | 13 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0755 | 0 | 5.4839 | 8.818 | 0 | 0 | 0 | 7.2 | 76.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.23 | 0 | 3081.23 | 128229 | 0 | 68 | 72 | 128229 | -1000000
8 | 13 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.8946 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 77.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.25 | 0 | 3080.25 | 128142 | 0 | 67 | 72 | 128142 | -1000000
8 | 13 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.5661 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 6.4 | 76.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3079.58 | 0 | 3079.58 | 127836 | 0 | 65 | 71 | 127836 | -1000000
8 | 13 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.5288 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 75.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3079.17 | 0 | 3079.17 | 127870 | 0 | 64 | 70 | 127870 | -1000000
8 | 13 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.3535 | 0 | 5.5018 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.25 | 0 | 7915.25 | 188504 | 0 | 64 | 69 | 188504 | -1000000
8 | 14 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 5.9018 | 0 | 5.4884 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.91 | 0 | 7914.91 | 127959 | 0 | 63 | 66 | 127959 | -1000000
8 | 14 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.6461 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.79 | 0 | 7913.79 | 127890 | 0 | 63 | 66 | 127890 | -1000000
8 | 14 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3425 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.27 | 0 | 7913.27 | 127829 | 0 | 63 | 65 | 127829 | -1000000
8 | 14 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.7799 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8769.5 | 0 | 8769.5 | 131596 | 0 | 63 | 65 | 131596 | -1000000
8 | 14 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.5197 | 0 | 5.6032 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10676.1 | 0 | 10676.1 | 263156 | 0 | 63 | 64 | 263156 | -1000000
8 | 14 | 6 | 1 | 48.3845 | 0 | 140.608 | 0 | 66.7427 | 0 | 6.332 | 23.3522 | 0 | 0 | 0 | 2.4 | 287.819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28639.9 | 0 | 28639.9 | 1253880 | -7408.88 | 63 | 64 | 1253880 | -1007408.88
8 | 14 | 7 | 1 | 39.3372 | 0 | 168.222 | 0 | 69.5578 | 0 | 6.332 | 22.7739 | 0 | 0 | 0 | 0.8 | 307.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31399.6 | 0 | 31399.6 | 1269120 | -28994.9 | 64 | 65 | 1269120 | -1028994.9
8 | 14 | 8 | 1 | 39.6828 | 0 | 173.795 | 0 | 64.1193 | 0 | 6.332 | 22.9615 | 0 | 0 | 0 | 0 | 306.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39717.6 | 0 | 39717.6 | 1194910 | -19920.2 | 64 | 67 | 1194910 | -1019920.2
8 | 14 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 67.3836 | 0 | 6.332 | 23.1014 | 0 | 0 | 0 | 0 | 309.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61831.5 | 0 | 61831.5 | 1251160 | -20231.5 | 65 | 68 | 1251160 | -1020231.5
8 | 14 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 68.5853 | 0 | 6.332 | 22.8993 | 0 | 0 | 0 | 0 | 302.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63215.3 | 0 | 63215.3 | 1267970 | -17597.4 | 65 | 71 | 1267970 | -1017597.4
8 | 14 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 65.9971 | 0 | 6.332 | 23.4967 | 0 | 0 | 0 | 0 | 286.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63216.9 | 0 | 63216.9 | 1202030 | -13425.4 | 66 | 75 | 1202030 | -1013425.4
8 | 14 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 64.5745 | 0 | 6.332 | 23.3237 | 0 | 0 | 0 | 0 | 284.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63218.7 | 0 | 63218.7 | 1227240 | -18111.9 | 66 | 73 | 1227240 | -1018111.9
8 | 14 | 13 | 1 | 41.2683 | 0 | 165.698 | 0 | 67.5082 | 0 | 6.332 | 23.7234 | 0 | 0 | 0 | 0 | 304.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63219.5 | 0 | 63219.5 | 1317670 | -16639.5 | 67 | 70 | 1317670 | -1016639.5
8 | 14 | 14 | 1 | 40.6355 | 0 | 172.702 | 0 | 80.0443 | 0 | 6.332 | 23.4722 | 0 | 0 | 0 | 0 | 323.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61837.7 | 0 | 61837.7 | 1406140 | -19139.3 | 68 | 75 | 1406140 | -1019139.3
8 | 14 | 15 | 1 | 40.5517 | 0 | 173.986 | 0 | 81.1784 | 0 | 6.332 | 23.5821 | 0 | 0 | 0 | 0 | 325.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56310.3 | 0 | 56310.3 | 1432050 | -20557.9 | 67 | 77 | 1432050 | -1020557.9
8 | 14 | 16 | 1 | 40.2928 | 0 | 169.782 | 0 | 83.9786 | 0 | 7.2725 | 23.4734 | 0 | 0 | 0 | 1.2 | 325.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46637.5 | 0 | 46637.5 | 1492680 | -25427 | 68 | 77 | 1492680 | -1025427
8 | 14 | 17 | 1 | 35.4917 | 0 | 152.497 | 0 | 72.891 | 0 | 6.8481 | 23.4319 | 0 | 0 | 0 | 4.8 | 295.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35582.6 | 0 | 35582.6 | 1363070 | -20805.6 | 68 | 77 | 1363070 | -1020805.6
8 | 14 | 18 | 1 | 24.681 | 0 | 93.4203 | 0 | 45.5871 | 0 | 6.332 | 21.9674 | 0 | 0 | 0 | 7.2 | 199.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21764 | 0 | 21764 | 911330 | -11438.4 | 67 | 74 | 911330 | -1011438.4
8 | 14 | 19 | 1 | 20.518 | 0 | 62.7906 | 0 | 8.6253 | 0 | 5.4881 | 8.818 | 0 | 0 | 0 | 7.2 | 113.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15545.7 | 0 | 15545.7 | 189412 | 0 | 66 | 68 | 189412 | -1000000
8 | 14 | 20 | 1 | 18.7228 | 0 | 54.6418 | 0 | 8.4044 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 103.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14855.7 | 0 | 14855.7 | 169418 | 0 | 66 | 67 | 169418 | -1000000
8 | 14 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.4182 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9314.12 | 0 | 9314.12 | 156138 | 0 | 64 | 65 | 156138 | -1000000
8 | 14 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.434 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9090.41 | 0 | 9090.41 | 145286 | 0 | 64 | 65 | 145286 | -1000000
8 | 14 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.1958 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.48 | 0 | 7927.48 | 140311 | 0 | 63 | 65 | 140311 | -1000000
8 | 14 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.533 | 0 | 5.4825 | 8.818 | 0 | 0 | 0 | 4.8 | 78.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.14 | 0 | 7927.14 | 139022 | 0 | 62 | 63 | 139022 | -1000000
8 | 15 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.0054 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.92 | 0 | 7926.92 | 137972 | 0 | 60 | 63 | 137972 | -1000000
8 | 15 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.9811 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.73 | 0 | 7926.73 | 137456 | 0 | 60 | 63 | 137456 | -1000000
8 | 15 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.9515 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.57 | 0 | 7926.57 | 136818 | 0 | 60 | 63 | 136818 | -1000000
8 | 15 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.8043 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8783.2 | 0 | 8783.2 | 140120 | 0 | 60 | 62 | 140120 | -1000000
8 | 15 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 11.8879 | 0 | 5.5661 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10690.1 | 0 | 10690.1 | 253468 | 0 | 60 | 61 | 253468 | -1000000
8 | 15 | 6 | 2 | 46.8584 | 0 | 140.608 | 0 | 45.2312 | 0 | 6.332 | 22.1185 | 0 | 0 | 0 | 2.4 | 263.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28654 | 0 | 28654 | 881897 | -8069.89 | 59 | 61 | 881897 | -1008069.89
8 | 15 | 7 | 2 | 45.4519 | 0 | 168.222 | 0 | 50.5209 | 0 | 6.332 | 21.9611 | 0 | 0 | 0 | 0.8 | 293.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31413.9 | 0 | 31413.9 | 947628 | -26389.9 | 59 | 61 | 947628 | -1026389.9
8 | 15 | 8 | 2 | 40.034 | 0 | 173.795 | 0 | 47.2567 | 0 | 6.332 | 21.9015 | 0 | 0 | 0 | 0 | 289.319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39724.5 | 0 | 39724.5 | 920996 | -25785.6 | 59 | 61 | 920996 | -1025785.6
8 | 15 | 9 | 2 | 41.2635 | 0 | 172.186 | 0 | 48.6519 | 0 | 25.335 | 22.0381 | 0 | 0 | 0 | 0 | 309.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61837.4 | 0 | 61837.4 | 931742 | -26226.9 | 59 | 62 | 931742 | -1026226.9
8 | 15 | 10 | 2 | 41.9192 | 0 | 163.102 | 0 | 50.3575 | 0 | 25.335 | 21.5971 | 0 | 0 | 0 | 0 | 302.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63220.3 | 0 | 63220.3 | 943034 | -23930.3 | 60 | 62 | 943034 | -1023930.3
8 | 15 | 11 | 2 | 40.9872 | 0 | 149.692 | 0 | 44.6351 | 0 | 25.335 | 21.7479 | 0 | 0 | 0 | 0 | 282.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221 | 0 | 63221 | 833065 | -20520.3 | 59 | 62 | 833065 | -1020520.3
8 | 15 | 12 | 2 | 39.8153 | 0 | 150.207 | 0 | 50.4171 | 0 | 25.335 | 22.3719 | 0 | 0 | 0 | 0 | 288.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.5 | 0 | 63221.5 | 899707 | -18190.7 | 61 | 65 | 899707 | -1018190.7
8 | 15 | 13 | 2 | 41.3863 | 0 | 165.698 | 0 | 57.1983 | 0 | 25.335 | 22.4258 | 0 | 0 | 0 | 0 | 312.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.1 | 0 | 63222.1 | 1009710 | -21526.9 | 61 | 67 | 1009710 | -1021526.9
8 | 15 | 14 | 2 | 40.856 | 0 | 172.702 | 0 | 58.5828 | 0 | 25.335 | 22.7296 | 0 | 0 | 0 | 0 | 320.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61840.7 | 0 | 61840.7 | 1045330 | -24343.5 | 61 | 67 | 1045330 | -1024343.5
8 | 15 | 15 | 2 | 40.5508 | 0 | 173.986 | 0 | 67.4779 | 0 | 25.335 | 23.1059 | 0 | 0 | 0 | 0 | 330.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56313.7 | 0 | 56313.7 | 1158610 | -24723.2 | 62 | 70 | 1158610 | -1024723.2
8 | 15 | 16 | 2 | 40.293 | 0 | 169.782 | 0 | 68.6691 | 0 | 25.335 | 23.3523 | 0 | 0 | 0 | 1.2 | 328.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46640.4 | 0 | 46640.4 | 1201110 | -23514.7 | 63 | 71 | 1201110 | -1023514.7
8 | 15 | 17 | 2 | 35.4834 | 0 | 152.497 | 0 | 61.7214 | 0 | 25.335 | 22.9512 | 0 | 0 | 0 | 4.8 | 302.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35585.1 | 0 | 35585.1 | 1099120 | -19539.8 | 63 | 71 | 1099120 | -1019539.8
8 | 15 | 18 | 2 | 24.6035 | 0 | 93.4203 | 0 | 39.8442 | 0 | 25.335 | 20.6442 | 0 | 0 | 0 | 7.2 | 211.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21766.2 | 0 | 21766.2 | 732906 | -14573.8 | 62 | 70 | 732906 | -1014573.8
8 | 15 | 19 | 2 | 19.6408 | 0 | 62.7906 | 0 | 9.5563 | 0 | 8.7325 | 8.818 | 0 | 0 | 0 | 7.2 | 116.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15548.1 | 0 | 15548.1 | 192383 | 0 | 61 | 66 | 192383 | -1000000
8 | 15 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 7.8339 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 102.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14859.2 | 0 | 14859.2 | 172346 | 0 | 60 | 63 | 172346 | -1000000
8 | 15 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.0931 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 7.2 | 91.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9318.47 | 0 | 9318.47 | 158963 | 0 | 59 | 60 | 158963 | -1000000
8 | 15 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.3585 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.48 | 0 | 9095.48 | 147970 | 0 | 59 | 59 | 147970 | -1000000
8 | 15 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1224 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.97 | 0 | 7932.97 | 142901 | 0 | 58 | 58 | 142901 | -1000000
8 | 15 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.0386 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.14 | 0 | 7933.14 | 141121 | 0 | 56 | 56 | 141121 | -1000000
8 | 16 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9948 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.03 | 0 | 7933.03 | 140178 | 0 | 55 | 55 | 140178 | -1000000
8 | 16 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9624 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.08 | 0 | 7933.08 | 139471 | 0 | 56 | 56 | 139471 | -1000000
8 | 16 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9304 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.09 | 0 | 7933.09 | 138771 | 0 | 57 | 57 | 138771 | -1000000
8 | 16 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.0699 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8789.85 | 0 | 8789.85 | 141889 | 0 | 58 | 58 | 141889 | -1000000
8 | 16 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 12.4248 | 0 | 5.5859 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10696.7 | 0 | 10696.7 | 261077 | 0 | 57 | 57 | 261077 | -1000000
8 | 16 | 6 | 3 | 46.934 | 0 | 140.608 | 0 | 37.0496 | 0 | 6.332 | 20.6046 | 0 | 0 | 0 | 2.4 | 253.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28660.6 | 0 | 28660.6 | 692223 | -10262 | 56 | 56 | 692223 | -1010262
8 | 16 | 7 | 3 | 43.3265 | 0 | 168.222 | 0 | 43.0038 | 0 | 6.332 | 20.4108 | 0 | 0 | 0 | 0.8 | 282.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31420.3 | 0 | 31420.3 | 785824 | -28493.6 | 57 | 57 | 785824 | -1028493.6
8 | 16 | 8 | 3 | 39.9527 | 0 | 173.795 | 0 | 42.7757 | 0 | 25.335 | 20.7572 | 0 | 0 | 0 | 0 | 302.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39728.5 | 0 | 39728.5 | 821755 | -28235.7 | 58 | 58 | 821755 | -1028235.7
8 | 16 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 54.5386 | 0 | 25.335 | 21.4609 | 0 | 0 | 0 | 0 | 314.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61840.8 | 0 | 61840.8 | 973032 | -25568.2 | 61 | 64 | 973032 | -1025568.2
8 | 16 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 60.4715 | 0 | 25.335 | 21.6098 | 0 | 0 | 0 | 0 | 311.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.6 | 0 | 63223.6 | 1067320 | -20892.3 | 63 | 68 | 1067320 | -1020892.3
8 | 16 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 55.5798 | 0 | 25.335 | 22.3949 | 0 | 0 | 0 | 0 | 293.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225 | 0 | 63225 | 959131 | -16473.9 | 62 | 71 | 959131 | -1016473.9
8 | 16 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 55.7312 | 0 | 25.335 | 22.6742 | 0 | 0 | 0 | 0 | 293.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.8 | 0 | 63225.8 | 929188 | -16482.3 | 59 | 75 | 929188 | -1016482.3
8 | 16 | 13 | 3 | 41.2566 | 0 | 165.698 | 0 | 63.5753 | 0 | 25.335 | 23.0839 | 0 | 0 | 0 | 0 | 318.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226.1 | 0 | 63226.1 | 1080010 | -17243.2 | 60 | 77 | 1080010 | -1017243.2
8 | 16 | 14 | 3 | 40.6613 | 0 | 172.702 | 0 | 70.9829 | 0 | 25.335 | 22.7632 | 0 | 0 | 0 | 0 | 332.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61844.4 | 0 | 61844.4 | 1198820 | -20785.3 | 62 | 77 | 1198820 | -1020785.3
8 | 16 | 15 | 3 | 40.568 | 0 | 173.986 | 0 | 71.4399 | 0 | 25.335 | 22.8803 | 0 | 0 | 0 | 0 | 334.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56317.7 | 0 | 56317.7 | 1207980 | -22162.9 | 62 | 78 | 1207980 | -1022162.9
8 | 16 | 16 | 3 | 40.3031 | 0 | 169.782 | 0 | 69.9992 | 0 | 25.335 | 23.0889 | 0 | 0 | 0 | 1.2 | 329.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46644.6 | 0 | 46644.6 | 1200110 | -21249.1 | 62 | 78 | 1200110 | -1021249.1
8 | 16 | 17 | 3 | 35.4904 | 0 | 152.497 | 0 | 64.1917 | 0 | 25.335 | 23.1155 | 0 | 0 | 0 | 4.8 | 305.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588.9 | 0 | 35588.9 | 1114010 | -17151.4 | 62 | 78 | 1114010 | -1017151.4
8 | 16 | 18 | 3 | 24.6068 | 0 | 93.4203 | 0 | 44.6717 | 0 | 25.335 | 21.0803 | 0 | 0 | 0 | 7.2 | 216.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.9 | 0 | 21769.9 | 788175 | -15767.9 | 62 | 76 | 788175 | -1015767.9
8 | 16 | 19 | 3 | 19.5442 | 0 | 62.7906 | 0 | 10.2919 | 0 | 9.6489 | 8.818 | 0 | 0 | 0 | 7.2 | 118.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15551.4 | 0 | 15551.4 | 194088 | 0 | 61 | 71 | 194088 | -1000000
8 | 16 | 20 | 3 | 18.7076 | 0 | 54.6418 | 0 | 8.1463 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 7.2 | 102.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14861.5 | 0 | 14861.5 | 174230 | 0 | 62 | 68 | 174230 | -1000000
8 | 16 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 6.446 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 7.2 | 90.6679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.59 | 0 | 9320.59 | 160143 | 0 | 58 | 62 | 160143 | -1000000
8 | 16 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 6.9055 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.09 | 0 | 9097.09 | 149286 | 0 | 58 | 60 | 149286 | -1000000
8 | 16 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.1793 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.05 | 0 | 7934.05 | 144146 | 0 | 57 | 58 | 144146 | -1000000
8 | 16 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.1002 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.73 | 0 | 7933.73 | 142471 | 0 | 56 | 57 | 142471 | -1000000
8 | 17 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0495 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.4 | 0 | 7933.4 | 141370 | 0 | 55 | 56 | 141370 | -1000000
8 | 17 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0107 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.2 | 0 | 7933.2 | 140527 | 0 | 55 | 55 | 140527 | -1000000
8 | 17 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9695 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.97 | 0 | 7932.97 | 139623 | 0 | 55 | 55 | 139623 | -1000000
8 | 17 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0878 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8789.54 | 0 | 8789.54 | 142273 | 0 | 53 | 53 | 142273 | -1000000
8 | 17 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.4252 | 0 | 5.586 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10696.4 | 0 | 10696.4 | 261079 | 0 | 53 | 53 | 261079 | -1000000
8 | 17 | 6 | 4 | 45.7263 | 0 | 140.608 | 0 | 33.1259 | 0 | 6.332 | 20.3118 | 0 | 0 | 0 | 2.4 | 248.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28660.3 | 0 | 28660.3 | 623343 | -10712.7 | 53 | 53 | 623343 | -1010712.7
8 | 17 | 7 | 4 | 39.1472 | 0 | 168.222 | 0 | 40.5434 | 0 | 6.332 | 20.144 | 0 | 0 | 0 | 0.8 | 275.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31420.2 | 0 | 31420.2 | 745925 | -29143.4 | 55 | 56 | 745925 | -1029143.4
8 | 17 | 8 | 4 | 39.6884 | 0 | 173.795 | 0 | 46.5933 | 0 | 25.335 | 20.6789 | 0 | 0 | 0 | 0 | 306.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39729.4 | 0 | 39729.4 | 860544 | -27447.2 | 58 | 62 | 860544 | -1027447.2
8 | 17 | 9 | 4 | 40.6158 | 0 | 172.186 | 0 | 60.9021 | 0 | 25.335 | 21.0264 | 0 | 0 | 0 | 0 | 320.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.9 | 0 | 61841.9 | 1042540 | -24470.1 | 62 | 68 | 1042540 | -1024470.1
8 | 17 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 67.6689 | 0 | 25.335 | 21.5985 | 0 | 0 | 0 | 0 | 318.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.6 | 0 | 63225.6 | 1146320 | -20278.6 | 64 | 73 | 1146320 | -1020278.6
8 | 17 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 65.7999 | 0 | 25.335 | 22.5776 | 0 | 0 | 0 | 0 | 304.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63227.4 | 0 | 63227.4 | 1113790 | -14404.8 | 65 | 79 | 1113790 | -1014404.8
8 | 17 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 66.8743 | 0 | 25.335 | 22.0166 | 0 | 0 | 0 | 0 | 304.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.1 | 0 | 63228.1 | 1131870 | -28526.2 | 63 | 78 | 1131870 | -1028526.2
8 | 17 | 13 | 4 | 41.2383 | 0 | 165.698 | 0 | 70.9289 | 0 | 25.335 | 23.2272 | 0 | 0 | 0 | 0 | 326.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.1 | 0 | 63228.1 | 1198850 | -15183.1 | 63 | 81 | 1198850 | -1015183.1
8 | 17 | 14 | 4 | 40.6194 | 0 | 172.702 | 0 | 72.3046 | 0 | 25.335 | 22.9779 | 0 | 0 | 0 | 0 | 333.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61846.6 | 0 | 61846.6 | 1216800 | -19287.8 | 62 | 83 | 1216800 | -1019287.8
8 | 17 | 15 | 4 | 40.5368 | 0 | 173.986 | 0 | 69.85 | 0 | 25.335 | 23.1019 | 0 | 0 | 0 | 0 | 332.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56319.1 | 0 | 56319.1 | 1177750 | -21674.4 | 60 | 79 | 1177750 | -1021674.4
8 | 17 | 16 | 4 | 40.2909 | 0 | 169.782 | 0 | 71.0304 | 0 | 25.335 | 23.2525 | 0 | 0 | 0 | 1.2 | 330.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46645.7 | 0 | 46645.7 | 1217950 | -20622.5 | 61 | 81 | 1217950 | -1020622.5
8 | 17 | 17 | 4 | 35.4804 | 0 | 152.497 | 0 | 63.773 | 0 | 25.335 | 23.1472 | 0 | 0 | 0 | 4.8 | 305.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35590.1 | 0 | 35590.1 | 1108230 | -17327.3 | 61 | 79 | 1108230 | -1017327.3
8 | 17 | 18 | 4 | 24.6075 | 0 | 93.4203 | 0 | 45.7488 | 0 | 25.335 | 21.3953 | 0 | 0 | 0 | 7.2 | 217.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21771.3 | 0 | 21771.3 | 798737 | -14364 | 62 | 77 | 798737 | -1014364
8 | 17 | 19 | 4 | 19.6133 | 0 | 62.7906 | 0 | 11.0799 | 0 | 10.8485 | 8.818 | 0 | 0 | 0 | 7.2 | 120.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15552.6 | 0 | 15552.6 | 194816 | 0 | 61 | 73 | 194816 | -1000000
8 | 17 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.3533 | 0 | 7.7576 | 8.818 | 0 | 0 | 0 | 7.2 | 105.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14862.3 | 0 | 14862.3 | 174567 | 0 | 60 | 69 | 174567 | -1000000
8 | 17 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.1231 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 7.2 | 91.3443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9321.39 | 0 | 9321.39 | 161075 | 0 | 59 | 65 | 161075 | -1000000
8 | 17 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.05 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.67 | 0 | 9097.67 | 149993 | 0 | 59 | 63 | 149993 | -1000000
8 | 17 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.4425 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 5.6 | 79.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.73 | 0 | 7934.73 | 144860 | 0 | 58 | 60 | 144860 | -1000000
8 | 17 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.1341 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.48 | 0 | 7934.48 | 143215 | 0 | 58 | 59 | 143215 | -1000000
8 | 18 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0793 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.46 | 0 | 7934.46 | 142022 | 0 | 57 | 58 | 142022 | -1000000
8 | 18 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0319 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.66 | 0 | 7934.66 | 140986 | 0 | 56 | 57 | 140986 | -1000000
8 | 18 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9993 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.93 | 0 | 7934.93 | 140279 | 0 | 57 | 58 | 140279 | -1000000
8 | 18 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.1223 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8791.96 | 0 | 8791.96 | 143030 | 0 | 56 | 57 | 143030 | -1000000
8 | 18 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.5763 | 0 | 5.5517 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10699.3 | 0 | 10699.3 | 242157 | 0 | 55 | 56 | 242157 | -1000000
8 | 18 | 6 | 5 | 45.4557 | 0 | 140.608 | 0 | 34.3172 | 0 | 6.332 | 20.2016 | 0 | 0 | 0 | 2.4 | 249.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28663.7 | 0 | 28663.7 | 652754 | -9946.54 | 55 | 57 | 652754 | -1009946.54
8 | 18 | 7 | 5 | 39.1856 | 0 | 168.222 | 0 | 44.3303 | 0 | 25.335 | 20.5982 | 0 | 0 | 0 | 0.8 | 298.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31423.9 | 0 | 31423.9 | 797945 | -29504.4 | 57 | 61 | 797945 | -1029504.4
8 | 18 | 8 | 5 | 39.7233 | 0 | 173.795 | 0 | 51.119 | 0 | 25.335 | 20.7297 | 0 | 0 | 0 | 0 | 310.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39731 | 0 | 39731 | 908964 | -27314.6 | 59 | 65 | 908964 | -1027314.6
8 | 18 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 62.2606 | 0 | 25.335 | 21.2446 | 0 | 0 | 0 | 0 | 321.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61842.6 | 0 | 61842.6 | 1027670 | -25172 | 61 | 72 | 1027670 | -1025172
8 | 18 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 63.5363 | 0 | 25.335 | 21.7569 | 0 | 0 | 0 | 0 | 314.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63227 | 0 | 63227 | 1068640 | -20908.4 | 61 | 75 | 1068640 | -1020908.4
8 | 18 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 62.0485 | 0 | 25.335 | 22.5164 | 0 | 0 | 0 | 0 | 300.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63228.5 | 0 | 63228.5 | 1056890 | -15668.2 | 63 | 77 | 1056890 | -1015668.2
8 | 18 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 67.2759 | 0 | 25.335 | 21.944 | 0 | 0 | 0 | 0 | 304.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63229.1 | 0 | 63229.1 | 1137800 | -30673.9 | 63 | 80 | 1137800 | -1030673.9
8 | 18 | 13 | 5 | 41.2626 | 0 | 165.698 | 0 | 73.1201 | 0 | 25.335 | 23.1099 | 0 | 0 | 0 | 0 | 328.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63229 | 0 | 63229 | 1229420 | -16457.7 | 63 | 82 | 1229420 | -1016457.7
8 | 18 | 14 | 5 | 40.6556 | 0 | 172.702 | 0 | 76.302 | 0 | 25.335 | 22.8493 | 0 | 0 | 0 | 0 | 337.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61847.4 | 0 | 61847.4 | 1280060 | -20776.5 | 63 | 83 | 1280060 | -1020776.5
8 | 18 | 15 | 5 | 40.5591 | 0 | 173.986 | 0 | 79.0293 | 0 | 25.335 | 22.979 | 0 | 0 | 0 | 0 | 341.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56320.3 | 0 | 56320.3 | 1325770 | -22544.3 | 63 | 83 | 1325770 | -1022544.3
8 | 18 | 16 | 5 | 40.306 | 0 | 169.782 | 0 | 74.8541 | 0 | 25.335 | 23.1878 | 0 | 0 | 0 | 1.2 | 334.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46646.9 | 0 | 46646.9 | 1273710 | -22086.4 | 62 | 83 | 1273710 | -1022086.4
8 | 18 | 17 | 5 | 35.4847 | 0 | 152.497 | 0 | 68.2788 | 0 | 25.335 | 22.7251 | 0 | 0 | 0 | 4.8 | 309.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35591.5 | 0 | 35591.5 | 1182500 | -25138.1 | 62 | 81 | 1182500 | -1025138.1
8 | 18 | 18 | 5 | 24.607 | 0 | 93.4203 | 0 | 46.3029 | 0 | 25.335 | 21.2588 | 0 | 0 | 0 | 7.2 | 218.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21772.4 | 0 | 21772.4 | 808456 | -22859.1 | 61 | 79 | 808456 | -1022859.1
8 | 18 | 19 | 5 | 20.4508 | 0 | 62.7906 | 0 | 11.8489 | 0 | 12.268 | 8.818 | 0 | 0 | 0 | 7.2 | 123.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15553.7 | 0 | 15553.7 | 195138 | 0 | 60 | 75 | 195138 | -1000000
8 | 18 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 7.8636 | 0 | 7.3375 | 8.818 | 0 | 0 | 0 | 7.2 | 104.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14863 | 0 | 14863 | 174915 | 0 | 59 | 69 | 174915 | -1000000
8 | 18 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.4481 | 0 | 5.7282 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9322.18 | 0 | 9322.18 | 161500 | 0 | 59 | 66 | 161500 | -1000000
8 | 18 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.1051 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.21 | 0 | 9098.21 | 150343 | 0 | 59 | 64 | 150343 | -1000000
8 | 18 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.0868 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935.31 | 0 | 7935.31 | 145272 | 0 | 59 | 63 | 145272 | -1000000
8 | 18 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.6644 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935 | 0 | 7935 | 143391 | 0 | 59 | 61 | 143391 | -1000000
8 | 19 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.1199 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.87 | 0 | 7934.87 | 142091 | 0 | 58 | 61 | 142091 | -1000000
8 | 19 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.6797 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 75.9035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935.5 | 0 | 7935.5 | 141270 | 0 | 59 | 63 | 141270 | -1000000
8 | 19 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.72 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 4.8 | 75.9442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935.85 | 0 | 7935.85 | 140315 | 0 | 59 | 65 | 140315 | -1000000
8 | 19 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.1562 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 75.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.19 | 0 | 7936.19 | 139535 | 0 | 59 | 65 | 139535 | -1000000
8 | 19 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.5233 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 4.8 | 74.7509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.41 | 0 | 7936.41 | 138822 | 0 | 59 | 63 | 138822 | -1000000
8 | 19 | 6 | 6 | 5.8635 | 0 | 42.7453 | 0 | 7.568 | 0 | 6.9059 | 8.818 | 0 | 0 | 0 | 2.4 | 74.3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.51 | 0 | 7936.51 | 138021 | 0 | 59 | 63 | 138021 | -1000000
8 | 19 | 7 | 6 | 4.6639 | 0 | 42.7453 | 0 | 26.5241 | 0 | 6.332 | 18.9528 | 0 | 0 | 0 | 0.8 | 100.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.55 | 0 | 7936.55 | 389753 | -9033.67 | 60 | 66 | 389753 | -1009033.67
8 | 19 | 8 | 6 | 5.0036 | 0 | 42.7453 | 0 | 22.5675 | 0 | 25.335 | 19.0079 | 0 | 0 | 0 | 0 | 114.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7936.63 | 0 | 7936.63 | 387916 | -7572.48 | 61 | 69 | 387916 | -1007572.48
8 | 19 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 28.1679 | 0 | 25.335 | 19.1211 | 0 | 0 | 0 | 0 | 120.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7950.84 | 0 | 7950.84 | 467786 | -11634.4 | 64 | 73 | 467786 | -1011634.4
8 | 19 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 29.6549 | 0 | 25.335 | 19.198 | 0 | 0 | 0 | 0 | 122.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7952.53 | 0 | 7952.53 | 500930 | -12577.3 | 65 | 76 | 500930 | -1012577.3
8 | 19 | 11 | 6 | 5.5769 | 0 | 42.7453 | 0 | 31.7721 | 0 | 25.335 | 19.2225 | 0 | 0 | 0 | 0 | 124.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.31 | 0 | 7954.31 | 548175 | -12853.8 | 67 | 78 | 548175 | -1012853.8
8 | 19 | 12 | 6 | 5.6627 | 0 | 42.7453 | 0 | 32.6445 | 0 | 25.335 | 19.3043 | 0 | 0 | 0 | 0 | 125.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.75 | 0 | 7954.75 | 558326 | -12959.6 | 67 | 78 | 558326 | -1012959.6
8 | 19 | 13 | 6 | 5.6523 | 0 | 42.7453 | 0 | 33.98 | 0 | 25.335 | 19.3598 | 0 | 0 | 0 | 0 | 127.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7955.42 | 0 | 7955.42 | 585837 | -13154.5 | 68 | 79 | 585837 | -1013154.5
8 | 19 | 14 | 6 | 5.6714 | 0 | 42.7453 | 0 | 8.6998 | 0 | 7.9761 | 8.818 | 0 | 0 | 0 | 0 | 73.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7956 | 0 | 7956 | 134108 | 0 | 68 | 77 | 134108 | -1000000
8 | 19 | 15 | 6 | 6.2625 | 0 | 42.7453 | 0 | 6.1241 | 0 | 6.1925 | 8.818 | 0 | 0 | 0 | 0 | 70.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7956.54 | 0 | 7956.54 | 133796 | 0 | 68 | 69 | 133796 | -1000000
8 | 19 | 16 | 6 | 6.5371 | 0 | 42.7453 | 0 | 8.2401 | 0 | 7.444 | 8.818 | 0 | 0 | 0 | 1.2 | 74.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7949.69 | 0 | 7949.69 | 133596 | 0 | 69 | 70 | 133596 | -1000000
8 | 19 | 17 | 6 | 6.9334 | 0 | 42.7453 | 0 | 7.8365 | 0 | 7.1908 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7946.22 | 0 | 7946.22 | 133303 | 0 | 69 | 70 | 133303 | -1000000
8 | 19 | 18 | 6 | 7.7281 | 0 | 42.7453 | 0 | 7.7012 | 0 | 7.1473 | 8.818 | 0 | 0 | 0 | 7.2 | 81.3399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7944.41 | 0 | 7944.41 | 132978 | 0 | 69 | 70 | 132978 | -1000000
8 | 19 | 19 | 6 | 8.0731 | 0 | 42.7453 | 0 | 7.3457 | 0 | 6.8877 | 8.818 | 0 | 0 | 0 | 7.2 | 81.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.08 | 0 | 7943.08 | 132664 | 0 | 69 | 69 | 132664 | -1000000
8 | 19 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.2865 | 0 | 6.1973 | 8.818 | 0 | 0 | 0 | 7.2 | 81.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7942.18 | 0 | 7942.18 | 132320 | 0 | 69 | 70 | 132320 | -1000000
8 | 19 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.6851 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 7.2 | 79.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7941.44 | 0 | 7941.44 | 131911 | 0 | 68 | 69 | 131911 | -1000000
8 | 19 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.9449 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 79.1844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7940.9 | 0 | 7940.9 | 131710 | 0 | 69 | 69 | 131710 | -1000000
8 | 19 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.9269 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 5.6 | 78.3664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7940.37 | 0 | 7940.37 | 131332 | 0 | 68 | 69 | 131332 | -1000000
8 | 19 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.9092 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.45 | 0 | 3103.45 | 130963 | 0 | 68 | 69 | 130963 | -1000000
8 | 20 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8954 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.01 | 0 | 3103.01 | 130678 | 0 | 68 | 69 | 130678 | -1000000
8 | 20 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8828 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.72 | 0 | 3102.72 | 130417 | 0 | 68 | 69 | 130417 | -1000000
8 | 20 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8661 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.33 | 0 | 3102.33 | 130066 | 0 | 67 | 69 | 130066 | -1000000
8 | 20 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2396 | 0 | 5.4839 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.07 | 0 | 3102.07 | 129757 | 0 | 66 | 67 | 129757 | -1000000
8 | 20 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.7618 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 73.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.79 | 0 | 3101.79 | 129530 | 0 | 66 | 67 | 129530 | -1000000
8 | 20 | 6 | 7 | 4.9667 | 0 | 42.7453 | 0 | 6.7518 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 2.4 | 71.1617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.54 | 0 | 3101.54 | 129318 | 0 | 66 | 67 | 129318 | -1000000
8 | 20 | 7 | 7 | 3.6996 | 0 | 42.7453 | 0 | 7.0437 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0.8 | 68.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.42 | 0 | 3101.42 | 129002 | 0 | 65 | 68 | 129002 | -1000000
8 | 20 | 8 | 7 | 3.7965 | 0 | 42.7453 | 0 | 7.7082 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 0 | 68.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.27 | 0 | 3101.27 | 128886 | 0 | 66 | 71 | 128886 | -1000000
8 | 20 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.6583 | 0 | 5.5116 | 12.8287 | 0 | 0 | 0 | 0 | 74.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.11 | 0 | 3101.11 | 186840 | 0 | 67 | 71 | 186840 | -1000000
8 | 20 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.6404 | 0 | 5.5464 | 12.8287 | 0 | 0 | 0 | 0 | 75.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.65 | 0 | 3099.65 | 192346 | 0 | 67 | 73 | 192346 | -1000000
8 | 20 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.1114 | 0 | 5.5707 | 12.8287 | 0 | 0 | 0 | 0 | 76.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3097.82 | 0 | 3097.82 | 199209 | 0 | 68 | 76 | 199209 | -1000000
8 | 20 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.8126 | 0 | 5.5578 | 12.8287 | 0 | 0 | 0 | 0 | 76.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3095.88 | 0 | 3095.88 | 204408 | 0 | 68 | 78 | 204408 | -1000000
8 | 20 | 13 | 7 | 4.1468 | 0 | 42.7453 | 0 | 11.426 | 0 | 12.106 | 12.8287 | 0 | 0 | 0 | 0 | 83.2527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.97 | 0 | 3093.97 | 207433 | 0 | 68 | 78 | 207433 | -1000000
8 | 20 | 14 | 7 | 4.1472 | 0 | 42.7453 | 0 | 12.3274 | 0 | 12.9323 | 12.8287 | 0 | 0 | 0 | 0 | 84.9809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092 | 0 | 3092 | 211171 | 0 | 68 | 79 | 211171 | -1000000
8 | 20 | 15 | 7 | 4.1482 | 0 | 42.7453 | 0 | 12.0539 | 0 | 12.4684 | 12.8287 | 0 | 0 | 0 | 0 | 84.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.3 | 0 | 3090.3 | 206386 | 0 | 66 | 80 | 206386 | -1000000
8 | 20 | 16 | 7 | 4.1482 | 0 | 42.7453 | 0 | 15.6247 | 0 | 20.6104 | 14.8767 | 0 | 0 | 0 | 1.2 | 99.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.61 | 0 | 3088.61 | 272610 | 0 | 67 | 80 | 272610 | -1000000
8 | 20 | 17 | 7 | 4.1495 | 0 | 42.7453 | 0 | 14.945 | 0 | 18.9929 | 14.8767 | 0 | 0 | 0 | 4.8 | 100.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3086.85 | 0 | 3086.85 | 261841 | 0 | 66 | 79 | 261841 | -1000000
8 | 20 | 18 | 7 | 4.1521 | 0 | 42.7453 | 0 | 7.3229 | 0 | 7.2317 | 8.818 | 0 | 0 | 0 | 7.2 | 77.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3085.34 | 0 | 3085.34 | 127982 | 0 | 65 | 77 | 127982 | -1000000
8 | 20 | 19 | 7 | 5.6837 | 0 | 42.7453 | 0 | 6.3835 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 7.2 | 76.3114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3083.82 | 0 | 3083.82 | 128135 | 0 | 65 | 73 | 128135 | -1000000
8 | 20 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.6884 | 0 | 5.4901 | 8.818 | 0 | 0 | 0 | 7.2 | 76.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3082.75 | 0 | 3082.75 | 128005 | 0 | 64 | 69 | 128005 | -1000000
8 | 20 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.8484 | 0 | 5.4892 | 8.818 | 0 | 0 | 0 | 7.2 | 76.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.79 | 0 | 3081.79 | 127832 | 0 | 63 | 66 | 127832 | -1000000
8 | 20 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3398 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 6.4 | 76.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.24 | 0 | 3081.24 | 127771 | 0 | 63 | 65 | 127771 | -1000000
8 | 20 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.9967 | 0 | 5.4885 | 8.818 | 0 | 0 | 0 | 5.6 | 75.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.95 | 0 | 3080.95 | 127487 | 0 | 62 | 63 | 127487 | -1000000
8 | 20 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.2289 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7917.27 | 0 | 7917.27 | 127609 | 0 | 61 | 62 | 127609 | -1000000
8 | 21 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.1897 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7916.88 | 0 | 7916.88 | 127473 | 0 | 60 | 61 | 127473 | -1000000
8 | 21 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.1535 | 0 | 5.4877 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.85 | 0 | 7915.85 | 127392 | 0 | 60 | 60 | 127392 | -1000000
8 | 21 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.6928 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 78.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.65 | 0 | 7915.65 | 127196 | 0 | 60 | 61 | 127196 | -1000000
8 | 21 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.1089 | 0 | 5.4901 | 12.8287 | 0 | 0 | 0 | 4.8 | 88.8722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8772.28 | 0 | 8772.28 | 186410 | 0 | 60 | 61 | 186410 | -1000000
8 | 21 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.691 | 0 | 5.6014 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10678.8 | 0 | 10678.8 | 264770 | 0 | 60 | 61 | 264770 | -1000000
8 | 21 | 6 | 1 | 47.123 | 0 | 140.608 | 0 | 63.1981 | 0 | 6.332 | 22.1443 | 0 | 0 | 0 | 2.4 | 281.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28642.5 | 0 | 28642.5 | 1123870 | -9320.47 | 61 | 62 | 1123870 | -1009320.47
8 | 21 | 7 | 1 | 39.5018 | 0 | 168.222 | 0 | 61.4856 | 0 | 6.332 | 21.739 | 0 | 0 | 0 | 0.8 | 298.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31402.1 | 0 | 31402.1 | 1105080 | -29575.2 | 61 | 62 | 1105080 | -1029575.2
8 | 21 | 8 | 1 | 39.685 | 0 | 173.795 | 0 | 55.989 | 0 | 6.332 | 22.3936 | 0 | 0 | 0 | 0 | 298.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39719.4 | 0 | 39719.4 | 1047460 | -21869.5 | 61 | 64 | 1047460 | -1021869.5
8 | 21 | 9 | 1 | 40.6158 | 0 | 172.186 | 0 | 66.9915 | 0 | 6.332 | 22.4119 | 0 | 0 | 0 | 0 | 308.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61833.2 | 0 | 61833.2 | 1177120 | -17966.3 | 64 | 70 | 1177120 | -1017966.3
8 | 21 | 10 | 1 | 41.1517 | 0 | 163.102 | 0 | 70.5455 | 0 | 6.3907 | 22.7026 | 0 | 0 | 0 | 0 | 303.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63216.1 | 0 | 63216.1 | 1253100 | -17008.8 | 65 | 73 | 1253100 | -1017008.8
8 | 21 | 11 | 1 | 40.7055 | 0 | 149.692 | 0 | 67.9566 | 0 | 7.8011 | 23.5137 | 0 | 0 | 0 | 0 | 289.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63218.8 | 0 | 63218.8 | 1233370 | -11094.9 | 68 | 76 | 1233370 | -1011094.9
8 | 21 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 74.7447 | 0 | 25.335 | 23.0445 | 0 | 0 | 0 | 0 | 313.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63220.3 | 0 | 63220.3 | 1338640 | -19394 | 69 | 80 | 1338640 | -1019394
8 | 21 | 13 | 1 | 41.2782 | 0 | 165.698 | 0 | 83.1211 | 0 | 25.335 | 24.1018 | 0 | 0 | 0 | 0 | 339.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63220.5 | 0 | 63220.5 | 1475320 | -11710.5 | 70 | 83 | 1475320 | -1011710.5
8 | 21 | 14 | 1 | 40.6367 | 0 | 172.702 | 0 | 92.3601 | 0 | 25.335 | 23.8272 | 0 | 0 | 0 | 0 | 354.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61839.1 | 0 | 61839.1 | 1599490 | -16271.8 | 71 | 86 | 1599490 | -1016271.8
8 | 21 | 15 | 1 | 40.5536 | 0 | 173.986 | 0 | 96.2814 | 0 | 25.335 | 23.5616 | 0 | 0 | 0 | 0 | 359.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56312.1 | 0 | 56312.1 | 1629710 | -25329.2 | 70 | 86 | 1629710 | -1025329.2
8 | 21 | 16 | 1 | 40.3022 | 0 | 169.782 | 0 | 109.687 | 0 | 6.332 | 23.2765 | 0 | 0 | 0 | 1.2 | 350.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46639.5 | 0 | 46639.5 | 1733310 | -33244.5 | 72 | 89 | 1733310 | -1033244.5
8 | 21 | 17 | 1 | 35.4879 | 0 | 152.497 | 0 | 103.206 | 0 | 6.332 | 23.0436 | 0 | 0 | 0 | 4.8 | 325.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35584.6 | 0 | 35584.6 | 1639550 | -31251.7 | 72 | 87 | 1639550 | -1031251.7
8 | 21 | 18 | 1 | 24.6584 | 0 | 93.4203 | 0 | 76.3939 | 0 | 6.332 | 21.4568 | 0 | 0 | 0 | 7.2 | 229.461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21765.9 | 0 | 21765.9 | 1180820 | -37116.3 | 71 | 84 | 1180820 | -1037116.3
8 | 21 | 19 | 1 | 21.8044 | 0 | 62.7906 | 0 | 10.9397 | 0 | 5.5632 | 8.818 | 0 | 0 | 0 | 7.2 | 117.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15547.7 | 0 | 15547.7 | 190367 | 0 | 71 | 81 | 190367 | -1000000
8 | 21 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 9.0961 | 0 | 5.5028 | 8.818 | 0 | 0 | 0 | 7.2 | 103.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14857.2 | 0 | 14857.2 | 169476 | 0 | 67 | 80 | 169476 | -1000000
8 | 21 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 8.4817 | 0 | 5.4908 | 8.818 | 0 | 0 | 0 | 7.2 | 92.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9314.51 | 0 | 9314.51 | 157274 | 0 | 70 | 78 | 157274 | -1000000
8 | 21 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.942 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 6.4 | 84.1742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9089.47 | 0 | 9089.47 | 146455 | 0 | 71 | 77 | 146455 | -1000000
8 | 21 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.6984 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 5.6 | 80.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.5 | 0 | 7925.5 | 141660 | 0 | 72 | 77 | 141660 | -1000000
8 | 21 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.6292 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.06 | 0 | 7924.06 | 140328 | 0 | 72 | 76 | 140328 | -1000000
8 | 22 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6171 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7922.91 | 0 | 7922.91 | 139291 | 0 | 69 | 72 | 139291 | -1000000
8 | 22 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 5.2488 | 0 | 5.5001 | 8.818 | 0 | 0 | 0 | 4.8 | 77.1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.83 | 0 | 7921.83 | 138198 | 0 | 64 | 65 | 138198 | -1000000
8 | 22 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.3735 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.84 | 0 | 7920.84 | 137676 | 0 | 65 | 66 | 137676 | -1000000
8 | 22 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.9608 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 82.7027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8776.82 | 0 | 8776.82 | 141058 | 0 | 65 | 65 | 141058 | -1000000
8 | 22 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.7121 | 0 | 5.6726 | 12.8287 | 0 | 0 | 0 | 4.8 | 131.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10683.4 | 0 | 10683.4 | 281637 | 0 | 64 | 65 | 281637 | -1000000
8 | 22 | 6 | 2 | 45.8103 | 0 | 140.608 | 0 | 59.6295 | 0 | 6.332 | 23.0562 | 0 | 0 | 0 | 2.4 | 277.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28647.1 | 0 | 28647.1 | 1240020 | -5983.7 | 64 | 65 | 1240020 | -1005983.7
8 | 22 | 7 | 2 | 39.4347 | 0 | 168.222 | 0 | 73.1493 | 0 | 25.335 | 22.8118 | 0 | 0 | 0 | 0.8 | 329.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31406.5 | 0 | 31406.5 | 1324020 | -23307.9 | 66 | 68 | 1324020 | -1023307.9
8 | 22 | 8 | 2 | 39.9178 | 0 | 173.795 | 0 | 77.8263 | 0 | 25.335 | 21.9191 | 0 | 0 | 0 | 0 | 338.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39722.5 | 0 | 39722.5 | 1331670 | -22729.5 | 67 | 72 | 1331670 | -1022729.5
8 | 22 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 86.3018 | 0 | 25.335 | 22.3347 | 0 | 0 | 0 | 0 | 346.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61837 | 0 | 61837 | 1441170 | -22229.7 | 69 | 75 | 1441170 | -1022229.7
8 | 22 | 10 | 2 | 41.1562 | 0 | 163.102 | 0 | 89.5955 | 0 | 25.335 | 23.0922 | 0 | 0 | 0 | 0 | 342.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.9 | 0 | 63221.9 | 1510320 | -18487.7 | 71 | 78 | 1510320 | -1018487.7
8 | 22 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 87.0974 | 0 | 25.335 | 23.3309 | 0 | 0 | 0 | 0 | 326.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.3 | 0 | 63223.3 | 1463980 | -13744.1 | 73 | 82 | 1463980 | -1013744.1
8 | 22 | 12 | 2 | 39.7744 | 0 | 150.207 | 0 | 92.695 | 0 | 25.335 | 23.6774 | 0 | 0 | 0 | 0 | 331.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.9 | 0 | 63222.9 | 1544170 | -14766.6 | 74 | 82 | 1544170 | -1014766.6
8 | 22 | 13 | 2 | 41.2764 | 0 | 165.698 | 0 | 107.909 | 0 | 25.335 | 23.713 | 0 | 0 | 0 | 0 | 363.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.8 | 0 | 63223.8 | 1777400 | -20546.8 | 75 | 85 | 1777400 | -1020546.8
8 | 22 | 14 | 2 | 40.6658 | 0 | 172.702 | 0 | 109.979 | 0 | 25.335 | 23.6642 | 0 | 0 | 0 | 0 | 372.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.7 | 0 | 61841.7 | 1800610 | -19869.3 | 75 | 87 | 1800610 | -1019869.3
8 | 22 | 15 | 2 | 40.5614 | 0 | 173.986 | 0 | 117.588 | 0 | 25.335 | 23.2191 | 0 | 0 | 0 | 0 | 380.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56315.2 | 0 | 56315.2 | 1878680 | -34062.4 | 75 | 87 | 1878680 | -1034062.4
8 | 22 | 16 | 2 | 40.3117 | 0 | 169.782 | 0 | 122.987 | 0 | 25.335 | 23.4255 | 0 | 0 | 0 | 1.2 | 383.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46642.2 | 0 | 46642.2 | 1933460 | -33715.1 | 76 | 88 | 1933460 | -1033715.1
8 | 22 | 17 | 2 | 35.49 | 0 | 152.497 | 0 | 114.091 | 0 | 11.5198 | 23.074 | 0 | 0 | 0 | 4.8 | 341.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35587.1 | 0 | 35587.1 | 1753370 | -35228.2 | 74 | 87 | 1753370 | -1035228.2
8 | 22 | 18 | 2 | 24.6093 | 0 | 93.4203 | 0 | 82.1779 | 0 | 11.1422 | 21.6209 | 0 | 0 | 0 | 7.2 | 240.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21768.3 | 0 | 21768.3 | 1290040 | -34791.5 | 74 | 84 | 1290040 | -1034791.5
8 | 22 | 19 | 2 | 21.7822 | 0 | 62.7906 | 0 | 12.2895 | 0 | 13.0713 | 8.818 | 0 | 0 | 0 | 7.2 | 125.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15550 | 0 | 15550 | 195580 | 0 | 73 | 79 | 195580 | -1000000
8 | 22 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 9.6212 | 0 | 9.2028 | 8.818 | 0 | 0 | 0 | 7.2 | 108.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14859.4 | 0 | 14859.4 | 174757 | 0 | 72 | 74 | 174757 | -1000000
8 | 22 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.6705 | 0 | 8.5329 | 8.818 | 0 | 0 | 0 | 7.2 | 95.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9316.99 | 0 | 9316.99 | 161591 | 0 | 72 | 74 | 161591 | -1000000
8 | 22 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.7709 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 6.4 | 84.0008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9092.08 | 0 | 9092.08 | 150547 | 0 | 71 | 73 | 150547 | -1000000
8 | 22 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.1492 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.47 | 0 | 7928.47 | 145368 | 0 | 70 | 71 | 145368 | -1000000
8 | 22 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.3002 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.02 | 0 | 7927.02 | 143814 | 0 | 70 | 70 | 143814 | -1000000
8 | 23 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.8333 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 80.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.84 | 0 | 7925.84 | 142673 | 0 | 68 | 71 | 142673 | -1000000
8 | 23 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1989 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.12 | 0 | 7925.12 | 141727 | 0 | 67 | 70 | 141727 | -1000000
8 | 23 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.4199 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.35 | 0 | 7924.35 | 140685 | 0 | 65 | 70 | 140685 | -1000000
8 | 23 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.2586 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 82.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8780.42 | 0 | 8780.42 | 143913 | 0 | 64 | 69 | 143913 | -1000000
8 | 23 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 13.5272 | 0 | 5.6704 | 12.8287 | 0 | 0 | 0 | 4.8 | 131.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10686.5 | 0 | 10686.5 | 285718 | 0 | 64 | 67 | 285718 | -1000000
8 | 23 | 6 | 3 | 48.2194 | 0 | 140.608 | 0 | 61.3295 | 0 | 25.335 | 23.4153 | 0 | 0 | 0 | 2.4 | 301.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28650 | 0 | 28650 | 1202070 | -4840.67 | 63 | 66 | 1202070 | -1004840.67
8 | 23 | 7 | 3 | 47.1709 | 0 | 168.222 | 0 | 68.8372 | 0 | 25.335 | 23.1467 | 0 | 0 | 0 | 0.8 | 333.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31409.3 | 0 | 31409.3 | 1253850 | -26776.3 | 64 | 66 | 1253850 | -1026776.3
8 | 23 | 8 | 3 | 40.1908 | 0 | 173.795 | 0 | 65.5511 | 0 | 25.335 | 22.7078 | 0 | 0 | 0 | 0 | 327.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39724.3 | 0 | 39724.3 | 1177660 | -26534.9 | 64 | 67 | 1177660 | -1026534.9
8 | 23 | 9 | 3 | 41.1269 | 0 | 172.186 | 0 | 69.5873 | 0 | 25.335 | 23.4387 | 0 | 0 | 0 | 0 | 331.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61837.8 | 0 | 61837.8 | 1224120 | -26477.6 | 65 | 69 | 1224120 | -1026477.6
8 | 23 | 10 | 3 | 41.9764 | 0 | 163.102 | 0 | 68.8294 | 0 | 25.335 | 23.2392 | 0 | 0 | 0 | 0 | 322.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63220.6 | 0 | 63220.6 | 1208410 | -23293.5 | 65 | 70 | 1208410 | -1023293.5
8 | 23 | 11 | 3 | 40.8126 | 0 | 149.692 | 0 | 67.7994 | 0 | 25.335 | 23.2808 | 0 | 0 | 0 | 0 | 306.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221 | 0 | 63221 | 1164970 | -18887 | 67 | 72 | 1164970 | -1018887
8 | 23 | 12 | 3 | 39.8448 | 0 | 150.207 | 0 | 68.4096 | 0 | 25.335 | 23.4371 | 0 | 0 | 0 | 0 | 307.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.4 | 0 | 63221.4 | 1182210 | -17747.3 | 67 | 72 | 1182210 | -1017747.3
8 | 23 | 13 | 3 | 41.5912 | 0 | 165.698 | 0 | 72.0594 | 0 | 25.335 | 23.3942 | 0 | 0 | 0 | 0 | 328.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.5 | 0 | 63222.5 | 1245930 | -21512.8 | 66 | 71 | 1245930 | -1021512.8
8 | 23 | 14 | 3 | 41.0791 | 0 | 172.702 | 0 | 72.82 | 0 | 25.335 | 23.7699 | 0 | 0 | 0 | 0 | 335.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.1 | 0 | 61841.1 | 1257610 | -25486.6 | 66 | 71 | 1257610 | -1025486.6
8 | 23 | 15 | 3 | 41.0207 | 0 | 173.986 | 0 | 75.2868 | 0 | 25.335 | 24.0018 | 0 | 0 | 0 | 0 | 339.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56313.8 | 0 | 56313.8 | 1285430 | -26711.7 | 66 | 71 | 1285430 | -1026711.7
8 | 23 | 16 | 3 | 41.3642 | 0 | 169.782 | 0 | 73.0744 | 0 | 25.335 | 23.4182 | 0 | 0 | 0 | 1.2 | 334.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46640.2 | 0 | 46640.2 | 1278520 | -25900.7 | 66 | 71 | 1278520 | -1025900.7
8 | 23 | 17 | 3 | 36.4116 | 0 | 152.497 | 0 | 65.2764 | 0 | 25.335 | 23.1972 | 0 | 0 | 0 | 4.8 | 307.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35584.9 | 0 | 35584.9 | 1170880 | -22057.8 | 66 | 71 | 1170880 | -1022057.8
8 | 23 | 18 | 3 | 27.7939 | 0 | 93.4203 | 0 | 43.0952 | 0 | 25.335 | 20.5554 | 0 | 0 | 0 | 7.2 | 217.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21766 | 0 | 21766 | 789305 | -16736.1 | 65 | 70 | 789305 | -1016736.1
8 | 23 | 19 | 3 | 23.0002 | 0 | 62.7906 | 0 | 10.9695 | 0 | 10.4493 | 8.818 | 0 | 0 | 0 | 7.2 | 123.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15548 | 0 | 15548 | 194379 | 0 | 64 | 69 | 194379 | -1000000
8 | 23 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.6874 | 0 | 5.515 | 8.818 | 0 | 0 | 0 | 7.2 | 103.585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14859.1 | 0 | 14859.1 | 174334 | 0 | 63 | 68 | 174334 | -1000000
8 | 23 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.0703 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 7.2 | 91.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9318.06 | 0 | 9318.06 | 160787 | 0 | 61 | 64 | 160787 | -1000000
8 | 23 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2981 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.77 | 0 | 9094.77 | 149724 | 0 | 61 | 63 | 149724 | -1000000
8 | 23 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.0167 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.9 | 0 | 7931.9 | 144580 | 0 | 60 | 62 | 144580 | -1000000
8 | 23 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.6067 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.73 | 0 | 7931.73 | 142899 | 0 | 59 | 60 | 142899 | -1000000
8 | 24 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0638 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.43 | 0 | 7931.43 | 141682 | 0 | 57 | 58 | 141682 | -1000000
8 | 24 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0234 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.6 | 0 | 7931.6 | 140804 | 0 | 56 | 56 | 140804 | -1000000
8 | 24 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9806 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7931.4 | 0 | 7931.4 | 139867 | 0 | 55 | 55 | 139867 | -1000000
8 | 24 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.113 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 82.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8788.52 | 0 | 8788.52 | 142829 | 0 | 55 | 55 | 142829 | -1000000
8 | 24 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.0258 | 0 | 5.569 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10695.4 | 0 | 10695.4 | 252173 | 0 | 53 | 53 | 252173 | -1000000
8 | 24 | 6 | 4 | 45.9266 | 0 | 140.608 | 0 | 33.8468 | 0 | 6.332 | 20.4877 | 0 | 0 | 0 | 2.4 | 249.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28659.6 | 0 | 28659.6 | 653587 | -9900.27 | 54 | 54 | 653587 | -1009900.27
8 | 24 | 7 | 4 | 39.1808 | 0 | 168.222 | 0 | 47.3748 | 0 | 6.332 | 21.0006 | 0 | 0 | 0 | 0.8 | 282.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31419.5 | 0 | 31419.5 | 869403 | -29186.3 | 58 | 60 | 869403 | -1029186.3
8 | 24 | 8 | 4 | 39.6671 | 0 | 173.795 | 0 | 51.3095 | 0 | 25.335 | 21.7768 | 0 | 0 | 0 | 0 | 311.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39728.2 | 0 | 39728.2 | 940174 | -27820.8 | 60 | 63 | 940174 | -1027820.8
8 | 24 | 9 | 4 | 41.8867 | 0 | 172.186 | 0 | 49.7937 | 0 | 25.335 | 21.4396 | 0 | 0 | 0 | 0 | 310.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61840.4 | 0 | 61840.4 | 934243 | -27190.9 | 60 | 63 | 934243 | -1027190.9
8 | 24 | 10 | 4 | 41.8043 | 0 | 163.102 | 0 | 55.057 | 0 | 25.335 | 21.6098 | 0 | 0 | 0 | 0 | 306.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.9 | 0 | 63222.9 | 998981 | -23945.9 | 62 | 66 | 998981 | -1023945.9
8 | 24 | 11 | 4 | 41.0905 | 0 | 149.692 | 0 | 49.4912 | 0 | 25.335 | 21.5604 | 0 | 0 | 0 | 0 | 287.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.3 | 0 | 63223.3 | 905893 | -19829 | 62 | 66 | 905893 | -1019829
8 | 24 | 12 | 4 | 39.8488 | 0 | 150.207 | 0 | 52.4553 | 0 | 25.335 | 21.9765 | 0 | 0 | 0 | 0 | 289.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63223.8 | 0 | 63223.8 | 950160 | -18331.5 | 63 | 67 | 950160 | -1018331.5
8 | 24 | 13 | 4 | 41.2775 | 0 | 165.698 | 0 | 67.5132 | 0 | 25.335 | 22.7596 | 0 | 0 | 0 | 0 | 322.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.5 | 0 | 63224.5 | 1152610 | -20785.1 | 64 | 72 | 1152610 | -1020785.1
8 | 24 | 14 | 4 | 40.6611 | 0 | 172.702 | 0 | 73.5761 | 0 | 25.335 | 22.8799 | 0 | 0 | 0 | 0 | 335.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61842.9 | 0 | 61842.9 | 1247630 | -23473.8 | 65 | 75 | 1247630 | -1023473.8
8 | 24 | 15 | 4 | 40.5505 | 0 | 173.986 | 0 | 72.2387 | 0 | 25.335 | 22.9432 | 0 | 0 | 0 | 0 | 335.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56316.4 | 0 | 56316.4 | 1260140 | -24646.1 | 64 | 74 | 1260140 | -1024646.1
8 | 24 | 16 | 4 | 40.3346 | 0 | 169.782 | 0 | 73.1214 | 0 | 25.335 | 23.2113 | 0 | 0 | 0 | 1.2 | 332.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46642.9 | 0 | 46642.9 | 1272580 | -22860.3 | 65 | 78 | 1272580 | -1022860.3
8 | 24 | 17 | 4 | 35.4919 | 0 | 152.497 | 0 | 64.4562 | 0 | 25.335 | 23.1124 | 0 | 0 | 0 | 4.8 | 305.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35587.8 | 0 | 35587.8 | 1130970 | -19184.1 | 63 | 76 | 1130970 | -1019184.1
8 | 24 | 18 | 4 | 24.9223 | 0 | 93.4203 | 0 | 44.0294 | 0 | 25.335 | 20.9265 | 0 | 0 | 0 | 7.2 | 215.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21768.7 | 0 | 21768.7 | 787200 | -13735.7 | 63 | 74 | 787200 | -1013735.7
8 | 24 | 19 | 4 | 20.9766 | 0 | 62.7906 | 0 | 9.559 | 0 | 9.2186 | 8.818 | 0 | 0 | 0 | 7.2 | 118.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15550.3 | 0 | 15550.3 | 194252 | 0 | 62 | 70 | 194252 | -1000000
8 | 24 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 7.7852 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 7.2 | 102.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14860.9 | 0 | 14860.9 | 174147 | 0 | 61 | 66 | 174147 | -1000000
8 | 24 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.586 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.05 | 0 | 9320.05 | 160606 | 0 | 60 | 64 | 160606 | -1000000
8 | 24 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2836 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.69 | 0 | 9096.69 | 149409 | 0 | 59 | 63 | 149409 | -1000000
8 | 24 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.3105 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 5.6 | 80.0651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.02 | 0 | 7934.02 | 144479 | 0 | 59 | 63 | 144479 | -1000000
8 | 24 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.6301 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.92 | 0 | 7933.92 | 142645 | 0 | 57 | 61 | 142645 | -1000000
8 | 25 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8186 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.96 | 0 | 7933.96 | 141939 | 0 | 58 | 60 | 141939 | -1000000
8 | 25 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0185 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.08 | 0 | 7934.08 | 140690 | 0 | 56 | 58 | 140690 | -1000000
8 | 25 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.979 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.25 | 0 | 7934.25 | 139832 | 0 | 55 | 56 | 139832 | -1000000
8 | 25 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.1063 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8791.22 | 0 | 8791.22 | 142680 | 0 | 54 | 54 | 142680 | -1000000
8 | 25 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.3133 | 0 | 5.5424 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10698.5 | 0 | 10698.5 | 236304 | 0 | 54 | 55 | 236304 | -1000000
8 | 25 | 6 | 5 | 47.3156 | 0 | 140.608 | 0 | 34.1048 | 0 | 6.332 | 20.1233 | 0 | 0 | 0 | 2.4 | 250.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28663.1 | 0 | 28663.1 | 642135 | -10369.6 | 55 | 56 | 642135 | -1010369.6
8 | 25 | 7 | 5 | 43.2855 | 0 | 168.222 | 0 | 42.9314 | 0 | 6.332 | 20.3219 | 0 | 0 | 0 | 0.8 | 281.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31423.5 | 0 | 31423.5 | 781902 | -30866.4 | 57 | 58 | 781902 | -1030866.4
8 | 25 | 8 | 5 | 39.9671 | 0 | 173.795 | 0 | 46.5909 | 0 | 25.335 | 20.8132 | 0 | 0 | 0 | 0 | 306.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39730.4 | 0 | 39730.4 | 861100 | -28606.8 | 59 | 62 | 861100 | -1028606.8
8 | 25 | 9 | 5 | 41.2067 | 0 | 172.186 | 0 | 51.685 | 0 | 25.335 | 21.2715 | 0 | 0 | 0 | 0 | 311.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61842.1 | 0 | 61842.1 | 942986 | -28178.8 | 61 | 64 | 942986 | -1028178.8
8 | 25 | 10 | 5 | 41.8164 | 0 | 163.102 | 0 | 55.7488 | 0 | 25.335 | 21.4451 | 0 | 0 | 0 | 0 | 307.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.7 | 0 | 63224.7 | 988315 | -23818 | 62 | 67 | 988315 | -1023818
8 | 25 | 11 | 5 | 40.9851 | 0 | 149.692 | 0 | 55.8941 | 0 | 25.335 | 21.7947 | 0 | 0 | 0 | 0 | 293.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.1 | 0 | 63225.1 | 967510 | -18864.5 | 64 | 70 | 967510 | -1018864.5
8 | 25 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 70.3274 | 0 | 25.335 | 22.0225 | 0 | 0 | 0 | 0 | 307.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.4 | 0 | 63225.4 | 1163000 | -26373.8 | 66 | 75 | 1163000 | -1026373.8
8 | 25 | 13 | 5 | 41.2666 | 0 | 165.698 | 0 | 77.9009 | 0 | 25.335 | 23.2221 | 0 | 0 | 0 | 0 | 333.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63226 | 0 | 63226 | 1307350 | -18550.5 | 68 | 77 | 1307350 | -1018550.5
8 | 25 | 14 | 5 | 40.7392 | 0 | 172.702 | 0 | 75.54 | 0 | 25.335 | 23.2239 | 0 | 0 | 0 | 0 | 337.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61845.5 | 0 | 61845.5 | 1277720 | -22790.1 | 67 | 75 | 1277720 | -1022790.1
8 | 25 | 15 | 5 | 40.8233 | 0 | 173.986 | 0 | 77.2289 | 0 | 25.335 | 23.6534 | 0 | 0 | 0 | 0 | 341.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56317.5 | 0 | 56317.5 | 1310050 | -24099 | 67 | 76 | 1310050 | -1024099
8 | 25 | 16 | 5 | 40.3114 | 0 | 169.782 | 0 | 80.0388 | 0 | 25.335 | 23.2788 | 0 | 0 | 0 | 1.2 | 339.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.6 | 0 | 46643.6 | 1380550 | -23211.4 | 68 | 76 | 1380550 | -1023211.4
8 | 25 | 17 | 5 | 35.6129 | 0 | 152.497 | 0 | 72.3674 | 0 | 25.335 | 23.3554 | 0 | 0 | 0 | 4.8 | 313.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588 | 0 | 35588 | 1263380 | -19182.6 | 68 | 76 | 1263380 | -1019182.6
8 | 25 | 18 | 5 | 25.197 | 0 | 93.4203 | 0 | 48.2302 | 0 | 25.335 | 20.9008 | 0 | 0 | 0 | 7.2 | 220.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.4 | 0 | 21769.4 | 857337 | -14215 | 67 | 74 | 857337 | -1014215
8 | 25 | 19 | 5 | 23.2803 | 0 | 62.7906 | 0 | 11.4638 | 0 | 11.3929 | 8.818 | 0 | 0 | 0 | 7.2 | 124.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15550.9 | 0 | 15550.9 | 194735 | 0 | 67 | 73 | 194735 | -1000000
8 | 25 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 9.2046 | 0 | 8.816 | 8.818 | 0 | 0 | 0 | 7.2 | 107.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14861.8 | 0 | 14861.8 | 174439 | 0 | 67 | 72 | 174439 | -1000000
8 | 25 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.6967 | 0 | 8.3535 | 8.818 | 0 | 0 | 0 | 7.2 | 95.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.91 | 0 | 9320.91 | 161008 | 0 | 66 | 72 | 161008 | -1000000
8 | 25 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.7099 | 0 | 7.4808 | 8.818 | 0 | 0 | 0 | 6.4 | 85.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.41 | 0 | 9097.41 | 149980 | 0 | 66 | 71 | 149980 | -1000000
8 | 25 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 8.0468 | 0 | 7.8053 | 8.818 | 0 | 0 | 0 | 5.6 | 83.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.33 | 0 | 7934.33 | 144753 | 0 | 65 | 72 | 144753 | -1000000
8 | 25 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.3724 | 0 | 7.218 | 8.818 | 0 | 0 | 0 | 4.8 | 77.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.68 | 0 | 7933.68 | 143247 | 0 | 65 | 71 | 143247 | -1000000
8 | 26 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2791 | 0 | 7.1204 | 8.818 | 0 | 0 | 0 | 4.8 | 77.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.08 | 0 | 7933.08 | 142227 | 0 | 65 | 70 | 142227 | -1000000
8 | 26 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.1854 | 0 | 7.0267 | 8.818 | 0 | 0 | 0 | 4.8 | 76.9571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.12 | 0 | 7933.12 | 141164 | 0 | 64 | 69 | 141164 | -1000000
8 | 26 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.1128 | 0 | 6.951 | 8.818 | 0 | 0 | 0 | 4.8 | 76.8088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.83 | 0 | 7932.83 | 140521 | 0 | 64 | 68 | 140521 | -1000000
8 | 26 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0256 | 0 | 6.8689 | 8.818 | 0 | 0 | 0 | 4.8 | 76.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.61 | 0 | 7932.61 | 139540 | 0 | 63 | 67 | 139540 | -1000000
8 | 26 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.2657 | 0 | 7.0275 | 8.818 | 0 | 0 | 0 | 4.8 | 77.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.43 | 0 | 7932.43 | 138950 | 0 | 63 | 67 | 138950 | -1000000
8 | 26 | 6 | 6 | 6.1891 | 0 | 42.7453 | 0 | 7.1693 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 2.4 | 72.8003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.29 | 0 | 7932.29 | 138102 | 0 | 62 | 67 | 138102 | -1000000
8 | 26 | 7 | 6 | 5.3589 | 0 | 42.7453 | 0 | 24.9624 | 0 | 13.2822 | 19.074 | 0 | 0 | 0 | 0.8 | 106.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.24 | 0 | 7932.24 | 509958 | -4301.83 | 64 | 69 | 509958 | -1004301.83
8 | 26 | 8 | 6 | 5.4263 | 0 | 42.7453 | 0 | 25.7343 | 0 | 25.335 | 19.1178 | 0 | 0 | 0 | 0 | 118.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.09 | 0 | 7932.09 | 457349 | -6084.09 | 64 | 70 | 457349 | -1006084.09
8 | 26 | 9 | 6 | 6.2916 | 0 | 42.7453 | 0 | 25.4232 | 0 | 25.335 | 19.0436 | 0 | 0 | 0 | 0 | 118.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.46 | 0 | 7948.46 | 455337 | -10876.6 | 65 | 70 | 455337 | -1010876.6
8 | 26 | 10 | 6 | 5.8282 | 0 | 42.7453 | 0 | 26.4377 | 0 | 25.335 | 19.0564 | 0 | 0 | 0 | 0 | 119.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7950.43 | 0 | 7950.43 | 474014 | -12375.1 | 66 | 70 | 474014 | -1012375.1
8 | 26 | 11 | 6 | 6.1426 | 0 | 42.7453 | 0 | 21.1335 | 0 | 25.335 | 18.9661 | 0 | 0 | 0 | 0 | 114.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7952.21 | 0 | 7952.21 | 412984 | -13423.6 | 65 | 65 | 412984 | -1013423.6
8 | 26 | 12 | 6 | 5.6755 | 0 | 42.7453 | 0 | 26.9591 | 0 | 25.335 | 19.0247 | 0 | 0 | 0 | 0 | 119.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7953.29 | 0 | 7953.29 | 465460 | -14143.3 | 67 | 68 | 465460 | -1014143.3
8 | 26 | 13 | 6 | 5.53 | 0 | 42.7453 | 0 | 33.9444 | 0 | 25.335 | 19.1279 | 0 | 0 | 0 | 0 | 126.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.12 | 0 | 7954.12 | 557446 | -14538.8 | 70 | 73 | 557446 | -1014538.8
8 | 26 | 14 | 6 | 5.5868 | 0 | 42.7453 | 0 | 8.669 | 0 | 7.8115 | 8.818 | 0 | 0 | 0 | 0 | 73.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7954.99 | 0 | 7954.99 | 134007 | 0 | 70 | 73 | 134007 | -1000000
8 | 26 | 15 | 6 | 5.7001 | 0 | 42.7453 | 0 | 8.2398 | 0 | 7.476 | 8.818 | 0 | 0 | 0 | 0 | 72.9792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7955.69 | 0 | 7955.69 | 133656 | 0 | 70 | 73 | 133656 | -1000000
8 | 26 | 16 | 6 | 5.4737 | 0 | 42.7453 | 0 | 8.7916 | 0 | 8.1014 | 8.818 | 0 | 0 | 0 | 1.2 | 75.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7949.19 | 0 | 7949.19 | 133451 | 0 | 71 | 76 | 133451 | -1000000
8 | 26 | 17 | 6 | 5.4748 | 0 | 42.7453 | 0 | 8.0033 | 0 | 7.5062 | 8.818 | 0 | 0 | 0 | 4.8 | 77.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.97 | 0 | 7945.97 | 133170 | 0 | 71 | 77 | 133170 | -1000000
8 | 26 | 18 | 6 | 5.5636 | 0 | 42.7453 | 0 | 7.8929 | 0 | 7.4654 | 8.818 | 0 | 0 | 0 | 7.2 | 79.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.6 | 0 | 7943.6 | 132910 | 0 | 71 | 76 | 132910 | -1000000
8 | 26 | 19 | 6 | 7.8588 | 0 | 42.7453 | 0 | 6.9756 | 0 | 6.849 | 8.818 | 0 | 0 | 0 | 7.2 | 80.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7941.56 | 0 | 7941.56 | 132572 | 0 | 70 | 73 | 132572 | -1000000
8 | 26 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.198 | 0 | 5.4833 | 8.818 | 0 | 0 | 0 | 7.2 | 79.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7940.03 | 0 | 7940.03 | 132246 | 0 | 69 | 70 | 132246 | -1000000
8 | 26 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.0014 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 80.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7938.92 | 0 | 7938.92 | 132035 | 0 | 69 | 70 | 132035 | -1000000
8 | 26 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3686 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7938.09 | 0 | 7938.09 | 131707 | 0 | 68 | 68 | 131707 | -1000000
8 | 26 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5808 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 5.6 | 78.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7937.63 | 0 | 7937.63 | 131328 | 0 | 67 | 67 | 131328 | -1000000
8 | 26 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 7.143 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 74.0903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.75 | 0 | 3100.75 | 131084 | 0 | 68 | 68 | 131084 | -1000000
8 | 27 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.8618 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.29 | 0 | 3100.29 | 130809 | 0 | 68 | 68 | 130809 | -1000000
8 | 27 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5387 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.04 | 0 | 3100.04 | 130441 | 0 | 67 | 67 | 130441 | -1000000
8 | 27 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4847 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.83 | 0 | 3099.83 | 130080 | 0 | 66 | 66 | 130080 | -1000000
8 | 27 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 7.3593 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 74.3066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.41 | 0 | 3099.41 | 130003 | 0 | 68 | 68 | 130003 | -1000000
8 | 27 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5016 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.06 | 0 | 3099.06 | 129661 | 0 | 67 | 67 | 129661 | -1000000
8 | 27 | 6 | 7 | 5.0381 | 0 | 42.7453 | 0 | 6.4482 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 2.4 | 70.9318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.73 | 0 | 3098.73 | 129307 | 0 | 66 | 66 | 129307 | -1000000
8 | 27 | 7 | 7 | 3.9867 | 0 | 42.7453 | 0 | 6.704 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 0.8 | 68.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.33 | 0 | 3098.33 | 129115 | 0 | 66 | 66 | 129115 | -1000000
8 | 27 | 8 | 7 | 3.7961 | 0 | 42.7453 | 0 | 9.6576 | 0 | 5.5063 | 12.8287 | 0 | 0 | 0 | 0 | 74.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.05 | 0 | 3098.05 | 185873 | 0 | 66 | 67 | 185873 | -1000000
8 | 27 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 8.024 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 0 | 69.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3097.97 | 0 | 3097.97 | 128820 | 0 | 68 | 71 | 128820 | -1000000
8 | 27 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.735 | 0 | 5.55 | 12.8287 | 0 | 0 | 0 | 0 | 76.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3097.61 | 0 | 3097.61 | 195287 | 0 | 69 | 73 | 195287 | -1000000
8 | 27 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 12.3749 | 0 | 13.4699 | 12.8287 | 0 | 0 | 0 | 0 | 85.5627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3096.35 | 0 | 3096.35 | 208224 | 0 | 71 | 78 | 208224 | -1000000
8 | 27 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 12.5372 | 0 | 13.2958 | 12.8287 | 0 | 0 | 0 | 0 | 85.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3094.04 | 0 | 3094.04 | 214687 | 0 | 72 | 81 | 214687 | -1000000
8 | 27 | 13 | 7 | 4.1456 | 0 | 42.7453 | 0 | 13.1386 | 0 | 14.5162 | 12.8287 | 0 | 0 | 0 | 0 | 87.3743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3092.43 | 0 | 3092.43 | 226416 | 0 | 70 | 82 | 226416 | -1000000
8 | 27 | 14 | 7 | 4.2565 | 0 | 42.7453 | 0 | 12.1935 | 0 | 12.8533 | 12.8287 | 0 | 0 | 0 | 0 | 84.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.07 | 0 | 3090.07 | 211117 | 0 | 69 | 83 | 211117 | -1000000
8 | 27 | 15 | 7 | 4.1481 | 0 | 42.7453 | 0 | 16.0608 | 0 | 22.1715 | 14.8767 | 0 | 0 | 0 | 0 | 100.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.07 | 0 | 3088.07 | 283322 | 0 | 69 | 85 | 283322 | -1000000
8 | 27 | 16 | 7 | 4.1476 | 0 | 42.7453 | 0 | 16.2082 | 0 | 22.6785 | 14.8767 | 0 | 0 | 0 | 1.2 | 101.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3085.78 | 0 | 3085.78 | 285314 | 0 | 70 | 84 | 285314 | -1000000
8 | 27 | 17 | 7 | 4.15 | 0 | 42.7453 | 0 | 15.5701 | 0 | 21.2587 | 14.8767 | 0 | 0 | 0 | 4.8 | 103.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.34 | 0 | 3084.34 | 278682 | 0 | 70 | 82 | 278682 | -1000000
8 | 27 | 18 | 7 | 4.7794 | 0 | 42.7453 | 0 | 7.1719 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 76.1934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3082.18 | 0 | 3082.18 | 128664 | 0 | 72 | 78 | 128664 | -1000000
8 | 27 | 19 | 7 | 6.1748 | 0 | 42.7453 | 0 | 7.0406 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 77.4573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.54 | 0 | 3080.54 | 128525 | 0 | 70 | 75 | 128525 | -1000000
8 | 27 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4057 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 7.2 | 77.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3079.17 | 0 | 3079.17 | 128584 | 0 | 70 | 73 | 128584 | -1000000
8 | 27 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.6401 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 7.2 | 77.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3078.13 | 0 | 3078.13 | 128550 | 0 | 70 | 72 | 128550 | -1000000
8 | 27 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.9065 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 77.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3077.45 | 0 | 3077.45 | 128384 | 0 | 69 | 72 | 128384 | -1000000
8 | 27 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.5889 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 5.6 | 75.8956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3076.9 | 0 | 3076.9 | 128309 | 0 | 69 | 71 | 128309 | -1000000
8 | 27 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 7.1829 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.61 | 0 | 7912.61 | 128429 | 0 | 68 | 72 | 128429 | -1000000
8 | 28 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.9017 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.2 | 0 | 7912.2 | 128285 | 0 | 67 | 72 | 128285 | -1000000
8 | 28 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5785 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7910.86 | 0 | 7910.86 | 128092 | 0 | 66 | 71 | 128092 | -1000000
8 | 28 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.9865 | 0 | 5.5207 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.3152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7910.01 | 0 | 7910.01 | 193726 | 0 | 66 | 71 | 193726 | -1000000
8 | 28 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 5.8567 | 0 | 5.4886 | 8.818 | 0 | 0 | 0 | 4.8 | 81.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8765.84 | 0 | 8765.84 | 131894 | 0 | 66 | 67 | 131894 | -1000000
8 | 28 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.3218 | 0 | 5.6537 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10672 | 0 | 10672 | 277427 | 0 | 65 | 66 | 277427 | -1000000
8 | 28 | 6 | 1 | 48.605 | 0 | 140.608 | 0 | 74.6566 | 0 | 6.332 | 23.556 | 0 | 0 | 0 | 2.4 | 296.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28635.5 | 0 | 28635.5 | 1424370 | -6278.02 | 66 | 66 | 1424370 | -1006278.02
8 | 28 | 7 | 1 | 48.4395 | 0 | 168.222 | 0 | 77.3821 | 0 | 6.332 | 23.0125 | 0 | 0 | 0 | 0.8 | 324.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31394.8 | 0 | 31394.8 | 1407850 | -32017.5 | 66 | 67 | 1407850 | -1032017.5
8 | 28 | 8 | 1 | 40.0685 | 0 | 173.795 | 0 | 70.2413 | 0 | 6.332 | 23.0033 | 0 | 0 | 0 | 0 | 313.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39717 | 0 | 39717 | 1315250 | -23397.9 | 67 | 68 | 1315250 | -1023397.9
8 | 28 | 9 | 1 | 41.5316 | 0 | 172.186 | 0 | 71.8226 | 0 | 6.332 | 23.5238 | 0 | 0 | 0 | 0 | 315.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61830.9 | 0 | 61830.9 | 1331320 | -19283.4 | 68 | 70 | 1331320 | -1019283.4
8 | 28 | 10 | 1 | 42.5753 | 0 | 163.102 | 0 | 70.2048 | 0 | 6.3821 | 23.3103 | 0 | 0 | 0 | 0 | 305.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63213.8 | 0 | 63213.8 | 1348190 | -17340.4 | 69 | 70 | 1348190 | -1017340.4
8 | 28 | 11 | 1 | 40.8989 | 0 | 149.692 | 0 | 61.9102 | 0 | 25.335 | 23.623 | 0 | 0 | 0 | 0 | 301.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63214.6 | 0 | 63214.6 | 1199770 | -14051.6 | 68 | 71 | 1199770 | -1014051.6
8 | 28 | 12 | 1 | 39.7554 | 0 | 150.207 | 0 | 77.9197 | 0 | 25.335 | 23.7988 | 0 | 0 | 0 | 0 | 317.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63215.2 | 0 | 63215.2 | 1371310 | -15404.7 | 71 | 74 | 1371310 | -1015404.7
8 | 28 | 13 | 1 | 41.2523 | 0 | 165.698 | 0 | 97.2075 | 0 | 25.335 | 24.2579 | 0 | 0 | 0 | 0 | 353.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63216.7 | 0 | 63216.7 | 1666180 | -14387.7 | 74 | 81 | 1666180 | -1014387.7
8 | 28 | 14 | 1 | 40.652 | 0 | 172.702 | 0 | 100.624 | 0 | 25.335 | 23.8588 | 0 | 0 | 0 | 0 | 363.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61835.8 | 0 | 61835.8 | 1720590 | -17674.3 | 75 | 82 | 1720590 | -1017674.3
8 | 28 | 15 | 1 | 40.5659 | 0 | 173.986 | 0 | 106.702 | 0 | 25.335 | 23.9287 | 0 | 0 | 0 | 0 | 370.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56309.8 | 0 | 56309.8 | 1821760 | -21830.1 | 75 | 85 | 1821760 | -1021830.1
8 | 28 | 16 | 1 | 40.4666 | 0 | 169.782 | 0 | 105.268 | 0 | 25.335 | 24.1493 | 0 | 0 | 0 | 1.2 | 366.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46636.7 | 0 | 46636.7 | 1799290 | -17683.5 | 76 | 82 | 1799290 | -1017683.5
8 | 28 | 17 | 1 | 35.5028 | 0 | 152.497 | 0 | 97.472 | 0 | 25.335 | 23.6084 | 0 | 0 | 0 | 4.8 | 339.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35582.3 | 0 | 35582.3 | 1686570 | -22625.4 | 75 | 82 | 1686570 | -1022625.4
8 | 28 | 18 | 1 | 24.6465 | 0 | 93.4203 | 0 | 64.1901 | 0 | 25.335 | 22.5315 | 0 | 0 | 0 | 7.2 | 237.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21763.2 | 0 | 21763.2 | 1163030 | -11689.7 | 74 | 79 | 1163030 | -1011689.7
8 | 28 | 19 | 1 | 22.4091 | 0 | 62.7906 | 0 | 10.9696 | 0 | 11.8094 | 8.818 | 0 | 0 | 0 | 7.2 | 123.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15545.2 | 0 | 15545.2 | 190945 | 0 | 73 | 77 | 190945 | -1000000
8 | 28 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 9.1371 | 0 | 5.5038 | 8.818 | 0 | 0 | 0 | 7.2 | 104.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14854.7 | 0 | 14854.7 | 170303 | 0 | 72 | 75 | 170303 | -1000000
8 | 28 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 8.1547 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 7.2 | 92.3785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9312.46 | 0 | 9312.46 | 157314 | 0 | 72 | 74 | 157314 | -1000000
8 | 28 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.5771 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 6.4 | 83.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9087.94 | 0 | 9087.94 | 146611 | 0 | 72 | 73 | 146611 | -1000000
8 | 28 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 7.2825 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 5.6 | 80.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.29 | 0 | 7924.29 | 141610 | 0 | 71 | 72 | 141610 | -1000000
8 | 28 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.1704 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7923.2 | 0 | 7923.2 | 140255 | 0 | 71 | 71 | 140255 | -1000000
8 | 29 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.086 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 78.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7922.11 | 0 | 7922.11 | 139389 | 0 | 70 | 70 | 139389 | -1000000
8 | 29 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.9656 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.24 | 0 | 7921.24 | 138815 | 0 | 71 | 72 | 138815 | -1000000
8 | 29 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.7078 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.34 | 0 | 7920.34 | 138208 | 0 | 71 | 73 | 138208 | -1000000
8 | 29 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 7.2844 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 83.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8776.2 | 0 | 8776.2 | 141791 | 0 | 70 | 72 | 141791 | -1000000
8 | 29 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.0712 | 0 | 5.721 | 12.8287 | 0 | 0 | 0 | 4.8 | 131.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10682.5 | 0 | 10682.5 | 292230 | 0 | 69 | 70 | 292230 | -1000000
8 | 29 | 6 | 2 | 47.1258 | 0 | 140.608 | 0 | 73.9735 | 0 | 6.332 | 23.7864 | 0 | 0 | 0 | 2.4 | 294.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28645.7 | 0 | 28645.7 | 1437820 | -4762.97 | 68 | 70 | 1437820 | -1004762.97
8 | 29 | 7 | 2 | 39.3755 | 0 | 168.222 | 0 | 81.366 | 0 | 25.335 | 23.7175 | 0 | 0 | 0 | 0.8 | 338.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31404.9 | 0 | 31404.9 | 1428190 | -22693.1 | 68 | 70 | 1428190 | -1022693.1
8 | 29 | 8 | 2 | 39.7214 | 0 | 173.795 | 0 | 79.2595 | 0 | 25.335 | 22.6004 | 0 | 0 | 0 | 0 | 340.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39721.3 | 0 | 39721.3 | 1351280 | -22149.1 | 67 | 73 | 1351280 | -1022149.1
8 | 29 | 9 | 2 | 40.6158 | 0 | 172.186 | 0 | 76.9537 | 0 | 25.335 | 22.8624 | 0 | 0 | 0 | 0 | 337.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61835.1 | 0 | 61835.1 | 1300950 | -22951.5 | 65 | 74 | 1300950 | -1022951.5
8 | 29 | 10 | 2 | 41.1517 | 0 | 163.102 | 0 | 72.9558 | 0 | 25.335 | 23.2943 | 0 | 0 | 0 | 0 | 325.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63220.1 | 0 | 63220.1 | 1233030 | -19705 | 63 | 75 | 1233030 | -1019705
8 | 29 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 69.9862 | 0 | 25.335 | 23.2788 | 0 | 0 | 0 | 0 | 308.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.6 | 0 | 63221.6 | 1185080 | -18398.7 | 64 | 77 | 1185080 | -1018398.7
8 | 29 | 12 | 2 | 39.7554 | 0 | 150.207 | 0 | 73.808 | 0 | 25.335 | 22.076 | 0 | 0 | 0 | 0 | 311.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.1 | 0 | 63222.1 | 1228720 | -36547 | 63 | 78 | 1228720 | -1036547
8 | 29 | 13 | 2 | 41.2813 | 0 | 165.698 | 0 | 74.8195 | 0 | 25.335 | 23.223 | 0 | 0 | 0 | 0 | 330.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63222.8 | 0 | 63222.8 | 1252020 | -20743.2 | 62 | 78 | 1252020 | -1020743.2
8 | 29 | 14 | 2 | 40.6714 | 0 | 172.702 | 0 | 79.4762 | 0 | 25.335 | 23.2269 | 0 | 0 | 0 | 0 | 341.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.8 | 0 | 61841.8 | 1323610 | -20980.4 | 63 | 79 | 1323610 | -1020980.4
8 | 29 | 15 | 2 | 40.5726 | 0 | 173.986 | 0 | 81.3003 | 0 | 25.335 | 23.236 | 0 | 0 | 0 | 0 | 344.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56314.9 | 0 | 56314.9 | 1355990 | -24560.8 | 63 | 79 | 1355990 | -1024560.8
8 | 29 | 16 | 2 | 40.3157 | 0 | 169.782 | 0 | 76.5082 | 0 | 25.335 | 23.5199 | 0 | 0 | 0 | 1.2 | 336.661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46641.8 | 0 | 46641.8 | 1296780 | -22030.5 | 62 | 79 | 1296780 | -1022030.5
8 | 29 | 17 | 2 | 35.4952 | 0 | 152.497 | 0 | 69.192 | 0 | 25.335 | 23.0341 | 0 | 0 | 0 | 4.8 | 310.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35586.6 | 0 | 35586.6 | 1192210 | -22955.4 | 62 | 77 | 1192210 | -1022955.4
8 | 29 | 18 | 2 | 24.8007 | 0 | 93.4203 | 0 | 44.2128 | 0 | 25.335 | 21.6851 | 0 | 0 | 0 | 7.2 | 216.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21767.7 | 0 | 21767.7 | 773872 | -16850.3 | 60 | 75 | 773872 | -1016850.3
8 | 29 | 19 | 2 | 22.1016 | 0 | 62.7906 | 0 | 9.5777 | 0 | 8.7112 | 8.818 | 0 | 0 | 0 | 7.2 | 119.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15549 | 0 | 15549 | 193890 | 0 | 60 | 69 | 193890 | -1000000
8 | 29 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 9.0502 | 0 | 8.3724 | 8.818 | 0 | 0 | 0 | 7.2 | 106.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14858.5 | 0 | 14858.5 | 173379 | 0 | 59 | 68 | 173379 | -1000000
8 | 29 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.9516 | 0 | 5.9959 | 8.818 | 0 | 0 | 0 | 7.2 | 92.6857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9317.15 | 0 | 9317.15 | 159987 | 0 | 58 | 67 | 159987 | -1000000
8 | 29 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 6.1961 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 6.4 | 82.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9093.3 | 0 | 9093.3 | 149171 | 0 | 58 | 62 | 149171 | -1000000
8 | 29 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.2581 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 5.6 | 80.0129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.28 | 0 | 7930.28 | 144197 | 0 | 59 | 62 | 144197 | -1000000
8 | 29 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.584 | 0 | 5.483 | 8.818 | 0 | 0 | 0 | 4.8 | 78.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.85 | 0 | 7929.85 | 142400 | 0 | 58 | 60 | 142400 | -1000000
8 | 30 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0386 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.68 | 0 | 7929.68 | 141130 | 0 | 56 | 60 | 141130 | -1000000
8 | 30 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.0153 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7929.2 | 0 | 7929.2 | 140632 | 0 | 57 | 58 | 140632 | -1000000
8 | 30 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9627 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.96 | 0 | 7928.96 | 139471 | 0 | 56 | 58 | 139471 | -1000000
8 | 30 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.0942 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8785.86 | 0 | 8785.86 | 142416 | 0 | 55 | 56 | 142416 | -1000000
8 | 30 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 11.9897 | 0 | 5.5676 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10692.6 | 0 | 10692.6 | 251375 | 0 | 55 | 56 | 251375 | -1000000
8 | 30 | 6 | 3 | 47.552 | 0 | 140.608 | 0 | 35.3302 | 0 | 25.335 | 21.006 | 0 | 0 | 0 | 2.4 | 272.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28656.5 | 0 | 28656.5 | 693730 | -9053.95 | 54 | 55 | 693730 | -1009053.95
8 | 30 | 7 | 3 | 39.3275 | 0 | 168.222 | 0 | 45.4945 | 0 | 25.335 | 21.0639 | 0 | 0 | 0 | 0.8 | 300.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31416.8 | 0 | 31416.8 | 852817 | -29803.1 | 57 | 59 | 852817 | -1029803.1
8 | 30 | 8 | 3 | 39.6631 | 0 | 173.795 | 0 | 52.7124 | 0 | 25.335 | 22.0502 | 0 | 0 | 0 | 0 | 313.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39726.7 | 0 | 39726.7 | 957110 | -26971.6 | 60 | 64 | 957110 | -1026971.6
8 | 30 | 9 | 3 | 40.6158 | 0 | 172.186 | 0 | 56.4112 | 0 | 25.335 | 21.7056 | 0 | 0 | 0 | 0 | 316.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61839.3 | 0 | 61839.3 | 1011690 | -26582.1 | 60 | 66 | 1011690 | -1026582.1
8 | 30 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 63.2722 | 0 | 25.335 | 22.2031 | 0 | 0 | 0 | 0 | 315.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63221.9 | 0 | 63221.9 | 1080540 | -21459.4 | 62 | 71 | 1080540 | -1021459.4
8 | 30 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 55.1665 | 0 | 25.335 | 22.6886 | 0 | 0 | 0 | 0 | 293.588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.6 | 0 | 63224.6 | 938120 | -17264.4 | 60 | 73 | 938120 | -1017264.4
8 | 30 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 63.5407 | 0 | 25.335 | 22.7393 | 0 | 0 | 0 | 0 | 301.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.5 | 0 | 63224.5 | 1062940 | -20966 | 62 | 75 | 1062940 | -1020966
8 | 30 | 13 | 3 | 41.2679 | 0 | 165.698 | 0 | 72.9593 | 0 | 25.335 | 23.2412 | 0 | 0 | 0 | 0 | 328.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.9 | 0 | 63224.9 | 1222540 | -18370.7 | 64 | 77 | 1222540 | -1018370.7
8 | 30 | 14 | 3 | 40.6511 | 0 | 172.702 | 0 | 75.6244 | 0 | 25.335 | 22.9828 | 0 | 0 | 0 | 0 | 337.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61843.6 | 0 | 61843.6 | 1261490 | -22178.3 | 64 | 77 | 1261490 | -1022178.3
8 | 30 | 15 | 3 | 40.6933 | 0 | 173.986 | 0 | 61.4204 | 0 | 25.335 | 23.2438 | 0 | 0 | 0 | 0 | 324.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56316.5 | 0 | 56316.5 | 1079660 | -24521.1 | 59 | 71 | 1079660 | -1024521.1
8 | 30 | 16 | 3 | 40.3098 | 0 | 169.782 | 0 | 58.8424 | 0 | 25.335 | 22.8428 | 0 | 0 | 0 | 1.2 | 318.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.3 | 0 | 46643.3 | 1078080 | -24961.1 | 59 | 67 | 1078080 | -1024961.1
8 | 30 | 17 | 3 | 35.4922 | 0 | 152.497 | 0 | 60.5597 | 0 | 25.335 | 22.7469 | 0 | 0 | 0 | 4.8 | 301.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35587.2 | 0 | 35587.2 | 1066940 | -21063.9 | 62 | 70 | 1066940 | -1021063.9
8 | 30 | 18 | 3 | 24.7392 | 0 | 93.4203 | 0 | 39.7046 | 0 | 25.335 | 20.4743 | 0 | 0 | 0 | 7.2 | 210.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21768.4 | 0 | 21768.4 | 728546 | -16137.3 | 62 | 69 | 728546 | -1016137.3
8 | 30 | 19 | 3 | 22.4534 | 0 | 62.7906 | 0 | 10.2792 | 0 | 9.265 | 8.818 | 0 | 0 | 0 | 7.2 | 120.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15549.8 | 0 | 15549.8 | 193944 | 0 | 61 | 66 | 193944 | -1000000
8 | 30 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.9834 | 0 | 7.9035 | 8.818 | 0 | 0 | 0 | 7.2 | 106.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14860.7 | 0 | 14860.7 | 173750 | 0 | 60 | 64 | 173750 | -1000000
8 | 30 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 8.2778 | 0 | 7.4405 | 8.818 | 0 | 0 | 0 | 7.2 | 94.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.2 | 0 | 9320.2 | 160389 | 0 | 60 | 63 | 160389 | -1000000
8 | 30 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.5849 | 0 | 6.9768 | 8.818 | 0 | 0 | 0 | 6.4 | 85.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.17 | 0 | 9097.17 | 149110 | 0 | 59 | 62 | 149110 | -1000000
8 | 30 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.9339 | 0 | 7.2384 | 8.818 | 0 | 0 | 0 | 5.6 | 82.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.58 | 0 | 7934.58 | 144315 | 0 | 60 | 63 | 144315 | -1000000
8 | 30 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.2586 | 0 | 6.7784 | 8.818 | 0 | 0 | 0 | 4.8 | 80.7155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.56 | 0 | 7934.56 | 142533 | 0 | 59 | 62 | 142533 | -1000000
8 | 31 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.1763 | 0 | 6.7083 | 8.818 | 0 | 0 | 0 | 4.8 | 80.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.61 | 0 | 7934.61 | 141638 | 0 | 59 | 61 | 141638 | -1000000
8 | 31 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.7129 | 0 | 7.0593 | 8.818 | 0 | 0 | 0 | 4.8 | 81.4506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.68 | 0 | 7934.68 | 140696 | 0 | 59 | 62 | 140696 | -1000000
8 | 31 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.4027 | 0 | 6.8641 | 8.818 | 0 | 0 | 0 | 4.8 | 80.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.71 | 0 | 7934.71 | 139910 | 0 | 59 | 62 | 139910 | -1000000
8 | 31 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.8706 | 0 | 7.1944 | 8.818 | 0 | 0 | 0 | 4.8 | 85.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8791.52 | 0 | 8791.52 | 143149 | 0 | 60 | 63 | 143149 | -1000000
8 | 31 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.7832 | 0 | 12.9896 | 12.8287 | 0 | 0 | 0 | 4.8 | 137.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10698.5 | 0 | 10698.5 | 251434 | 0 | 61 | 63 | 251434 | -1000000
8 | 31 | 6 | 4 | 48.1637 | 0 | 140.608 | 0 | 56.3915 | 0 | 6.332 | 21.1996 | 0 | 0 | 0 | 2.4 | 275.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28662.6 | 0 | 28662.6 | 997262 | -8126.43 | 64 | 67 | 997262 | -1008126.43
8 | 31 | 7 | 4 | 39.3879 | 0 | 168.222 | 0 | 65.6238 | 0 | 25.335 | 21.8007 | 0 | 0 | 0 | 0.8 | 321.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31422.5 | 0 | 31422.5 | 1117110 | -25064.8 | 65 | 69 | 1117110 | -1025064.8
8 | 31 | 8 | 4 | 40.0577 | 0 | 173.795 | 0 | 68.7397 | 0 | 25.335 | 22.2839 | 0 | 0 | 0 | 0 | 330.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39729.7 | 0 | 39729.7 | 1185490 | -24338.9 | 67 | 71 | 1185490 | -1024338.9
8 | 31 | 9 | 4 | 41.7723 | 0 | 172.186 | 0 | 72.3325 | 0 | 25.335 | 22.519 | 0 | 0 | 0 | 0 | 334.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61841.6 | 0 | 61841.6 | 1240660 | -24445.9 | 68 | 72 | 1240660 | -1024445.9
8 | 31 | 10 | 4 | 42.1884 | 0 | 163.102 | 0 | 80.2946 | 0 | 25.335 | 22.7945 | 0 | 0 | 0 | 0 | 333.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.2 | 0 | 63224.2 | 1340000 | -20874.3 | 70 | 75 | 1340000 | -1020874.3
8 | 31 | 11 | 4 | 41.7147 | 0 | 149.692 | 0 | 71.9221 | 0 | 25.335 | 22.4266 | 0 | 0 | 0 | 0 | 311.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.5 | 0 | 63224.5 | 1227070 | -17191 | 71 | 74 | 1227070 | -1017191
8 | 31 | 12 | 4 | 39.9881 | 0 | 150.207 | 0 | 71.91 | 0 | 25.335 | 22.6002 | 0 | 0 | 0 | 0 | 310.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63224.7 | 0 | 63224.7 | 1246300 | -16572.5 | 71 | 72 | 1246300 | -1016572.5
8 | 31 | 13 | 4 | 41.2681 | 0 | 165.698 | 0 | 84.5578 | 0 | 25.335 | 23.237 | 0 | 0 | 0 | 0 | 340.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63225.3 | 0 | 63225.3 | 1422340 | -20781.6 | 72 | 73 | 1422340 | -1020781.6
8 | 31 | 14 | 4 | 40.6302 | 0 | 172.702 | 0 | 93.1247 | 0 | 25.335 | 23.3255 | 0 | 0 | 0 | 0 | 355.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61843.6 | 0 | 61843.6 | 1528790 | -23869.1 | 73 | 77 | 1528790 | -1023869.1
8 | 31 | 15 | 4 | 40.5655 | 0 | 173.986 | 0 | 97.0528 | 0 | 25.335 | 23.3128 | 0 | 0 | 0 | 0 | 360.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56316.1 | 0 | 56316.1 | 1605780 | -24763.2 | 72 | 80 | 1605780 | -1024763.2
8 | 31 | 16 | 4 | 40.3006 | 0 | 169.782 | 0 | 96.5997 | 0 | 25.335 | 23.4463 | 0 | 0 | 0 | 1.2 | 356.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46643.2 | 0 | 46643.2 | 1618800 | -23332.7 | 72 | 80 | 1618800 | -1023332.7
8 | 31 | 17 | 4 | 35.564 | 0 | 152.497 | 0 | 83.5997 | 0 | 25.335 | 23.3985 | 0 | 0 | 0 | 4.8 | 325.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35588.6 | 0 | 35588.6 | 1421980 | -19117.2 | 71 | 79 | 1421980 | -1019117.2
8 | 31 | 18 | 4 | 25.755 | 0 | 93.4203 | 0 | 56.6627 | 0 | 25.335 | 21.3702 | 0 | 0 | 0 | 7.2 | 229.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21769.8 | 0 | 21769.8 | 992928 | -13737.1 | 71 | 77 | 992928 | -1013737.1
8 | 31 | 19 | 4 | 24.1066 | 0 | 62.7906 | 0 | 10.9592 | 0 | 10.5597 | 8.818 | 0 | 0 | 0 | 7.2 | 124.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15551.1 | 0 | 15551.1 | 195547 | 0 | 70 | 72 | 195547 | -1000000
8 | 31 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.9899 | 0 | 8.6541 | 8.818 | 0 | 0 | 0 | 7.2 | 107.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14861.4 | 0 | 14861.4 | 174840 | 0 | 69 | 71 | 174840 | -1000000
8 | 31 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 6.9012 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 91.1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9320.32 | 0 | 9320.32 | 161137 | 0 | 65 | 66 | 161137 | -1000000
8 | 31 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.6952 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.71 | 0 | 9096.71 | 149929 | 0 | 64 | 66 | 149929 | -1000000
8 | 31 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.4529 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 5.6 | 80.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.72 | 0 | 7933.72 | 144899 | 0 | 64 | 66 | 144899 | -1000000
8 | 31 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.0722 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7933.39 | 0 | 7933.39 | 143347 | 0 | 64 | 65 | 143347 | -1000000
9 | 1 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2773 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7894.73 | 0 | 7894.73 | 142109 | 0 | 63 | 65 | 142109 | -1000000
9 | 1 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9369 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7894.54 | 0 | 7894.54 | 141298 | 0 | 62 | 64 | 141298 | -1000000
9 | 1 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.859 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7894.37 | 0 | 7894.37 | 140436 | 0 | 61 | 63 | 140436 | -1000000
9 | 1 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.6632 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8746.18 | 0 | 8746.18 | 143447 | 0 | 60 | 61 | 143447 | -1000000
9 | 1 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.8807 | 0 | 5.5632 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10642.4 | 0 | 10642.4 | 254641 | 0 | 58 | 59 | 254641 | -1000000
9 | 1 | 6 | 5 | 48.1409 | 0 | 140.608 | 0 | 36.6933 | 0 | 25.335 | 20.8312 | 0 | 0 | 0 | 2.4 | 274.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28506.4 | 0 | 28506.4 | 732065 | -8792.86 | 56 | 56 | 732065 | -1008792.86
9 | 1 | 7 | 5 | 39.3255 | 0 | 168.222 | 0 | 41.8544 | 0 | 6.332 | 20.7919 | 0 | 0 | 0 | 0.8 | 277.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31251.1 | 0 | 31251.1 | 795697 | -30844.4 | 56 | 58 | 795697 | -1030844.4
9 | 1 | 8 | 5 | 39.6873 | 0 | 173.795 | 0 | 47.7364 | 0 | 25.335 | 21.2463 | 0 | 0 | 0 | 0 | 307.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39513.7 | 0 | 39513.7 | 886273 | -29292.1 | 58 | 62 | 886273 | -1029292.1
9 | 1 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 53.1314 | 0 | 25.335 | 21.4771 | 0 | 0 | 0 | 0 | 312.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61503 | 0 | 61503 | 955284 | -28401.5 | 59 | 65 | 955284 | -1028401.5
9 | 1 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 55.3439 | 0 | 25.335 | 21.7244 | 0 | 0 | 0 | 0 | 306.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62879.2 | 0 | 62879.2 | 982024 | -24525.9 | 59 | 67 | 982024 | -1024525.9
9 | 1 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 52.1475 | 0 | 25.335 | 22.4224 | 0 | 0 | 0 | 0 | 290.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.6 | 0 | 62880.6 | 913332 | -19527.9 | 59 | 69 | 913332 | -1019527.9
9 | 1 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 55.4708 | 0 | 25.335 | 21.5747 | 0 | 0 | 0 | 0 | 292.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.3 | 0 | 62881.3 | 950808 | -32453.8 | 58 | 71 | 950808 | -1032453.8
9 | 1 | 13 | 5 | 41.2748 | 0 | 165.698 | 0 | 56.9279 | 0 | 25.335 | 22.5174 | 0 | 0 | 0 | 0 | 311.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.3 | 0 | 62881.3 | 986681 | -20758.3 | 58 | 71 | 986681 | -1020758.3
9 | 1 | 14 | 5 | 40.6686 | 0 | 172.702 | 0 | 59.7894 | 0 | 25.335 | 22.4281 | 0 | 0 | 0 | 0 | 320.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61507.9 | 0 | 61507.9 | 1018340 | -24182.4 | 58 | 72 | 1018340 | -1024182.4
9 | 1 | 15 | 5 | 40.5542 | 0 | 173.986 | 0 | 61.3492 | 0 | 25.335 | 22.5831 | 0 | 0 | 0 | 0 | 323.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56010.9 | 0 | 56010.9 | 1053110 | -25658.8 | 58 | 72 | 1053110 | -1025658.8
9 | 1 | 16 | 5 | 40.3299 | 0 | 169.782 | 0 | 56.744 | 0 | 25.335 | 22.7978 | 0 | 0 | 0 | 1.2 | 316.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46391.1 | 0 | 46391.1 | 1011440 | -25228.1 | 58 | 70 | 1011440 | -1025228.1
9 | 1 | 17 | 5 | 36.2621 | 0 | 152.497 | 0 | 46.0388 | 0 | 25.335 | 22.2397 | 0 | 0 | 0 | 4.8 | 287.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35397.2 | 0 | 35397.2 | 850709 | -22544.4 | 57 | 67 | 850709 | -1022544.4
9 | 1 | 18 | 5 | 29.6906 | 0 | 93.4203 | 0 | 29.7533 | 0 | 25.335 | 19.7507 | 0 | 0 | 0 | 7.2 | 205.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21654.7 | 0 | 21654.7 | 567903 | -18782.1 | 57 | 65 | 567903 | -1018782.1
9 | 1 | 19 | 5 | 23.4888 | 0 | 62.7906 | 0 | 10.6005 | 0 | 9.4966 | 8.818 | 0 | 0 | 0 | 7.2 | 122.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15470.7 | 0 | 15470.7 | 193888 | 0 | 57 | 64 | 193888 | -1000000
9 | 1 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.1385 | 0 | 7.5353 | 8.818 | 0 | 0 | 0 | 7.2 | 105.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14785.5 | 0 | 14785.5 | 173942 | 0 | 57 | 62 | 173942 | -1000000
9 | 1 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.7126 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9276.33 | 0 | 9276.33 | 160406 | 0 | 57 | 61 | 160406 | -1000000
9 | 1 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.1598 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9054.94 | 0 | 9054.94 | 149232 | 0 | 57 | 60 | 149232 | -1000000
9 | 1 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1813 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.05 | 0 | 7899.05 | 144191 | 0 | 57 | 60 | 144191 | -1000000
9 | 1 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0949 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 75.3196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.24 | 0 | 7899.24 | 142354 | 0 | 57 | 59 | 142354 | -1000000
9 | 2 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0373 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.39 | 0 | 7899.39 | 141103 | 0 | 56 | 59 | 141103 | -1000000
9 | 2 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9991 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.17 | 0 | 7900.17 | 140273 | 0 | 56 | 58 | 140273 | -1000000
9 | 2 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9583 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.58 | 0 | 7900.58 | 139378 | 0 | 56 | 58 | 139378 | -1000000
9 | 2 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9175 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.86 | 0 | 7900.86 | 138487 | 0 | 55 | 56 | 138487 | -1000000
9 | 2 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8767 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.39 | 0 | 7901.39 | 137593 | 0 | 54 | 55 | 137593 | -1000000
9 | 2 | 6 | 6 | 6.2793 | 0 | 42.7453 | 0 | 6.8419 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 2.4 | 72.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.95 | 0 | 7901.95 | 136833 | 0 | 53 | 53 | 136833 | -1000000
9 | 2 | 7 | 6 | 4.6773 | 0 | 42.7453 | 0 | 17.2351 | 0 | 6.0379 | 18.8896 | 0 | 0 | 0 | 0.8 | 90.3852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.67 | 0 | 7902.67 | 217221 | -22567.8 | 54 | 56 | 217221 | -1022567.8
9 | 2 | 8 | 6 | 4.9485 | 0 | 42.7453 | 0 | 12.0169 | 0 | 11.6487 | 18.8896 | 0 | 0 | 0 | 0 | 90.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.31 | 0 | 7903.31 | 233932 | -24475.3 | 55 | 60 | 233932 | -1024475.3
9 | 2 | 9 | 6 | 5.4698 | 0 | 42.7453 | 0 | 18.2615 | 0 | 6.1735 | 18.8896 | 0 | 0 | 0 | 0 | 91.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.01 | 0 | 7915.01 | 255802 | -21415.9 | 56 | 63 | 255802 | -1021415.9
9 | 2 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.8454 | 0 | 18.8483 | 18.8975 | 0 | 0 | 0 | 0 | 101.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7916.48 | 0 | 7916.48 | 276724 | -17667.6 | 56 | 65 | 276724 | -1017667.6
9 | 2 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 19.8782 | 0 | 25.335 | 19.0058 | 0 | 0 | 0 | 0 | 112.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7917.69 | 0 | 7917.69 | 339291 | -24439.5 | 57 | 68 | 339291 | -1024439.5
9 | 2 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 21.0888 | 0 | 25.335 | 19.0914 | 0 | 0 | 0 | 0 | 113.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.26 | 0 | 7918.26 | 361224 | -23726.6 | 56 | 70 | 361224 | -1023726.6
9 | 2 | 13 | 6 | 5.4723 | 0 | 42.7453 | 0 | 20.5089 | 0 | 25.335 | 19.166 | 0 | 0 | 0 | 0 | 113.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.87 | 0 | 7918.87 | 366750 | -24579.3 | 56 | 69 | 366750 | -1024579.3
9 | 2 | 14 | 6 | 5.4733 | 0 | 42.7453 | 0 | 10.0135 | 0 | 8.8125 | 12.8287 | 0 | 0 | 0 | 0 | 79.8733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.38 | 0 | 7919.38 | 181292 | 0 | 55 | 67 | 181292 | -1000000
9 | 2 | 15 | 6 | 5.4741 | 0 | 42.7453 | 0 | 9.915 | 0 | 8.6499 | 12.8287 | 0 | 0 | 0 | 0 | 79.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.95 | 0 | 7919.95 | 177626 | 0 | 54 | 66 | 177626 | -1000000
9 | 2 | 16 | 6 | 5.4758 | 0 | 42.7453 | 0 | 7.2964 | 0 | 6.7221 | 8.818 | 0 | 0 | 0 | 1.2 | 72.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.37 | 0 | 7914.37 | 131986 | 0 | 55 | 65 | 131986 | -1000000
9 | 2 | 17 | 6 | 5.4779 | 0 | 42.7453 | 0 | 7.1096 | 0 | 6.6277 | 8.818 | 0 | 0 | 0 | 4.8 | 75.5786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7911.43 | 0 | 7911.43 | 131591 | 0 | 55 | 64 | 131591 | -1000000
9 | 2 | 18 | 6 | 5.5691 | 0 | 42.7453 | 0 | 7.0151 | 0 | 6.5714 | 8.818 | 0 | 0 | 0 | 7.2 | 77.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.74 | 0 | 7909.74 | 131340 | 0 | 55 | 63 | 131340 | -1000000
9 | 2 | 19 | 6 | 8.4599 | 0 | 42.7453 | 0 | 6.0854 | 0 | 6.1675 | 8.818 | 0 | 0 | 0 | 7.2 | 79.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.54 | 0 | 7908.54 | 131098 | 0 | 55 | 60 | 131098 | -1000000
9 | 2 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5586 | 0 | 5.4832 | 8.818 | 0 | 0 | 0 | 7.2 | 79.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.01 | 0 | 7908.01 | 130638 | 0 | 54 | 57 | 130638 | -1000000
9 | 2 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5364 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 7.2 | 79.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.73 | 0 | 7907.73 | 130151 | 0 | 52 | 54 | 130151 | -1000000
9 | 2 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5251 | 0 | 5.4836 | 8.818 | 0 | 0 | 0 | 6.4 | 78.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.66 | 0 | 7907.66 | 129908 | 0 | 52 | 53 | 129908 | -1000000
9 | 2 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5037 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 5.6 | 77.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.72 | 0 | 7907.72 | 129437 | 0 | 51 | 52 | 129437 | -1000000
9 | 2 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.4821 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.36 | 0 | 3098.36 | 128965 | 0 | 50 | 51 | 128965 | -1000000
9 | 3 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4634 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.56 | 0 | 3098.56 | 128555 | 0 | 49 | 50 | 128555 | -1000000
9 | 3 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4472 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.48 | 0 | 3099.48 | 128203 | 0 | 48 | 48 | 128203 | -1000000
9 | 3 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4267 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.41 | 0 | 3100.41 | 127752 | 0 | 47 | 47 | 127752 | -1000000
9 | 3 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4097 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 73.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.56 | 0 | 3101.56 | 127380 | 0 | 46 | 46 | 127380 | -1000000
9 | 3 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.6951 | 0 | 5.8972 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.78 | 0 | 3102.78 | 127118 | -7746.28 | 46 | 46 | 127118 | -1007746.28
9 | 3 | 6 | 7 | 5.0719 | 0 | 42.7453 | 0 | 6.3771 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 2.4 | 70.8973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.11 | 0 | 3104.11 | 126666 | 0 | 45 | 45 | 126666 | -1000000
9 | 3 | 7 | 7 | 3.9021 | 0 | 42.7453 | 0 | 6.6512 | 0 | 5.9005 | 12.8287 | 0 | 0 | 0 | 0.8 | 72.8278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.46 | 0 | 3105.46 | 132775 | -1438.7 | 49 | 50 | 132775 | -1001438.7
9 | 3 | 8 | 7 | 3.7862 | 0 | 42.7453 | 0 | 6.3788 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 0 | 67.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.76 | 0 | 3106.76 | 126609 | 0 | 53 | 54 | 126609 | -1000000
9 | 3 | 9 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.3663 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 0 | 67.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.81 | 0 | 3107.81 | 126436 | 0 | 56 | 59 | 126436 | -1000000
9 | 3 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 6.9431 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 0 | 68.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.97 | 0 | 3107.97 | 126225 | 0 | 57 | 62 | 126225 | -1000000
9 | 3 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 7.3223 | 0 | 7.0317 | 8.818 | 0 | 0 | 0 | 0 | 70.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.75 | 0 | 3107.75 | 125982 | 0 | 57 | 65 | 125982 | -1000000
9 | 3 | 12 | 7 | 4.144 | 0 | 42.7453 | 0 | 9.4372 | 0 | 8.4493 | 12.8287 | 0 | 0 | 0 | 0 | 77.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.21 | 0 | 3106.21 | 149568 | 0 | 57 | 68 | 149568 | -1000000
9 | 3 | 13 | 7 | 4.147 | 0 | 42.7453 | 0 | 9.0368 | 0 | 8.0199 | 12.8287 | 0 | 0 | 0 | 0 | 76.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.45 | 0 | 3105.45 | 164743 | 0 | 56 | 67 | 164743 | -1000000
9 | 3 | 14 | 7 | 4.1494 | 0 | 42.7453 | 0 | 9.2515 | 0 | 8.2102 | 12.8287 | 0 | 0 | 0 | 0 | 77.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.46 | 0 | 3104.46 | 162926 | 0 | 55 | 67 | 162926 | -1000000
9 | 3 | 15 | 7 | 4.5374 | 0 | 42.7453 | 0 | 6.9261 | 0 | 6.5687 | 8.818 | 0 | 0 | 0 | 0 | 69.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.29 | 0 | 3103.29 | 125704 | 0 | 54 | 66 | 125704 | -1000000
9 | 3 | 16 | 7 | 4.6995 | 0 | 42.7453 | 0 | 6.8404 | 0 | 6.5147 | 8.818 | 0 | 0 | 0 | 1.2 | 70.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.25 | 0 | 3102.25 | 126019 | 0 | 55 | 65 | 126019 | -1000000
9 | 3 | 17 | 7 | 4.8274 | 0 | 42.7453 | 0 | 6.7411 | 0 | 6.4654 | 8.818 | 0 | 0 | 0 | 4.8 | 74.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.63 | 0 | 3101.63 | 126020 | 0 | 56 | 64 | 126020 | -1000000
9 | 3 | 18 | 7 | 5.6483 | 0 | 42.7453 | 0 | 6.1841 | 0 | 5.5854 | 8.818 | 0 | 0 | 0 | 7.2 | 76.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.07 | 0 | 3101.07 | 125912 | 0 | 56 | 63 | 125912 | -1000000
9 | 3 | 19 | 7 | 6.494 | 0 | 42.7453 | 0 | 5.8588 | 0 | 5.4914 | 8.818 | 0 | 0 | 0 | 7.2 | 76.6076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.69 | 0 | 3100.69 | 125886 | 0 | 56 | 61 | 125886 | -1000000
9 | 3 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0778 | 0 | 5.4887 | 8.818 | 0 | 0 | 0 | 7.2 | 76.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.42 | 0 | 3100.42 | 125736 | 0 | 55 | 58 | 125736 | -1000000
9 | 3 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3312 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.34 | 0 | 3100.34 | 125668 | 0 | 55 | 56 | 125668 | -1000000
9 | 3 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3192 | 0 | 5.4857 | 8.818 | 0 | 0 | 0 | 6.4 | 76.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.4 | 0 | 3100.4 | 125402 | 0 | 54 | 55 | 125402 | -1000000
9 | 3 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3115 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 5.6 | 75.6239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.59 | 0 | 3100.59 | 125236 | 0 | 53 | 53 | 125236 | -1000000
9 | 3 | 24 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3009 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.81 | 0 | 3100.81 | 125002 | 0 | 52 | 52 | 125002 | -1000000
9 | 4 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.2963 | 0 | 5.486 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.05 | 0 | 3101.05 | 124904 | 0 | 52 | 52 | 124904 | -1000000
9 | 4 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.2853 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.64 | 0 | 3101.64 | 124661 | 0 | 51 | 51 | 124661 | -1000000
9 | 4 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.2807 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.41 | 0 | 3102.41 | 124563 | 0 | 51 | 51 | 124563 | -1000000
9 | 4 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.2736 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.28 | 0 | 3103.28 | 124405 | 0 | 51 | 51 | 124405 | -1000000
9 | 4 | 5 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.8949 | 0 | 5.8988 | 12.8287 | 0 | 0 | 0 | 4.8 | 78.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.1 | 0 | 3104.1 | 138237 | -3210.54 | 50 | 50 | 138237 | -1003210.54
9 | 4 | 6 | 8 | 5.0319 | 0 | 42.7453 | 0 | 6.2653 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 2.4 | 70.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.87 | 0 | 3104.87 | 123990 | 0 | 50 | 50 | 123990 | -1000000
9 | 4 | 7 | 8 | 3.7755 | 0 | 42.7453 | 0 | 6.2562 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 0.8 | 67.8815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.45 | 0 | 3105.45 | 124030 | 0 | 52 | 53 | 124030 | -1000000
9 | 4 | 8 | 8 | 3.7873 | 0 | 42.7453 | 0 | 8.6648 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 73.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.4 | 0 | 3106.4 | 133533 | -4144.09 | 53 | 57 | 133533 | -1004144.09
9 | 4 | 9 | 8 | 4.1455 | 0 | 42.7453 | 0 | 6.261 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 0 | 67.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.13 | 0 | 3107.13 | 123973 | 0 | 55 | 60 | 123973 | -1000000
9 | 4 | 10 | 8 | 4.144 | 0 | 42.7453 | 0 | 6.8377 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 0 | 68.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.18 | 0 | 3107.18 | 123947 | 0 | 56 | 62 | 123947 | -1000000
9 | 4 | 11 | 8 | 4.144 | 0 | 42.7453 | 0 | 7.2339 | 0 | 6.9725 | 8.818 | 0 | 0 | 0 | 0 | 69.9136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.62 | 0 | 3106.62 | 124107 | 0 | 58 | 65 | 124107 | -1000000
9 | 4 | 12 | 8 | 4.144 | 0 | 42.7453 | 0 | 9.1966 | 0 | 8.5948 | 12.8287 | 0 | 0 | 0 | 0 | 77.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.92 | 0 | 3105.92 | 151677 | -1531.55 | 59 | 67 | 151677 | -1001531.55
9 | 4 | 13 | 8 | 4.1477 | 0 | 42.7453 | 0 | 9.5862 | 0 | 8.9421 | 12.8287 | 0 | 0 | 0 | 0 | 78.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.74 | 0 | 3104.74 | 169619 | -1031.96 | 60 | 67 | 169619 | -1001031.96
9 | 4 | 14 | 8 | 4.1487 | 0 | 42.7453 | 0 | 7.5874 | 0 | 6.9737 | 8.818 | 0 | 0 | 0 | 0 | 70.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.51 | 0 | 3103.51 | 124137 | 0 | 60 | 68 | 124137 | -1000000
9 | 4 | 15 | 8 | 4.1492 | 0 | 42.7453 | 0 | 9.4519 | 0 | 8.9153 | 12.8287 | 0 | 0 | 0 | 0 | 78.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.35 | 0 | 3102.35 | 168126 | -144.525 | 61 | 68 | 168126 | -1000144.525
9 | 4 | 16 | 8 | 4.15 | 0 | 42.7453 | 0 | 7.2019 | 0 | 6.7766 | 8.818 | 0 | 0 | 0 | 1.2 | 70.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.24 | 0 | 3101.24 | 124372 | 0 | 61 | 68 | 124372 | -1000000
9 | 4 | 17 | 8 | 4.1514 | 0 | 42.7453 | 0 | 6.7759 | 0 | 6.5406 | 8.818 | 0 | 0 | 0 | 4.8 | 73.8312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.48 | 0 | 3100.48 | 124495 | 0 | 61 | 67 | 124495 | -1000000
9 | 4 | 18 | 8 | 4.2402 | 0 | 42.7453 | 0 | 6.5243 | 0 | 5.6189 | 8.818 | 0 | 0 | 0 | 7.2 | 75.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.65 | 0 | 3099.65 | 124530 | 0 | 61 | 67 | 124530 | -1000000
9 | 4 | 19 | 8 | 6.3771 | 0 | 42.7453 | 0 | 5.6286 | 0 | 5.4936 | 8.818 | 0 | 0 | 0 | 7.2 | 76.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.94 | 0 | 3098.94 | 124517 | 0 | 60 | 64 | 124517 | -1000000
9 | 4 | 20 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.8241 | 0 | 5.4915 | 8.818 | 0 | 0 | 0 | 7.2 | 76.7421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.56 | 0 | 3098.56 | 124454 | 0 | 59 | 62 | 124454 | -1000000
9 | 4 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 5.7621 | 0 | 5.4935 | 8.818 | 0 | 0 | 0 | 7.2 | 76.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.37 | 0 | 3098.37 | 124444 | 0 | 58 | 59 | 124444 | -1000000
9 | 4 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.2808 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 6.4 | 76.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.4 | 0 | 3098.4 | 124570 | 0 | 59 | 59 | 124570 | -1000000
9 | 4 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.277 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 5.6 | 75.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.62 | 0 | 3098.62 | 124481 | 0 | 59 | 59 | 124481 | -1000000
9 | 4 | 24 | 8 | 10.424 | 0 | 42.3304 | 0 | 6.2832 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.5 | 0 | 7908.5 | 124621 | 0 | 58 | 59 | 124621 | -1000000
9 | 5 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.2912 | 0 | 5.486 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.9 | 0 | 7908.9 | 124797 | 0 | 59 | 59 | 124797 | -1000000
9 | 5 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.2866 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.48 | 0 | 7908.48 | 124691 | 0 | 59 | 59 | 124691 | -1000000
9 | 5 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.2843 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.5 | 0 | 7908.5 | 124643 | 0 | 59 | 59 | 124643 | -1000000
9 | 5 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 7.3912 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760.49 | 0 | 8760.49 | 149278 | -2273.01 | 59 | 59 | 149278 | -1002273.01
9 | 5 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 11.0341 | 0 | 5.9514 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656.9 | 0 | 10656.9 | 229973 | -2212.55 | 59 | 59 | 229973 | -1002212.55
9 | 5 | 6 | 2 | 48.7284 | 0 | 140.608 | 0 | 41.9271 | 0 | 6.332 | 20.0292 | 0 | 0 | 0 | 2.4 | 260.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28521.1 | 0 | 28521.1 | 631910 | -24575.7 | 59 | 59 | 631910 | -1024575.7
9 | 5 | 7 | 2 | 47.9815 | 0 | 168.222 | 0 | 48.5914 | 0 | 6.332 | 20.1223 | 0 | 0 | 0 | 0.8 | 292.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31265.8 | 0 | 31265.8 | 756829 | -18195.1 | 60 | 60 | 756829 | -1018195.1
9 | 5 | 8 | 2 | 40.596 | 0 | 173.795 | 0 | 46.2647 | 0 | 6.332 | 20.1078 | 0 | 0 | 0 | 0 | 287.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39521.6 | 0 | 39521.6 | 761119 | -16215.3 | 60 | 60 | 761119 | -1016215.3
9 | 5 | 9 | 2 | 41.5587 | 0 | 172.186 | 0 | 46.3444 | 0 | 6.332 | 20.3494 | 0 | 0 | 0 | 0 | 286.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61509.4 | 0 | 61509.4 | 793009 | -14557.1 | 60 | 61 | 793009 | -1014557.1
9 | 5 | 10 | 2 | 42.1543 | 0 | 163.102 | 0 | 49.1469 | 0 | 6.332 | 20.5079 | 0 | 0 | 0 | 0 | 281.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884 | 0 | 62884 | 833294 | -12981.1 | 61 | 63 | 833294 | -1012981.1
9 | 5 | 11 | 2 | 41.0682 | 0 | 149.692 | 0 | 45.3732 | 0 | 6.332 | 20.6598 | 0 | 0 | 0 | 0 | 263.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884 | 0 | 62884 | 791322 | -9843.79 | 62 | 64 | 791322 | -1009843.79
9 | 5 | 12 | 2 | 39.847 | 0 | 150.207 | 0 | 48.2334 | 0 | 6.332 | 21.1324 | 0 | 0 | 0 | 0 | 265.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.3 | 0 | 62884.3 | 840803 | -9079.24 | 63 | 66 | 840803 | -1009079.24
9 | 5 | 13 | 2 | 41.2755 | 0 | 165.698 | 0 | 62.1652 | 0 | 6.332 | 21.8729 | 0 | 0 | 0 | 0 | 297.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.7 | 0 | 62884.7 | 1032770 | -9197.8 | 65 | 70 | 1032770 | -1009197.8
9 | 5 | 14 | 2 | 40.6513 | 0 | 172.702 | 0 | 72.8915 | 0 | 6.332 | 22.2758 | 0 | 0 | 0 | 0 | 314.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61510.5 | 0 | 61510.5 | 1182250 | -12788.9 | 67 | 73 | 1182250 | -1012788.9
9 | 5 | 15 | 2 | 40.5494 | 0 | 173.986 | 0 | 83.2027 | 0 | 6.332 | 22.771 | 0 | 0 | 0 | 0 | 326.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56013 | 0 | 56013 | 1325290 | -13183.9 | 69 | 77 | 1325290 | -1013183.9
9 | 5 | 16 | 2 | 40.313 | 0 | 169.782 | 0 | 79.8956 | 0 | 6.332 | 22.9338 | 0 | 0 | 0 | 1.2 | 320.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46393.5 | 0 | 46393.5 | 1325650 | -12783.4 | 68 | 75 | 1325650 | -1012783.4
9 | 5 | 17 | 2 | 35.5019 | 0 | 152.497 | 0 | 65.0632 | 0 | 6.332 | 22.6526 | 0 | 0 | 0 | 4.8 | 286.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35399.7 | 0 | 35399.7 | 1162050 | -10157.8 | 67 | 72 | 1162050 | -1010157.8
9 | 5 | 18 | 2 | 25.0124 | 0 | 93.4203 | 0 | 38.3758 | 0 | 6.332 | 20.4594 | 0 | 0 | 0 | 7.2 | 190.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21657.8 | 0 | 21657.8 | 775119 | -7221.37 | 67 | 70 | 775119 | -1007221.37
9 | 5 | 19 | 2 | 23.526 | 0 | 62.7906 | 0 | 9.173 | 0 | 5.4962 | 8.818 | 0 | 0 | 0 | 7.2 | 117.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15473.7 | 0 | 15473.7 | 187382 | 0 | 65 | 67 | 187382 | -1000000
9 | 5 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 7.6444 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 102.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14788.3 | 0 | 14788.3 | 167364 | 0 | 63 | 64 | 167364 | -1000000
9 | 5 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 6.9073 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 91.1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9279.49 | 0 | 9279.49 | 154105 | 0 | 61 | 61 | 154105 | -1000000
9 | 5 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.495 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9057.81 | 0 | 9057.81 | 143621 | 0 | 62 | 62 | 143621 | -1000000
9 | 5 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.615 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 5.6 | 80.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.7 | 0 | 7901.7 | 138917 | 0 | 63 | 64 | 138917 | -1000000
9 | 5 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.3314 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.55 | 0 | 7901.55 | 137646 | 0 | 64 | 65 | 137646 | -1000000
9 | 6 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.021 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.25 | 0 | 7901.25 | 136652 | 0 | 63 | 65 | 136652 | -1000000
9 | 6 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6984 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.26 | 0 | 7901.26 | 136196 | 0 | 63 | 64 | 136196 | -1000000
9 | 6 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.9224 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.11 | 0 | 7901.11 | 135374 | 0 | 62 | 64 | 135374 | -1000000
9 | 6 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.079 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8752.94 | 0 | 8752.94 | 138799 | 0 | 61 | 64 | 138799 | -1000000
9 | 6 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 12.2212 | 0 | 5.5891 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649.2 | 0 | 10649.2 | 250813 | 0 | 61 | 64 | 250813 | -1000000
9 | 6 | 6 | 3 | 48.8804 | 0 | 140.608 | 0 | 44.8438 | 0 | 6.332 | 21.2468 | 0 | 0 | 0 | 2.4 | 264.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28513.1 | 0 | 28513.1 | 795987 | -9442.57 | 60 | 64 | 795987 | -1009442.57
9 | 6 | 7 | 3 | 47.464 | 0 | 168.222 | 0 | 50.5751 | 0 | 6.5657 | 21.1063 | 0 | 0 | 0 | 0.8 | 294.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31257.5 | 0 | 31257.5 | 882190 | -15951.8 | 60 | 64 | 882190 | -1015951.8
9 | 6 | 8 | 3 | 41.5159 | 0 | 173.795 | 0 | 49.2395 | 0 | 25.335 | 21.0403 | 0 | 0 | 0 | 0 | 310.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39517.6 | 0 | 39517.6 | 886376 | -17789.8 | 60 | 65 | 886376 | -1017789.8
9 | 6 | 9 | 3 | 41.4725 | 0 | 172.186 | 0 | 49.52 | 0 | 25.335 | 21.3472 | 0 | 0 | 0 | 0 | 309.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61506.2 | 0 | 61506.2 | 903638 | -18731.2 | 60 | 65 | 903638 | -1018731.2
9 | 6 | 10 | 3 | 42.0539 | 0 | 163.102 | 0 | 55.2075 | 0 | 25.335 | 21.4197 | 0 | 0 | 0 | 0 | 307.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.9 | 0 | 62880.9 | 970337 | -15851.9 | 62 | 68 | 970337 | -1015851.9
9 | 6 | 11 | 3 | 41.1782 | 0 | 149.692 | 0 | 54.468 | 0 | 25.335 | 21.5911 | 0 | 0 | 0 | 0 | 292.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.2 | 0 | 62881.2 | 944208 | -12312.5 | 64 | 70 | 944208 | -1012312.5
9 | 6 | 12 | 3 | 39.8707 | 0 | 150.207 | 0 | 61.5491 | 0 | 25.335 | 22.2513 | 0 | 0 | 0 | 0 | 299.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.5 | 0 | 62881.5 | 1037160 | -10495.6 | 66 | 73 | 1037160 | -1010495.6
9 | 6 | 13 | 3 | 41.26 | 0 | 165.698 | 0 | 73.3997 | 0 | 25.335 | 23.2831 | 0 | 0 | 0 | 0 | 328.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882 | 0 | 62882 | 1218710 | -13420.1 | 67 | 75 | 1218710 | -1013420.1
9 | 6 | 14 | 3 | 40.6426 | 0 | 172.702 | 0 | 76.826 | 0 | 25.335 | 23.2254 | 0 | 0 | 0 | 0 | 338.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61507.9 | 0 | 61507.9 | 1279200 | -16232.5 | 67 | 76 | 1279200 | -1016232.5
9 | 6 | 15 | 3 | 40.5377 | 0 | 173.986 | 0 | 84.1375 | 0 | 25.335 | 23.199 | 0 | 0 | 0 | 0 | 347.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56011.2 | 0 | 56011.2 | 1400630 | -17427 | 68 | 78 | 1400630 | -1017427
9 | 6 | 16 | 3 | 40.3136 | 0 | 169.782 | 0 | 78.7975 | 0 | 25.335 | 23.3021 | 0 | 0 | 0 | 1.2 | 338.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46391.6 | 0 | 46391.6 | 1331870 | -16678.4 | 67 | 77 | 1331870 | -1016678.4
9 | 6 | 17 | 3 | 35.5215 | 0 | 152.497 | 0 | 70.0131 | 0 | 25.335 | 23.1661 | 0 | 0 | 0 | 4.8 | 311.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35398.5 | 0 | 35398.5 | 1205500 | -13524.5 | 67 | 75 | 1205500 | -1013524.5
9 | 6 | 18 | 3 | 31.2731 | 0 | 93.4203 | 0 | 45.2993 | 0 | 25.335 | 20.8119 | 0 | 0 | 0 | 7.2 | 223.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21656.2 | 0 | 21656.2 | 804933 | -9647.75 | 66 | 74 | 804933 | -1009647.75
9 | 6 | 19 | 3 | 24.042 | 0 | 62.7906 | 0 | 11.2812 | 0 | 11.1467 | 8.818 | 0 | 0 | 0 | 7.2 | 125.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15472.1 | 0 | 15472.1 | 192819 | 0 | 67 | 73 | 192819 | -1000000
9 | 6 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.9802 | 0 | 8.6586 | 8.818 | 0 | 0 | 0 | 7.2 | 107.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14786.5 | 0 | 14786.5 | 172461 | 0 | 67 | 72 | 172461 | -1000000
9 | 6 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 8.1037 | 0 | 5.4835 | 8.818 | 0 | 0 | 0 | 7.2 | 92.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9276.76 | 0 | 9276.76 | 159268 | 0 | 68 | 71 | 159268 | -1000000
9 | 6 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.8361 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 6.4 | 84.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9054.57 | 0 | 9054.57 | 148178 | 0 | 67 | 71 | 148178 | -1000000
9 | 6 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.2751 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 5.6 | 80.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7898.02 | 0 | 7898.02 | 143237 | 0 | 67 | 70 | 143237 | -1000000
9 | 6 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.4704 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7897.47 | 0 | 7897.47 | 141723 | 0 | 67 | 70 | 141723 | -1000000
9 | 7 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8025 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.96 | 0 | 7896.96 | 140784 | 0 | 66 | 68 | 140784 | -1000000
9 | 7 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9885 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.5 | 0 | 7896.5 | 139908 | 0 | 65 | 67 | 139908 | -1000000
9 | 7 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.6082 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.03 | 0 | 7896.03 | 139089 | 0 | 64 | 65 | 139089 | -1000000
9 | 7 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.6682 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8747.6 | 0 | 8747.6 | 142003 | 0 | 62 | 63 | 142003 | -1000000
9 | 7 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 12.0196 | 0 | 5.5715 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10643.6 | 0 | 10643.6 | 262066 | 0 | 60 | 61 | 262066 | -1000000
9 | 7 | 6 | 4 | 48.6926 | 0 | 140.608 | 0 | 39.6599 | 0 | 25.335 | 21.4822 | 0 | 0 | 0 | 2.4 | 278.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28507.5 | 0 | 28507.5 | 801994 | -7801.17 | 58 | 59 | 801994 | -1007801.17
9 | 7 | 7 | 4 | 41.1297 | 0 | 168.222 | 0 | 49.8652 | 0 | 25.335 | 21.1983 | 0 | 0 | 0 | 0.8 | 306.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31251.9 | 0 | 31251.9 | 938653 | -22734 | 60 | 61 | 938653 | -1022734
9 | 7 | 8 | 4 | 39.8285 | 0 | 173.795 | 0 | 51.9337 | 0 | 25.335 | 21.7197 | 0 | 0 | 0 | 0 | 312.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39514.6 | 0 | 39514.6 | 966576 | -22516.9 | 61 | 62 | 966576 | -1022516.9
9 | 7 | 9 | 4 | 40.8068 | 0 | 172.186 | 0 | 53.6554 | 0 | 25.335 | 21.9333 | 0 | 0 | 0 | 0 | 313.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61504.2 | 0 | 61504.2 | 974891 | -23054.8 | 61 | 64 | 974891 | -1023054.8
9 | 7 | 10 | 4 | 41.1687 | 0 | 163.102 | 0 | 58.5634 | 0 | 25.335 | 22.2173 | 0 | 0 | 0 | 0 | 310.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62879 | 0 | 62879 | 1050010 | -19858.6 | 63 | 66 | 1050010 | -1019858.6
9 | 7 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 58.4158 | 0 | 25.335 | 22.5261 | 0 | 0 | 0 | 0 | 296.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62879.2 | 0 | 62879.2 | 1031070 | -15501.5 | 64 | 69 | 1031070 | -1015501.5
9 | 7 | 12 | 4 | 39.7554 | 0 | 150.207 | 0 | 65.7363 | 0 | 25.335 | 21.4896 | 0 | 0 | 0 | 0 | 302.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62879.6 | 0 | 62879.6 | 1136400 | -32552.2 | 64 | 71 | 1136400 | -1032552.2
9 | 7 | 13 | 4 | 41.2858 | 0 | 165.698 | 0 | 69.2847 | 0 | 25.335 | 22.6111 | 0 | 0 | 0 | 0 | 324.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.4 | 0 | 62881.4 | 1203180 | -16096.6 | 65 | 71 | 1203180 | -1016096.6
9 | 7 | 14 | 4 | 40.6608 | 0 | 172.702 | 0 | 72.4824 | 0 | 25.335 | 22.4132 | 0 | 0 | 0 | 0 | 333.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61508.2 | 0 | 61508.2 | 1241000 | -19705.4 | 65 | 72 | 1241000 | -1019705.4
9 | 7 | 15 | 4 | 40.5639 | 0 | 173.986 | 0 | 72.9973 | 0 | 25.335 | 22.5973 | 0 | 0 | 0 | 0 | 335.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56011.5 | 0 | 56011.5 | 1256660 | -21413.8 | 65 | 72 | 1256660 | -1021413.8
9 | 7 | 16 | 4 | 40.318 | 0 | 169.782 | 0 | 68.1928 | 0 | 25.335 | 22.5809 | 0 | 0 | 0 | 1.2 | 327.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46392 | 0 | 46392 | 1219530 | -21220.1 | 64 | 70 | 1219530 | -1021220.1
9 | 7 | 17 | 4 | 35.6503 | 0 | 152.497 | 0 | 57.5645 | 0 | 25.335 | 22.5598 | 0 | 0 | 0 | 4.8 | 298.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35397.8 | 0 | 35397.8 | 1059190 | -18304.4 | 64 | 68 | 1059190 | -1018304.4
9 | 7 | 18 | 4 | 25.738 | 0 | 93.4203 | 0 | 37.0153 | 0 | 25.335 | 20.0977 | 0 | 0 | 0 | 7.2 | 208.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21655.7 | 0 | 21655.7 | 694839 | -14810.6 | 63 | 66 | 694839 | -1014810.6
9 | 7 | 19 | 4 | 24.036 | 0 | 62.7906 | 0 | 10.7357 | 0 | 9.7244 | 8.818 | 0 | 0 | 0 | 7.2 | 123.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15471.2 | 0 | 15471.2 | 193257 | 0 | 62 | 65 | 193257 | -1000000
9 | 7 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.8468 | 0 | 7.7854 | 8.818 | 0 | 0 | 0 | 7.2 | 106.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14785.9 | 0 | 14785.9 | 173363 | 0 | 61 | 63 | 173363 | -1000000
9 | 7 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 8.1582 | 0 | 7.3375 | 8.818 | 0 | 0 | 0 | 7.2 | 94.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9276.73 | 0 | 9276.73 | 159619 | 0 | 59 | 62 | 159619 | -1000000
9 | 7 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.4993 | 0 | 6.9064 | 8.818 | 0 | 0 | 0 | 6.4 | 85.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9055.19 | 0 | 9055.19 | 148652 | 0 | 59 | 61 | 148652 | -1000000
9 | 7 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.2102 | 0 | 6.7127 | 8.818 | 0 | 0 | 0 | 5.6 | 81.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.25 | 0 | 7899.25 | 143524 | 0 | 58 | 60 | 143524 | -1000000
9 | 7 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.3962 | 0 | 6.8196 | 8.818 | 0 | 0 | 0 | 4.8 | 81.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.38 | 0 | 7899.38 | 141860 | 0 | 57 | 59 | 141860 | -1000000
9 | 8 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.3407 | 0 | 6.7872 | 8.818 | 0 | 0 | 0 | 4.8 | 80.9253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.55 | 0 | 7899.55 | 140706 | 0 | 55 | 57 | 140706 | -1000000
9 | 8 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2986 | 0 | 6.7629 | 8.818 | 0 | 0 | 0 | 4.8 | 80.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.8 | 0 | 7899.8 | 139830 | 0 | 54 | 56 | 139830 | -1000000
9 | 8 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.2579 | 0 | 6.7397 | 8.818 | 0 | 0 | 0 | 4.8 | 80.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.07 | 0 | 7900.07 | 138979 | 0 | 53 | 54 | 138979 | -1000000
9 | 8 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.3892 | 0 | 6.8155 | 8.818 | 0 | 0 | 0 | 4.8 | 84.4672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8752.47 | 0 | 8752.47 | 141787 | 0 | 52 | 53 | 141787 | -1000000
9 | 8 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.2117 | 0 | 10.3319 | 12.8287 | 0 | 0 | 0 | 4.8 | 133.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649.3 | 0 | 10649.3 | 223117 | 0 | 51 | 51 | 223117 | -1000000
9 | 8 | 6 | 5 | 48.403 | 0 | 140.608 | 0 | 21.9155 | 0 | 6.332 | 19.6642 | 0 | 0 | 0 | 2.4 | 239.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28514 | 0 | 28514 | 407130 | -15606.6 | 49 | 50 | 407130 | -1015606.6
9 | 8 | 7 | 5 | 39.8603 | 0 | 168.222 | 0 | 30.8755 | 0 | 25.335 | 19.6219 | 0 | 0 | 0 | 0.8 | 284.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31259.2 | 0 | 31259.2 | 556131 | -38085.8 | 51 | 53 | 556131 | -1038085.8
9 | 8 | 8 | 5 | 39.8747 | 0 | 173.795 | 0 | 34.698 | 0 | 25.335 | 19.9565 | 0 | 0 | 0 | 0 | 293.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39518 | 0 | 39518 | 654458 | -33049 | 53 | 57 | 654458 | -1033049
9 | 8 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 39.3771 | 0 | 25.335 | 20.3926 | 0 | 0 | 0 | 0 | 297.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61506.4 | 0 | 61506.4 | 736582 | -27919.6 | 54 | 60 | 736582 | -1027919.6
9 | 8 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 44.1749 | 0 | 25.335 | 21.0297 | 0 | 0 | 0 | 0 | 294.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882 | 0 | 62882 | 792223 | -22365.6 | 55 | 63 | 792223 | -1022365.6
9 | 8 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 44.6113 | 0 | 25.335 | 21.3244 | 0 | 0 | 0 | 0 | 281.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62883.2 | 0 | 62883.2 | 788208 | -21107.6 | 56 | 65 | 788208 | -1021107.6
9 | 8 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 50.2673 | 0 | 25.335 | 20.7136 | 0 | 0 | 0 | 0 | 286.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62883.5 | 0 | 62883.5 | 861906 | -39789.1 | 56 | 68 | 861906 | -1039789.1
9 | 8 | 13 | 5 | 41.2878 | 0 | 165.698 | 0 | 54.6978 | 0 | 25.335 | 21.7528 | 0 | 0 | 0 | 0 | 308.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884 | 0 | 62884 | 945572 | -21519.8 | 57 | 69 | 945572 | -1021519.8
9 | 8 | 14 | 5 | 40.6778 | 0 | 172.702 | 0 | 57.0879 | 0 | 25.335 | 21.882 | 0 | 0 | 0 | 0 | 317.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61510.3 | 0 | 61510.3 | 994087 | -20168.6 | 57 | 69 | 994087 | -1020168.6
9 | 8 | 15 | 5 | 40.5787 | 0 | 173.986 | 0 | 61.6549 | 0 | 25.335 | 21.9812 | 0 | 0 | 0 | 0 | 323.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56013.8 | 0 | 56013.8 | 1061230 | -22757 | 58 | 70 | 1061230 | -1022757
9 | 8 | 16 | 5 | 40.3311 | 0 | 169.782 | 0 | 56.1869 | 0 | 25.335 | 22.0297 | 0 | 0 | 0 | 1.2 | 314.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46394.3 | 0 | 46394.3 | 1001890 | -21551.4 | 57 | 69 | 1001890 | -1021551.4
9 | 8 | 17 | 5 | 35.5089 | 0 | 152.497 | 0 | 47.5147 | 0 | 25.335 | 21.7717 | 0 | 0 | 0 | 4.8 | 287.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35400.4 | 0 | 35400.4 | 874615 | -18826.7 | 57 | 67 | 874615 | -1018826.7
9 | 8 | 18 | 5 | 25.3259 | 0 | 93.4203 | 0 | 29.6646 | 0 | 25.335 | 19.9443 | 0 | 0 | 0 | 7.2 | 200.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21657.9 | 0 | 21657.9 | 552438 | -14747 | 56 | 66 | 552438 | -1014747
9 | 8 | 19 | 5 | 23.6545 | 0 | 62.7906 | 0 | 9.235 | 0 | 7.9928 | 8.818 | 0 | 0 | 0 | 7.2 | 119.691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15473.3 | 0 | 15473.3 | 193086 | 0 | 55 | 61 | 193086 | -1000000
9 | 8 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 9.0316 | 0 | 7.779 | 8.818 | 0 | 0 | 0 | 7.2 | 106.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14787.7 | 0 | 14787.7 | 172899 | 0 | 53 | 57 | 172899 | -1000000
9 | 8 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 8.3721 | 0 | 7.4076 | 8.818 | 0 | 0 | 0 | 7.2 | 94.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9279.25 | 0 | 9279.25 | 159418 | 0 | 51 | 52 | 159418 | -1000000
9 | 8 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.3601 | 0 | 5.4959 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9058.03 | 0 | 9058.03 | 147998 | 0 | 49 | 50 | 147998 | -1000000
9 | 8 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1329 | 0 | 5.4911 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.54 | 0 | 7902.54 | 143134 | 0 | 48 | 48 | 143134 | -1000000
9 | 8 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0332 | 0 | 5.4892 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.11 | 0 | 7903.11 | 140996 | 0 | 46 | 46 | 140996 | -1000000
9 | 9 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9891 | 0 | 5.4884 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.46 | 0 | 7903.46 | 140052 | 0 | 46 | 46 | 140052 | -1000000
9 | 9 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9402 | 0 | 5.4876 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7904.55 | 0 | 7904.55 | 138979 | 0 | 45 | 45 | 138979 | -1000000
9 | 9 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8997 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7905.31 | 0 | 7905.31 | 138096 | 0 | 45 | 45 | 138096 | -1000000
9 | 9 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8588 | 0 | 5.4863 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7906.03 | 0 | 7906.03 | 137201 | 0 | 45 | 45 | 137201 | -1000000
9 | 9 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8203 | 0 | 5.4857 | 8.818 | 0 | 0 | 0 | 4.8 | 75.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7906.75 | 0 | 7906.75 | 136360 | 0 | 45 | 45 | 136360 | -1000000
9 | 9 | 6 | 6 | 6.3251 | 0 | 42.7453 | 0 | 7.3941 | 0 | 6.7086 | 8.818 | 0 | 0 | 0 | 2.4 | 74.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.43 | 0 | 7907.43 | 135556 | 0 | 45 | 45 | 135556 | -1000000
9 | 9 | 7 | 6 | 4.8775 | 0 | 42.7453 | 0 | 12.3432 | 0 | 5.9287 | 18.8896 | 0 | 0 | 0 | 0.8 | 85.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.09 | 0 | 7908.09 | 184371 | -28719.6 | 47 | 48 | 184371 | -1028719.6
9 | 9 | 8 | 6 | 4.9479 | 0 | 42.7453 | 0 | 15.0288 | 0 | 6.0472 | 18.8896 | 0 | 0 | 0 | 0 | 87.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.58 | 0 | 7908.58 | 230080 | -78971.6 | 50 | 50 | 230080 | -1078971.6
9 | 9 | 9 | 6 | 5.4754 | 0 | 42.7453 | 0 | 17.6722 | 0 | 17.8116 | 18.8896 | 0 | 0 | 0 | 0 | 102.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.23 | 0 | 7918.23 | 272212 | -96142.1 | 52 | 53 | 272212 | -1096142.1
9 | 9 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 16.891 | 0 | 6.1208 | 18.8896 | 0 | 0 | 0 | 0 | 90.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.52 | 0 | 7919.52 | 273841 | -51680.4 | 55 | 59 | 273841 | -1051680.4
9 | 9 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 20.8098 | 0 | 25.335 | 18.9246 | 0 | 0 | 0 | 0 | 113.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.41 | 0 | 7920.41 | 328667 | -35542.8 | 58 | 65 | 328667 | -1035542.8
9 | 9 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 25.3143 | 0 | 25.335 | 18.955 | 0 | 0 | 0 | 0 | 117.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.78 | 0 | 7920.78 | 409337 | -40488 | 60 | 71 | 409337 | -1040488
9 | 9 | 13 | 6 | 5.4764 | 0 | 42.7453 | 0 | 26.5543 | 0 | 25.335 | 19.0604 | 0 | 0 | 0 | 0 | 119.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.14 | 0 | 7921.14 | 452327 | -38197 | 61 | 72 | 452327 | -1038197
9 | 9 | 14 | 6 | 5.4768 | 0 | 42.7453 | 0 | 11.7812 | 0 | 11.394 | 12.8287 | 0 | 0 | 0 | 0 | 84.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.64 | 0 | 7921.64 | 186305 | 0 | 62 | 73 | 186305 | -1000000
9 | 9 | 15 | 6 | 5.4751 | 0 | 42.7453 | 0 | 11.624 | 0 | 11.2279 | 12.8287 | 0 | 0 | 0 | 0 | 83.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7922.06 | 0 | 7922.06 | 186109 | 0 | 62 | 74 | 186109 | -1000000
9 | 9 | 16 | 6 | 5.476 | 0 | 42.7453 | 0 | 10.5199 | 0 | 9.7064 | 12.8287 | 0 | 0 | 0 | 1.2 | 82.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7916.86 | 0 | 7916.86 | 188599 | 0 | 62 | 72 | 188599 | -1000000
9 | 9 | 17 | 6 | 5.4792 | 0 | 42.7453 | 0 | 7.1465 | 0 | 6.7557 | 8.818 | 0 | 0 | 0 | 4.8 | 75.7447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.62 | 0 | 7913.62 | 130904 | 0 | 61 | 70 | 130904 | -1000000
9 | 9 | 18 | 6 | 5.8796 | 0 | 42.7453 | 0 | 6.8975 | 0 | 6.6084 | 8.818 | 0 | 0 | 0 | 7.2 | 78.1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7911.56 | 0 | 7911.56 | 130696 | 0 | 60 | 68 | 130696 | -1000000
9 | 9 | 19 | 6 | 8.6679 | 0 | 42.7453 | 0 | 6.5038 | 0 | 6.3486 | 8.818 | 0 | 0 | 0 | 7.2 | 80.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.95 | 0 | 7909.95 | 130485 | 0 | 59 | 65 | 130485 | -1000000
9 | 9 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.1608 | 0 | 6.3147 | 8.818 | 0 | 0 | 0 | 7.2 | 80.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.16 | 0 | 7909.16 | 130186 | 0 | 58 | 63 | 130186 | -1000000
9 | 9 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.7547 | 0 | 5.4936 | 8.818 | 0 | 0 | 0 | 7.2 | 78.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.7 | 0 | 7908.7 | 129890 | 0 | 57 | 60 | 129890 | -1000000
9 | 9 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.8032 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 6.4 | 79.0447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.63 | 0 | 7908.63 | 129597 | 0 | 57 | 61 | 129597 | -1000000
9 | 9 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.534 | 0 | 5.4831 | 8.818 | 0 | 0 | 0 | 5.6 | 77.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.7 | 0 | 7908.7 | 129353 | 0 | 57 | 61 | 129353 | -1000000
9 | 9 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.8105 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 73.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.41 | 0 | 3099.41 | 128967 | 0 | 57 | 62 | 128967 | -1000000
9 | 10 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.5392 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.62 | 0 | 3099.62 | 128707 | 0 | 57 | 62 | 128707 | -1000000
9 | 10 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2283 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.99 | 0 | 3099.99 | 128308 | 0 | 56 | 61 | 128308 | -1000000
9 | 10 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4707 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.23 | 0 | 3100.23 | 127974 | 0 | 55 | 61 | 127974 | -1000000
9 | 10 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.1756 | 0 | 5.4874 | 8.818 | 0 | 0 | 0 | 4.8 | 73.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.48 | 0 | 3100.48 | 127877 | 0 | 55 | 60 | 127877 | -1000000
9 | 10 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4135 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.78 | 0 | 3100.78 | 127464 | 0 | 54 | 60 | 127464 | -1000000
9 | 10 | 6 | 7 | 5.0752 | 0 | 42.7453 | 0 | 6.4092 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 2.4 | 70.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.11 | 0 | 3101.11 | 127375 | 0 | 54 | 59 | 127375 | -1000000
9 | 10 | 7 | 7 | 4.1981 | 0 | 42.7453 | 0 | 6.3991 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 0.8 | 68.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.51 | 0 | 3101.51 | 127151 | 0 | 54 | 59 | 127151 | -1000000
9 | 10 | 8 | 7 | 3.987 | 0 | 42.7453 | 0 | 6.3934 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 0 | 67.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.96 | 0 | 3101.96 | 127030 | 0 | 55 | 60 | 127030 | -1000000
9 | 10 | 9 | 7 | 4.4699 | 0 | 42.7453 | 0 | 6.3823 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 0 | 67.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.43 | 0 | 3102.43 | 126784 | 0 | 55 | 60 | 126784 | -1000000
9 | 10 | 10 | 7 | 4.5767 | 0 | 42.7453 | 0 | 6.9639 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 0 | 68.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.67 | 0 | 3102.67 | 126677 | 0 | 56 | 62 | 126677 | -1000000
9 | 10 | 11 | 7 | 4.5692 | 0 | 42.7453 | 0 | 7.0429 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 0 | 68.6545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.5 | 0 | 3102.5 | 126741 | 0 | 58 | 64 | 126741 | -1000000
9 | 10 | 12 | 7 | 4.399 | 0 | 42.7453 | 0 | 7.1136 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.5546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.31 | 0 | 3102.31 | 126562 | 0 | 59 | 66 | 126562 | -1000000
9 | 10 | 13 | 7 | 4.4388 | 0 | 42.7453 | 0 | 6.5847 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 0 | 68.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3102.06 | 0 | 3102.06 | 126591 | 0 | 60 | 66 | 126591 | -1000000
9 | 10 | 14 | 7 | 4.4103 | 0 | 42.7453 | 0 | 6.4137 | 0 | 6.4417 | 8.818 | 0 | 0 | 0 | 0 | 68.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.73 | 0 | 3101.73 | 126414 | 0 | 60 | 65 | 126414 | -1000000
9 | 10 | 15 | 7 | 4.5735 | 0 | 42.7453 | 0 | 6.7566 | 0 | 6.5991 | 8.818 | 0 | 0 | 0 | 0 | 69.4925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.1 | 0 | 3101.1 | 126445 | 0 | 61 | 65 | 126445 | -1000000
9 | 10 | 16 | 7 | 4.7201 | 0 | 42.7453 | 0 | 6.5278 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 1.2 | 69.4932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100.54 | 0 | 3100.54 | 126159 | 0 | 60 | 65 | 126159 | -1000000
9 | 10 | 17 | 7 | 4.9531 | 0 | 42.7453 | 0 | 6.23 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 4.8 | 73.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.97 | 0 | 3099.97 | 126170 | 0 | 60 | 64 | 126170 | -1000000
9 | 10 | 18 | 7 | 5.6972 | 0 | 42.7453 | 0 | 6.4875 | 0 | 5.4826 | 8.818 | 0 | 0 | 0 | 7.2 | 76.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.6 | 0 | 3099.6 | 126070 | 0 | 60 | 64 | 126070 | -1000000
9 | 10 | 19 | 7 | 6.6114 | 0 | 42.7453 | 0 | 6.1832 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 7.2 | 77.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.31 | 0 | 3099.31 | 125893 | 0 | 59 | 63 | 125893 | -1000000
9 | 10 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 8.1008 | 0 | 5.4806 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.24 | 0 | 3099.24 | 162189 | 0 | 59 | 63 | 162189 | -1000000
9 | 10 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.1713 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 7.2 | 77.0846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.31 | 0 | 3099.31 | 125753 | 0 | 59 | 62 | 125753 | -1000000
9 | 10 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.1071 | 0 | 5.4879 | 8.818 | 0 | 0 | 0 | 6.4 | 76.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.49 | 0 | 3099.49 | 125675 | 0 | 59 | 61 | 125675 | -1000000
9 | 10 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3666 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 5.6 | 75.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3099.79 | 0 | 3099.79 | 125714 | 0 | 60 | 61 | 125714 | -1000000
9 | 10 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.0786 | 0 | 5.4887 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.49 | 0 | 7909.49 | 125755 | 0 | 59 | 60 | 125755 | -1000000
9 | 11 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3418 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.77 | 0 | 7909.77 | 125904 | 0 | 60 | 60 | 125904 | -1000000
9 | 11 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3346 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.23 | 0 | 7909.23 | 125741 | 0 | 60 | 60 | 125741 | -1000000
9 | 11 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 7.4168 | 0 | 5.4787 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.15 | 0 | 7909.15 | 149831 | 0 | 60 | 60 | 149831 | -1000000
9 | 11 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.5138 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 4.8 | 82.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8761.08 | 0 | 8761.08 | 129324 | 0 | 60 | 60 | 129324 | -1000000
9 | 11 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 10.9125 | 0 | 5.5295 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10657.5 | 0 | 10657.5 | 227603 | 0 | 60 | 60 | 227603 | -1000000
9 | 11 | 6 | 1 | 48.8196 | 0 | 140.608 | 0 | 39.935 | 0 | 6.332 | 20.2746 | 0 | 0 | 0 | 2.4 | 258.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28521.6 | 0 | 28521.6 | 656229 | -13692.9 | 60 | 60 | 656229 | -1013692.9
9 | 11 | 7 | 1 | 46.1317 | 0 | 168.222 | 0 | 47.6841 | 0 | 6.332 | 20.0645 | 0 | 0 | 0 | 0.8 | 289.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31266.1 | 0 | 31266.1 | 784933 | -16233.9 | 61 | 61 | 784933 | -1016233.9
9 | 11 | 8 | 1 | 40.159 | 0 | 173.795 | 0 | 48.4772 | 0 | 6.332 | 20.1983 | 0 | 0 | 0 | 0 | 288.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39521.7 | 0 | 39521.7 | 832922 | -13957.6 | 62 | 62 | 832922 | -1013957.6
9 | 11 | 9 | 1 | 41.2563 | 0 | 172.186 | 0 | 49.5391 | 0 | 6.332 | 20.5862 | 0 | 0 | 0 | 0 | 289.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61509.4 | 0 | 61509.4 | 877331 | -14460.3 | 62 | 63 | 877331 | -1014460.3
9 | 11 | 10 | 1 | 41.623 | 0 | 163.102 | 0 | 51.9263 | 0 | 6.332 | 20.8157 | 0 | 0 | 0 | 0 | 283.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884 | 0 | 62884 | 921720 | -12512.2 | 63 | 64 | 921720 | -1012512.2
9 | 11 | 11 | 1 | 40.9553 | 0 | 149.692 | 0 | 49.194 | 0 | 6.332 | 21.0914 | 0 | 0 | 0 | 0 | 267.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.1 | 0 | 62884.1 | 877459 | -9205.35 | 64 | 66 | 877459 | -1009205.35
9 | 11 | 12 | 1 | 39.829 | 0 | 150.207 | 0 | 50.879 | 0 | 6.332 | 21.4197 | 0 | 0 | 0 | 0 | 268.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.3 | 0 | 62884.3 | 924471 | -8299.15 | 65 | 67 | 924471 | -1008299.15
9 | 11 | 13 | 1 | 41.5731 | 0 | 165.698 | 0 | 57.2874 | 0 | 6.332 | 21.8243 | 0 | 0 | 0 | 0 | 292.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.6 | 0 | 62884.6 | 1035090 | -11772.9 | 65 | 67 | 1035090 | -1011772.9
9 | 11 | 14 | 1 | 40.9121 | 0 | 172.702 | 0 | 59.09 | 0 | 6.332 | 22.2788 | 0 | 0 | 0 | 0 | 301.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61510.5 | 0 | 61510.5 | 1066680 | -14723.6 | 65 | 67 | 1066680 | -1014723.6
9 | 11 | 15 | 1 | 40.8193 | 0 | 173.986 | 0 | 60.996 | 0 | 7.4892 | 22.603 | 0 | 0 | 0 | 0 | 305.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56013.1 | 0 | 56013.1 | 1107270 | -15918.9 | 65 | 67 | 1107270 | -1015918.9
9 | 11 | 16 | 1 | 41.3949 | 0 | 169.782 | 0 | 60.3904 | 0 | 7.8974 | 21.8698 | 0 | 0 | 0 | 1.2 | 302.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46393 | 0 | 46393 | 1102610 | -15669.1 | 65 | 67 | 1102610 | -1015669.1
9 | 11 | 17 | 1 | 36.5498 | 0 | 152.497 | 0 | 52.7926 | 0 | 6.332 | 21.3704 | 0 | 0 | 0 | 4.8 | 274.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35398.9 | 0 | 35398.9 | 992530 | -13031.8 | 65 | 67 | 992530 | -1013031.8
9 | 11 | 18 | 1 | 29.5744 | 0 | 93.4203 | 0 | 34.6423 | 0 | 6.332 | 19.6805 | 0 | 0 | 0 | 7.2 | 190.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21657 | 0 | 21657 | 674059 | -9515.21 | 65 | 67 | 674059 | -1009515.21
9 | 11 | 19 | 1 | 24.0902 | 0 | 62.7906 | 0 | 9.5826 | 0 | 5.5034 | 8.818 | 0 | 0 | 0 | 7.2 | 117.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15473.9 | 0 | 15473.9 | 187618 | 0 | 65 | 66 | 187618 | -1000000
9 | 11 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.2266 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 7.2 | 103.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14788.6 | 0 | 14788.6 | 167637 | 0 | 64 | 65 | 167637 | -1000000
9 | 11 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.565 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9280.09 | 0 | 9280.09 | 154550 | 0 | 64 | 64 | 154550 | -1000000
9 | 11 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.014 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9058.63 | 0 | 9058.63 | 143605 | 0 | 63 | 63 | 143605 | -1000000
9 | 11 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.4486 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 5.6 | 79.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.58 | 0 | 7902.58 | 138642 | 0 | 61 | 61 | 138642 | -1000000
9 | 11 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6135 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.48 | 0 | 7902.48 | 137441 | 0 | 60 | 60 | 137441 | -1000000
9 | 12 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8377 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.31 | 0 | 7902.31 | 136743 | 0 | 60 | 60 | 136743 | -1000000
9 | 12 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.1069 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.19 | 0 | 7902.19 | 136206 | 0 | 61 | 61 | 136206 | -1000000
9 | 12 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.8195 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.98 | 0 | 7901.98 | 135562 | 0 | 61 | 61 | 135562 | -1000000
9 | 12 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.9668 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 82.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8753.73 | 0 | 8753.73 | 138834 | 0 | 61 | 61 | 138834 | -1000000
9 | 12 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.6065 | 0 | 5.5974 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649.8 | 0 | 10649.8 | 263702 | 0 | 61 | 61 | 263702 | -1000000
9 | 12 | 6 | 2 | 48.9279 | 0 | 140.608 | 0 | 43.9141 | 0 | 6.332 | 20.937 | 0 | 0 | 0 | 2.4 | 263.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28513.6 | 0 | 28513.6 | 795471 | -9930.26 | 61 | 61 | 795471 | -1009930.26
9 | 12 | 7 | 2 | 44.8676 | 0 | 168.222 | 0 | 52.6312 | 0 | 6.332 | 20.6276 | 0 | 0 | 0 | 0.8 | 293.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31257.8 | 0 | 31257.8 | 924597 | -16549.1 | 62 | 62 | 924597 | -1016549.1
9 | 12 | 8 | 2 | 41.0467 | 0 | 173.795 | 0 | 53.0905 | 0 | 6.332 | 20.8692 | 0 | 0 | 0 | 0 | 295.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39517.9 | 0 | 39517.9 | 959449 | -17781.4 | 63 | 64 | 959449 | -1017781.4
9 | 12 | 9 | 2 | 41.3761 | 0 | 172.186 | 0 | 55.4947 | 0 | 25.335 | 21.2125 | 0 | 0 | 0 | 0 | 315.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61506.6 | 0 | 61506.6 | 1008150 | -18438.2 | 64 | 65 | 1008150 | -1018438.2
9 | 12 | 10 | 2 | 41.9975 | 0 | 163.102 | 0 | 57.5673 | 0 | 25.335 | 21.1725 | 0 | 0 | 0 | 0 | 309.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.3 | 0 | 62881.3 | 1042110 | -16063 | 65 | 66 | 1042110 | -1016063
9 | 12 | 11 | 2 | 41.0361 | 0 | 149.692 | 0 | 52.2298 | 0 | 25.335 | 21.2122 | 0 | 0 | 0 | 0 | 289.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.5 | 0 | 62881.5 | 944921 | -13323.5 | 65 | 66 | 944921 | -1013323.5
9 | 12 | 12 | 2 | 39.819 | 0 | 150.207 | 0 | 54.571 | 0 | 25.335 | 21.7121 | 0 | 0 | 0 | 0 | 291.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.8 | 0 | 62881.8 | 968180 | -12013.3 | 65 | 67 | 968180 | -1012013.3
9 | 12 | 13 | 2 | 41.5888 | 0 | 165.698 | 0 | 60.0745 | 0 | 25.335 | 22.0686 | 0 | 0 | 0 | 0 | 314.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882.4 | 0 | 62882.4 | 1069090 | -15604 | 65 | 67 | 1069090 | -1015604
9 | 12 | 14 | 2 | 40.9014 | 0 | 172.702 | 0 | 65.2094 | 0 | 25.335 | 22.761 | 0 | 0 | 0 | 0 | 326.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61508.4 | 0 | 61508.4 | 1136000 | -18077.4 | 66 | 68 | 1136000 | -1018077.4
9 | 12 | 15 | 2 | 40.8345 | 0 | 173.986 | 0 | 66.8063 | 0 | 25.335 | 23.0098 | 0 | 0 | 0 | 0 | 329.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56011 | 0 | 56011 | 1175210 | -19791.6 | 66 | 68 | 1175210 | -1019791.6
9 | 12 | 16 | 2 | 41.1715 | 0 | 169.782 | 0 | 65.474 | 0 | 25.335 | 22.3313 | 0 | 0 | 0 | 1.2 | 325.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46391 | 0 | 46391 | 1174480 | -19378.1 | 66 | 68 | 1174480 | -1019378.1
9 | 12 | 17 | 2 | 36.6405 | 0 | 152.497 | 0 | 56.766 | 0 | 25.335 | 21.4742 | 0 | 0 | 0 | 4.8 | 297.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35397.2 | 0 | 35397.2 | 1054060 | -16459.1 | 66 | 67 | 1054060 | -1016459.1
9 | 12 | 18 | 2 | 31.2731 | 0 | 93.4203 | 0 | 38.4534 | 0 | 25.335 | 19.6352 | 0 | 0 | 0 | 7.2 | 215.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21655.2 | 0 | 21655.2 | 715166 | -12568.7 | 66 | 67 | 715166 | -1012568.7
9 | 12 | 19 | 2 | 24.0597 | 0 | 62.7906 | 0 | 9.8228 | 0 | 9.4077 | 8.818 | 0 | 0 | 0 | 7.2 | 122.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15472.2 | 0 | 15472.2 | 192076 | 0 | 66 | 66 | 192076 | -1000000
9 | 12 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.738 | 0 | 5.4883 | 8.818 | 0 | 0 | 0 | 7.2 | 103.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14787 | 0 | 14787 | 171874 | 0 | 66 | 66 | 171874 | -1000000
9 | 12 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.792 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9278.03 | 0 | 9278.03 | 158486 | 0 | 65 | 65 | 158486 | -1000000
9 | 12 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.5379 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9056.66 | 0 | 9056.66 | 147498 | 0 | 65 | 65 | 147498 | -1000000
9 | 12 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9946 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.65 | 0 | 7900.65 | 142464 | 0 | 64 | 64 | 142464 | -1000000
9 | 12 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.1825 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.66 | 0 | 7900.66 | 140934 | 0 | 64 | 64 | 140934 | -1000000
9 | 13 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.141 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.4172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.62 | 0 | 7900.62 | 140055 | 0 | 64 | 64 | 140055 | -1000000
9 | 13 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.4112 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.63 | 0 | 7900.63 | 139354 | 0 | 65 | 65 | 139354 | -1000000
9 | 13 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.1135 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.58 | 0 | 7900.58 | 138626 | 0 | 65 | 65 | 138626 | -1000000
9 | 13 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9559 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8752.48 | 0 | 8752.48 | 141771 | 0 | 64 | 64 | 141771 | -1000000
9 | 13 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 12.5206 | 0 | 5.6032 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10648.7 | 0 | 10648.7 | 257291 | 0 | 64 | 64 | 257291 | -1000000
9 | 13 | 6 | 3 | 48.7654 | 0 | 140.608 | 0 | 46.2053 | 0 | 6.332 | 20.778 | 0 | 0 | 0 | 2.4 | 265.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28512.5 | 0 | 28512.5 | 876335 | -8388.84 | 63 | 63 | 876335 | -1008388.84
9 | 13 | 7 | 3 | 40.8936 | 0 | 168.222 | 0 | 59.1193 | 0 | 6.332 | 21.1516 | 0 | 0 | 0 | 0.8 | 296.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31256.9 | 0 | 31256.9 | 1046890 | -19789.3 | 65 | 65 | 1046890 | -1019789.3
9 | 13 | 8 | 3 | 39.7943 | 0 | 173.795 | 0 | 60.3185 | 0 | 6.332 | 21.828 | 0 | 0 | 0 | 0 | 302.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39517 | 0 | 39517 | 1099320 | -20243 | 66 | 66 | 1099320 | -1020243
9 | 13 | 9 | 3 | 41.4957 | 0 | 172.186 | 0 | 66.2112 | 0 | 25.335 | 21.9702 | 0 | 0 | 0 | 0 | 327.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61505.5 | 0 | 61505.5 | 1183050 | -20637.1 | 68 | 68 | 1183050 | -1020637.1
9 | 13 | 10 | 3 | 42.2066 | 0 | 163.102 | 0 | 65.5734 | 0 | 25.335 | 21.6814 | 0 | 0 | 0 | 0 | 317.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.4 | 0 | 62880.4 | 1183290 | -18281.2 | 68 | 68 | 1183290 | -1018281.2
9 | 13 | 11 | 3 | 41.0301 | 0 | 149.692 | 0 | 59.8403 | 0 | 25.335 | 21.8201 | 0 | 0 | 0 | 0 | 297.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.5 | 0 | 62880.5 | 1072120 | -14769.4 | 68 | 69 | 1072120 | -1014769.4
9 | 13 | 12 | 3 | 39.7969 | 0 | 150.207 | 0 | 61.5976 | 0 | 25.335 | 22.4381 | 0 | 0 | 0 | 0 | 299.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.8 | 0 | 62880.8 | 1102600 | -13896.3 | 68 | 69 | 1102600 | -1013896.3
9 | 13 | 13 | 3 | 41.6594 | 0 | 165.698 | 0 | 68.7152 | 0 | 25.335 | 22.6813 | 0 | 0 | 0 | 0 | 324.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.4 | 0 | 62881.4 | 1210340 | -16938.6 | 68 | 70 | 1210340 | -1016938.6
9 | 13 | 14 | 3 | 40.8094 | 0 | 172.702 | 0 | 72.6439 | 0 | 25.335 | 23.2856 | 0 | 0 | 0 | 0 | 334.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61507.4 | 0 | 61507.4 | 1256870 | -20464.2 | 68 | 72 | 1256870 | -1020464.2
9 | 13 | 15 | 3 | 40.8114 | 0 | 173.986 | 0 | 75.3904 | 0 | 25.335 | 23.6472 | 0 | 0 | 0 | 0 | 339.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56010 | 0 | 56010 | 1304340 | -21544.2 | 68 | 73 | 1304340 | -1021544.2
9 | 13 | 16 | 3 | 40.3134 | 0 | 169.782 | 0 | 69.1066 | 0 | 25.335 | 23.3369 | 0 | 0 | 0 | 1.2 | 329.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46390.6 | 0 | 46390.6 | 1245680 | -21155.9 | 66 | 71 | 1245680 | -1021155.9
9 | 13 | 17 | 3 | 35.523 | 0 | 152.497 | 0 | 58.5448 | 0 | 25.335 | 22.4477 | 0 | 0 | 0 | 4.8 | 299.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35396.7 | 0 | 35396.7 | 1084720 | -18050.3 | 65 | 69 | 1084720 | -1018050.3
9 | 13 | 18 | 3 | 25.8152 | 0 | 93.4203 | 0 | 34.893 | 0 | 25.335 | 19.8383 | 0 | 0 | 0 | 7.2 | 206.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21654.7 | 0 | 21654.7 | 702008 | -14348.8 | 64 | 67 | 702008 | -1014348.8
9 | 13 | 19 | 3 | 24.1632 | 0 | 62.7906 | 0 | 9.5451 | 0 | 5.5015 | 8.818 | 0 | 0 | 0 | 7.2 | 118.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15471.4 | 0 | 15471.4 | 193203 | 0 | 63 | 65 | 193203 | -1000000
9 | 13 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.4475 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 7.2 | 103.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14786.2 | 0 | 14786.2 | 173345 | 0 | 63 | 64 | 173345 | -1000000
9 | 13 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.4623 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9276.97 | 0 | 9276.97 | 159704 | 0 | 62 | 62 | 159704 | -1000000
9 | 13 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.1647 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9055.63 | 0 | 9055.63 | 148514 | 0 | 61 | 61 | 148514 | -1000000
9 | 13 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8963 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.66 | 0 | 7899.66 | 143567 | 0 | 60 | 60 | 143567 | -1000000
9 | 13 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.0653 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.71 | 0 | 7899.71 | 141705 | 0 | 58 | 59 | 141705 | -1000000
9 | 14 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0222 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.61 | 0 | 7899.61 | 140778 | 0 | 57 | 57 | 140778 | -1000000
9 | 14 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.97 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.86 | 0 | 7899.86 | 139630 | 0 | 55 | 56 | 139630 | -1000000
9 | 14 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9356 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.15 | 0 | 7900.15 | 138884 | 0 | 54 | 54 | 138884 | -1000000
9 | 14 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0622 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8752.58 | 0 | 8752.58 | 141716 | 0 | 53 | 53 | 141716 | -1000000
9 | 14 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 10.9471 | 0 | 5.5305 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10649.4 | 0 | 10649.4 | 228164 | 0 | 53 | 53 | 228164 | -1000000
9 | 14 | 6 | 4 | 48.7681 | 0 | 140.608 | 0 | 24.6052 | 0 | 6.332 | 19.6577 | 0 | 0 | 0 | 2.4 | 242.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28514.1 | 0 | 28514.1 | 458241 | -14507.9 | 52 | 52 | 458241 | -1014507.9
9 | 14 | 7 | 4 | 40.5407 | 0 | 168.222 | 0 | 33.4819 | 0 | 6.332 | 19.7011 | 0 | 0 | 0 | 0.8 | 269.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31259.3 | 0 | 31259.3 | 604734 | -33668.3 | 53 | 55 | 604734 | -1033668.3
9 | 14 | 8 | 4 | 39.9947 | 0 | 173.795 | 0 | 36.2654 | 0 | 6.332 | 19.8626 | 0 | 0 | 0 | 0 | 276.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39518.1 | 0 | 39518.1 | 689000 | -30575.2 | 54 | 57 | 689000 | -1030575.2
9 | 14 | 9 | 4 | 40.7281 | 0 | 172.186 | 0 | 40.9778 | 0 | 6.332 | 20.4114 | 0 | 0 | 0 | 0 | 280.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61506.4 | 0 | 61506.4 | 771056 | -26595.2 | 55 | 60 | 771056 | -1026595.2
9 | 14 | 10 | 4 | 41.1517 | 0 | 163.102 | 0 | 46.0398 | 0 | 6.332 | 21.133 | 0 | 0 | 0 | 0 | 277.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882.6 | 0 | 62882.6 | 847408 | -22393.9 | 57 | 62 | 847408 | -1022393.9
9 | 14 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 45.0512 | 0 | 6.332 | 21.4672 | 0 | 0 | 0 | 0 | 263.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62883.6 | 0 | 62883.6 | 822412 | -18269.1 | 58 | 65 | 822412 | -1018269.1
9 | 14 | 12 | 4 | 39.7562 | 0 | 150.207 | 0 | 52.3333 | 0 | 6.332 | 20.7863 | 0 | 0 | 0 | 0 | 269.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62883.7 | 0 | 62883.7 | 923391 | -34582.2 | 59 | 67 | 923391 | -1034582.2
9 | 14 | 13 | 4 | 41.3143 | 0 | 165.698 | 0 | 52.598 | 0 | 25.335 | 21.7586 | 0 | 0 | 0 | 0 | 306.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.1 | 0 | 62884.1 | 954487 | -19289 | 58 | 68 | 954487 | -1019289
9 | 14 | 14 | 4 | 40.6952 | 0 | 172.702 | 0 | 55.5146 | 0 | 25.335 | 21.6436 | 0 | 0 | 0 | 0 | 315.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61510.4 | 0 | 61510.4 | 995189 | -20694.5 | 58 | 69 | 995189 | -1020694.5
9 | 14 | 15 | 4 | 40.5971 | 0 | 173.986 | 0 | 59.1375 | 0 | 25.335 | 21.928 | 0 | 0 | 0 | 0 | 320.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56014 | 0 | 56014 | 1053510 | -22051.6 | 58 | 70 | 1053510 | -1022051.6
9 | 14 | 16 | 4 | 40.3487 | 0 | 169.782 | 0 | 55.6198 | 0 | 17.7218 | 21.9581 | 0 | 0 | 0 | 1.2 | 306.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46394.3 | 0 | 46394.3 | 1024280 | -21605.6 | 58 | 69 | 1024280 | -1021605.6
9 | 14 | 17 | 4 | 35.6767 | 0 | 152.497 | 0 | 45.0734 | 0 | 6.332 | 21.7472 | 0 | 0 | 0 | 4.8 | 266.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35400.5 | 0 | 35400.5 | 881422 | -18783.1 | 57 | 67 | 881422 | -1018783.1
9 | 14 | 18 | 4 | 25.6946 | 0 | 93.4203 | 0 | 28.1265 | 0 | 6.332 | 19.9501 | 0 | 0 | 0 | 7.2 | 180.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21658 | 0 | 21658 | 575701 | -14658.9 | 57 | 66 | 575701 | -1014658.9
9 | 14 | 19 | 4 | 23.9953 | 0 | 62.7906 | 0 | 8.7681 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 7.2 | 117.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15473.5 | 0 | 15473.5 | 193069 | 0 | 56 | 62 | 193069 | -1000000
9 | 14 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.0019 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 102.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14787.8 | 0 | 14787.8 | 173133 | 0 | 55 | 58 | 173133 | -1000000
9 | 14 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.8856 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 92.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9279.31 | 0 | 9279.31 | 159462 | 0 | 53 | 54 | 159462 | -1000000
9 | 14 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.3753 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9057.88 | 0 | 9057.88 | 148336 | 0 | 53 | 54 | 148336 | -1000000
9 | 14 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.1485 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.07 | 0 | 7902.07 | 143476 | 0 | 54 | 55 | 143476 | -1000000
9 | 14 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.0686 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.3457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.25 | 0 | 7902.25 | 141780 | 0 | 54 | 55 | 141780 | -1000000
9 | 15 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.0211 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.34 | 0 | 7902.34 | 140752 | 0 | 54 | 55 | 140752 | -1000000
9 | 15 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9772 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.9 | 0 | 7902.9 | 139791 | 0 | 54 | 56 | 139791 | -1000000
9 | 15 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9392 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.4 | 0 | 7903.4 | 138961 | 0 | 54 | 56 | 138961 | -1000000
9 | 15 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.0712 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8755.96 | 0 | 8755.96 | 141913 | 0 | 54 | 56 | 141913 | -1000000
9 | 15 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 10.8816 | 0 | 5.5286 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10652.8 | 0 | 10652.8 | 226701 | 0 | 54 | 57 | 226701 | -1000000
9 | 15 | 6 | 5 | 48.8973 | 0 | 140.608 | 0 | 29.6976 | 0 | 6.332 | 19.6645 | 0 | 0 | 0 | 2.4 | 247.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28517.4 | 0 | 28517.4 | 533511 | -13889.2 | 54 | 57 | 533511 | -1013889.2
9 | 15 | 7 | 5 | 41.3439 | 0 | 168.222 | 0 | 39.8968 | 0 | 6.332 | 19.7019 | 0 | 0 | 0 | 0.8 | 276.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31262.3 | 0 | 31262.3 | 691811 | -27377.7 | 56 | 61 | 691811 | -1027377.7
9 | 15 | 8 | 5 | 39.6811 | 0 | 173.795 | 0 | 46.5831 | 0 | 6.332 | 20.2713 | 0 | 0 | 0 | 0 | 286.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39519.8 | 0 | 39519.8 | 821309 | -23858.4 | 59 | 64 | 821309 | -1023858.4
9 | 15 | 9 | 5 | 40.6158 | 0 | 172.186 | 0 | 54.5522 | 0 | 6.332 | 20.9983 | 0 | 0 | 0 | 0 | 294.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61507.8 | 0 | 61507.8 | 931136 | -22820.5 | 60 | 68 | 931136 | -1022820.5
9 | 15 | 10 | 5 | 41.1517 | 0 | 163.102 | 0 | 58.5655 | 0 | 6.332 | 21.7386 | 0 | 0 | 0 | 0 | 290.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882.4 | 0 | 62882.4 | 1023260 | -19121.3 | 62 | 70 | 1023260 | -1019121.3
9 | 15 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 57.8694 | 0 | 6.8013 | 21.833 | 0 | 0 | 0 | 0 | 276.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62883.9 | 0 | 62883.9 | 1013320 | -19486.7 | 63 | 72 | 1013320 | -1019486.7
9 | 15 | 12 | 5 | 39.7554 | 0 | 150.207 | 0 | 69.305 | 0 | 25.335 | 20.9735 | 0 | 0 | 0 | 0 | 305.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884 | 0 | 62884 | 1149680 | -39571.9 | 64 | 74 | 1149680 | -1039571.9
9 | 15 | 13 | 5 | 41.2831 | 0 | 165.698 | 0 | 70.1566 | 0 | 25.335 | 22.1061 | 0 | 0 | 0 | 0 | 324.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62884.9 | 0 | 62884.9 | 1212630 | -21631.5 | 64 | 75 | 1212630 | -1021631.5
9 | 15 | 14 | 5 | 40.6706 | 0 | 172.702 | 0 | 72.056 | 0 | 25.335 | 22.2918 | 0 | 0 | 0 | 0 | 333.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61511.4 | 0 | 61511.4 | 1250960 | -19116.5 | 64 | 75 | 1250960 | -1019116.5
9 | 15 | 15 | 5 | 40.5726 | 0 | 173.986 | 0 | 75.5147 | 0 | 25.335 | 22.2654 | 0 | 0 | 0 | 0 | 337.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56014.9 | 0 | 56014.9 | 1294660 | -23249.2 | 64 | 76 | 1294660 | -1023249.2
9 | 15 | 16 | 5 | 40.3296 | 0 | 169.782 | 0 | 70.5773 | 0 | 25.335 | 22.3467 | 0 | 0 | 0 | 1.2 | 329.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46395.4 | 0 | 46395.4 | 1261130 | -20879 | 64 | 74 | 1261130 | -1020879
9 | 15 | 17 | 5 | 35.5153 | 0 | 152.497 | 0 | 55.9459 | 0 | 15.2404 | 22.0581 | 0 | 0 | 0 | 4.8 | 286.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35401.5 | 0 | 35401.5 | 1083600 | -18073.8 | 63 | 71 | 1083600 | -1018073.8
9 | 15 | 18 | 5 | 25.9029 | 0 | 93.4203 | 0 | 33.405 | 0 | 6.332 | 20.1802 | 0 | 0 | 0 | 7.2 | 186.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21659 | 0 | 21659 | 687855 | -14120.2 | 62 | 69 | 687855 | -1014120.2
9 | 15 | 19 | 5 | 24.1581 | 0 | 62.7906 | 0 | 9.0217 | 0 | 5.4918 | 8.818 | 0 | 0 | 0 | 7.2 | 117.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15474.5 | 0 | 15474.5 | 193520 | 0 | 60 | 65 | 193520 | -1000000
9 | 15 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 7.5294 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 102.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14788.3 | 0 | 14788.3 | 173145 | 0 | 57 | 61 | 173145 | -1000000
9 | 15 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.6337 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9279.56 | 0 | 9279.56 | 159564 | 0 | 54 | 57 | 159564 | -1000000
9 | 15 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.3825 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 6.4 | 83.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9058.04 | 0 | 9058.04 | 148494 | 0 | 53 | 55 | 148494 | -1000000
9 | 15 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.1447 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 5.6 | 79.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.31 | 0 | 7902.31 | 143387 | 0 | 51 | 52 | 143387 | -1000000
9 | 15 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 7.0552 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 75.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.65 | 0 | 7902.65 | 141483 | 0 | 50 | 50 | 141483 | -1000000
9 | 16 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 7.0064 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.72 | 0 | 7902.72 | 140428 | 0 | 50 | 50 | 140428 | -1000000
9 | 16 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9617 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 75.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.61 | 0 | 7903.61 | 139453 | 0 | 50 | 50 | 139453 | -1000000
9 | 16 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9211 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7904.12 | 0 | 7904.12 | 138564 | 0 | 50 | 50 | 138564 | -1000000
9 | 16 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8802 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 75.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7904.61 | 0 | 7904.61 | 137670 | 0 | 50 | 50 | 137670 | -1000000
9 | 16 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.838 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7905.05 | 0 | 7905.05 | 136746 | 0 | 49 | 49 | 136746 | -1000000
9 | 16 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8044 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 2.4 | 72.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7905.49 | 0 | 7905.49 | 136014 | 0 | 49 | 49 | 136014 | -1000000
9 | 16 | 7 | 6 | 5.0696 | 0 | 42.7453 | 0 | 13.8839 | 0 | 5.9647 | 18.8896 | 0 | 0 | 0 | 0.8 | 87.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7905.9 | 0 | 7905.9 | 206934 | -14192.4 | 53 | 55 | 206934 | -1014192.4
9 | 16 | 8 | 6 | 5.0468 | 0 | 42.7453 | 0 | 15.0707 | 0 | 6.0253 | 18.8896 | 0 | 0 | 0 | 0 | 87.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7906.2 | 0 | 7906.2 | 242471 | -24241.9 | 57 | 60 | 242471 | -1024241.9
9 | 16 | 9 | 6 | 5.4689 | 0 | 42.7453 | 0 | 15.9855 | 0 | 6.2983 | 18.8896 | 0 | 0 | 0 | 0 | 89.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7917.11 | 0 | 7917.11 | 293016 | -19614.6 | 60 | 66 | 293016 | -1019614.6
9 | 16 | 10 | 6 | 5.4689 | 0 | 42.7453 | 0 | 24.5341 | 0 | 25.335 | 18.9653 | 0 | 0 | 0 | 0 | 117.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.51 | 0 | 7918.51 | 414608 | -18319.9 | 64 | 71 | 414608 | -1018319.9
9 | 16 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 34.0002 | 0 | 25.335 | 19.0479 | 0 | 0 | 0 | 0 | 126.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.84 | 0 | 7919.84 | 573943 | -29171.7 | 68 | 76 | 573943 | -1029171.7
9 | 16 | 12 | 6 | 5.4689 | 0 | 42.7453 | 0 | 42.4957 | 0 | 25.335 | 19.1601 | 0 | 0 | 0 | 0 | 135.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.1 | 0 | 7920.1 | 731137 | -35513.8 | 72 | 81 | 731137 | -1035513.8
9 | 16 | 13 | 6 | 5.473 | 0 | 42.7453 | 0 | 47.1415 | 0 | 25.335 | 19.2862 | 0 | 0 | 0 | 0 | 139.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.48 | 0 | 7920.48 | 790520 | -35307.9 | 73 | 83 | 790520 | -1035307.9
9 | 16 | 14 | 6 | 5.475 | 0 | 42.7453 | 0 | 12.8797 | 0 | 13.8592 | 12.8287 | 0 | 0 | 0 | 0 | 87.7879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.86 | 0 | 7920.86 | 209707 | 0 | 74 | 85 | 209707 | -1000000
9 | 16 | 15 | 6 | 5.4758 | 0 | 42.7453 | 0 | 12.7452 | 0 | 13.6442 | 12.8287 | 0 | 0 | 0 | 0 | 87.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.27 | 0 | 7921.27 | 217791 | 0 | 75 | 87 | 217791 | -1000000
9 | 16 | 16 | 6 | 5.4769 | 0 | 42.7453 | 0 | 15.1055 | 0 | 19.5056 | 14.8767 | 0 | 0 | 0 | 1.2 | 98.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.72 | 0 | 7914.72 | 266633 | 0 | 73 | 85 | 266633 | -1000000
9 | 16 | 17 | 6 | 5.5044 | 0 | 42.7453 | 0 | 14.8039 | 0 | 18.8733 | 14.8767 | 0 | 0 | 0 | 4.8 | 101.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7910.36 | 0 | 7910.36 | 262254 | 0 | 71 | 82 | 262254 | -1000000
9 | 16 | 18 | 6 | 6.3078 | 0 | 42.7453 | 0 | 7.3251 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 7.2 | 77.8754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.17 | 0 | 7907.17 | 132072 | 0 | 70 | 80 | 132072 | -1000000
9 | 16 | 19 | 6 | 8.7584 | 0 | 42.7453 | 0 | 7.2022 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 80.2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7904.59 | 0 | 7904.59 | 131769 | 0 | 68 | 78 | 131769 | -1000000
9 | 16 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.1794 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 80.2188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7902.93 | 0 | 7902.93 | 131307 | 0 | 66 | 77 | 131307 | -1000000
9 | 16 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 7.1651 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 80.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7901.59 | 0 | 7901.59 | 131024 | 0 | 63 | 75 | 131024 | -1000000
9 | 16 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.5947 | 0 | 5.4911 | 8.818 | 0 | 0 | 0 | 6.4 | 77.8464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7900.58 | 0 | 7900.58 | 130989 | 0 | 62 | 70 | 130989 | -1000000
9 | 16 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.7092 | 0 | 5.4913 | 8.818 | 0 | 0 | 0 | 5.6 | 77.1611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.73 | 0 | 7899.73 | 130494 | 0 | 60 | 66 | 130494 | -1000000
9 | 16 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 5.2713 | 0 | 5.5021 | 8.818 | 0 | 0 | 0 | 4.8 | 72.2421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.49 | 0 | 3089.49 | 129928 | 0 | 57 | 61 | 129928 | -1000000
9 | 17 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2633 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.09 | 0 | 3089.09 | 129795 | 0 | 57 | 59 | 129795 | -1000000
9 | 17 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4985 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 4.8 | 73.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.14 | 0 | 3089.14 | 129322 | 0 | 56 | 58 | 129322 | -1000000
9 | 17 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4831 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.28 | 0 | 3089.28 | 128987 | 0 | 55 | 56 | 128987 | -1000000
9 | 17 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4695 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.22 | 0 | 3089.22 | 128691 | 0 | 55 | 55 | 128691 | -1000000
9 | 17 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4485 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.26 | 0 | 3089.26 | 128229 | 0 | 54 | 54 | 128229 | -1000000
9 | 17 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4319 | 0 | 5.5503 | 8.818 | 0 | 0 | 0 | 2.4 | 71.0508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.34 | 0 | 3089.34 | 127866 | 0 | 53 | 53 | 127866 | -1000000
9 | 17 | 7 | 7 | 3.9047 | 0 | 42.7453 | 0 | 6.4325 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 0.8 | 68.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.44 | 0 | 3089.44 | 127888 | 0 | 56 | 57 | 127888 | -1000000
9 | 17 | 8 | 7 | 3.7996 | 0 | 42.7453 | 0 | 6.7155 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 0 | 67.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.55 | 0 | 3089.55 | 127691 | 0 | 58 | 61 | 127691 | -1000000
9 | 17 | 9 | 7 | 4.1443 | 0 | 42.7453 | 0 | 7.6484 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 0 | 68.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3089.66 | 0 | 3089.66 | 127575 | 0 | 60 | 65 | 127575 | -1000000
9 | 17 | 10 | 7 | 4.144 | 0 | 42.7453 | 0 | 10.7399 | 0 | 5.5415 | 12.8287 | 0 | 0 | 0 | 0 | 75.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3088.97 | 0 | 3088.97 | 189327 | 0 | 61 | 69 | 189327 | -1000000
9 | 17 | 11 | 7 | 4.144 | 0 | 42.7453 | 0 | 11.087 | 0 | 5.5618 | 12.8287 | 0 | 0 | 0 | 0 | 76.3667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3087.53 | 0 | 3087.53 | 197219 | 0 | 62 | 72 | 197219 | -1000000
9 | 17 | 12 | 7 | 4.1442 | 0 | 42.7453 | 0 | 11.9362 | 0 | 5.611 | 12.8287 | 0 | 0 | 0 | 0 | 77.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3085.56 | 0 | 3085.56 | 210275 | 0 | 62 | 76 | 210275 | -1000000
9 | 17 | 13 | 7 | 4.1485 | 0 | 42.7453 | 0 | 11.6109 | 0 | 5.5942 | 12.8287 | 0 | 0 | 0 | 0 | 76.9275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3083.56 | 0 | 3083.56 | 220540 | 0 | 61 | 75 | 220540 | -1000000
9 | 17 | 14 | 7 | 4.1475 | 0 | 42.7453 | 0 | 12.8718 | 0 | 5.6611 | 14.8767 | 0 | 0 | 0 | 0 | 80.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3081.74 | 0 | 3081.74 | 253480 | 0 | 60 | 74 | 253480 | -1000000
9 | 17 | 15 | 7 | 4.1534 | 0 | 42.7453 | 0 | 10.0355 | 0 | 5.5255 | 12.8287 | 0 | 0 | 0 | 0 | 75.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.01 | 0 | 3080.01 | 195834 | 0 | 60 | 73 | 195834 | -1000000
9 | 17 | 16 | 7 | 4.3408 | 0 | 42.7453 | 0 | 6.6286 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 1.2 | 69.2123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3078.23 | 0 | 3078.23 | 127171 | 0 | 62 | 72 | 127171 | -1000000
9 | 17 | 17 | 7 | 4.7607 | 0 | 42.7453 | 0 | 6.8487 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3076.83 | 0 | 3076.83 | 127205 | 0 | 63 | 72 | 127205 | -1000000
9 | 17 | 18 | 7 | 6.2558 | 0 | 42.7453 | 0 | 6.5463 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 77.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3076.11 | 0 | 3076.11 | 127438 | 0 | 65 | 71 | 127438 | -1000000
9 | 17 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4926 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 7.2 | 77.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3075.29 | 0 | 3075.29 | 127115 | 0 | 65 | 70 | 127115 | -1000000
9 | 17 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.7573 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 7.2 | 77.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3074.78 | 0 | 3074.78 | 126984 | 0 | 65 | 70 | 126984 | -1000000
9 | 17 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4463 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 7.2 | 77.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3074.3 | 0 | 3074.3 | 126945 | 0 | 65 | 69 | 126945 | -1000000
9 | 17 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0932 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 6.4 | 76.2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3073.84 | 0 | 3073.84 | 126674 | 0 | 64 | 67 | 126674 | -1000000
9 | 17 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0129 | 0 | 5.4874 | 8.818 | 0 | 0 | 0 | 5.6 | 75.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3073.51 | 0 | 3073.51 | 126418 | 0 | 62 | 65 | 126418 | -1000000
9 | 17 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 5.9638 | 0 | 5.4889 | 8.818 | 0 | 0 | 0 | 4.8 | 78.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7882.78 | 0 | 7882.78 | 126790 | 0 | 61 | 63 | 126790 | -1000000
9 | 18 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.4913 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7882.68 | 0 | 7882.68 | 126919 | 0 | 62 | 63 | 126919 | -1000000
9 | 18 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.7852 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7881.88 | 0 | 7881.88 | 126834 | 0 | 63 | 64 | 126834 | -1000000
9 | 18 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.5141 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 4.8 | 78.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7881.64 | 0 | 7881.64 | 126638 | 0 | 63 | 64 | 126638 | -1000000
9 | 18 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.6964 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8733.43 | 0 | 8733.43 | 130612 | 0 | 64 | 64 | 130612 | -1000000
9 | 18 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.8076 | 0 | 5.6213 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10629.6 | 0 | 10629.6 | 256486 | 0 | 64 | 65 | 256486 | -1000000
9 | 18 | 6 | 1 | 49.0171 | 0 | 140.608 | 0 | 74.0469 | 0 | 6.332 | 21.7393 | 0 | 0 | 0 | 2.4 | 294.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28493.3 | 0 | 28493.3 | 1240130 | -9992.4 | 65 | 65 | 1240130 | -1009992.4
9 | 18 | 7 | 1 | 49.2993 | 0 | 168.222 | 0 | 72.343 | 0 | 6.332 | 21.9594 | 0 | 0 | 0 | 0.8 | 318.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31237.5 | 0 | 31237.5 | 1217440 | -27042 | 65 | 66 | 1217440 | -1027042
9 | 18 | 8 | 1 | 41.1186 | 0 | 173.795 | 0 | 63.0009 | 0 | 6.332 | 21.9443 | 0 | 0 | 0 | 0 | 306.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39506.2 | 0 | 39506.2 | 1139600 | -19808 | 65 | 66 | 1139600 | -1019808
9 | 18 | 9 | 1 | 41.534 | 0 | 172.186 | 0 | 63.0803 | 0 | 6.332 | 22.4297 | 0 | 0 | 0 | 0 | 305.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61496.3 | 0 | 61496.3 | 1155840 | -14801.3 | 66 | 67 | 1155840 | -1014801.3
9 | 18 | 10 | 1 | 42.0939 | 0 | 163.102 | 0 | 62.2619 | 0 | 6.332 | 22.6075 | 0 | 0 | 0 | 0 | 296.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62871.5 | 0 | 62871.5 | 1154630 | -13368.2 | 66 | 68 | 1154630 | -1013368.2
9 | 18 | 11 | 1 | 40.9737 | 0 | 149.692 | 0 | 58.5853 | 0 | 6.332 | 23.2025 | 0 | 0 | 0 | 0 | 278.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62872.1 | 0 | 62872.1 | 1089140 | -10217.4 | 67 | 70 | 1089140 | -1010217.4
9 | 18 | 12 | 1 | 39.8108 | 0 | 150.207 | 0 | 61.4609 | 0 | 6.332 | 23.4709 | 0 | 0 | 0 | 0 | 281.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62872.7 | 0 | 62872.7 | 1154680 | -9440.05 | 68 | 71 | 1154680 | -1009440.05
9 | 18 | 13 | 1 | 41.6155 | 0 | 165.698 | 0 | 69.1585 | 0 | 6.332 | 23.7024 | 0 | 0 | 0 | 0 | 306.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62873.4 | 0 | 62873.4 | 1267940 | -12722.2 | 68 | 72 | 1267940 | -1012722.2
9 | 18 | 14 | 1 | 40.8718 | 0 | 172.702 | 0 | 73.8369 | 0 | 6.332 | 23.592 | 0 | 0 | 0 | 0 | 317.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61499.9 | 0 | 61499.9 | 1333360 | -15996.1 | 69 | 72 | 1333360 | -1015996.1
9 | 18 | 15 | 1 | 40.9636 | 0 | 173.986 | 0 | 76.9814 | 0 | 6.332 | 23.8157 | 0 | 0 | 0 | 0 | 322.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56003.4 | 0 | 56003.4 | 1368410 | -17029 | 69 | 73 | 1368410 | -1017029
9 | 18 | 16 | 1 | 41.4622 | 0 | 169.782 | 0 | 71.7507 | 0 | 6.332 | 23.5772 | 0 | 0 | 0 | 1.2 | 314.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46384.2 | 0 | 46384.2 | 1319390 | -16687.1 | 68 | 72 | 1319390 | -1016687.1
9 | 18 | 17 | 1 | 36.6752 | 0 | 152.497 | 0 | 60.6526 | 0 | 6.332 | 23.248 | 0 | 0 | 0 | 4.8 | 284.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35390.6 | 0 | 35390.6 | 1169110 | -13874.5 | 67 | 71 | 1169110 | -1013874.5
9 | 18 | 18 | 1 | 30.422 | 0 | 93.4203 | 0 | 39.9134 | 0 | 6.332 | 20.7648 | 0 | 0 | 0 | 7.2 | 198.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21648.6 | 0 | 21648.6 | 808086 | -10326 | 67 | 70 | 808086 | -1010326
9 | 18 | 19 | 1 | 24.2092 | 0 | 62.7906 | 0 | 9.8985 | 0 | 5.5151 | 8.818 | 0 | 0 | 0 | 7.2 | 118.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15465.2 | 0 | 15465.2 | 188520 | 0 | 66 | 69 | 188520 | -1000000
9 | 18 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.4067 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 7.2 | 103.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14780.2 | 0 | 14780.2 | 168452 | 0 | 65 | 68 | 168452 | -1000000
9 | 18 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.7245 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9269.9 | 0 | 9269.9 | 155206 | 0 | 64 | 67 | 155206 | -1000000
9 | 18 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.4793 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 6.4 | 83.7066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.84 | 0 | 9047.84 | 144467 | 0 | 64 | 67 | 144467 | -1000000
9 | 18 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.9467 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7891.35 | 0 | 7891.35 | 139794 | 0 | 64 | 66 | 139794 | -1000000
9 | 18 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 7.1409 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 4.8 | 78.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7891 | 0 | 7891 | 138348 | 0 | 64 | 66 | 138348 | -1000000
9 | 19 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.1057 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7890.67 | 0 | 7890.67 | 137614 | 0 | 64 | 66 | 137614 | -1000000
9 | 19 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.3794 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7890.45 | 0 | 7890.45 | 136915 | 0 | 64 | 67 | 136915 | -1000000
9 | 19 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 7.0887 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7890.21 | 0 | 7890.21 | 136410 | 0 | 64 | 67 | 136410 | -1000000
9 | 19 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.6399 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 82.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8741.96 | 0 | 8741.96 | 139835 | 0 | 64 | 65 | 139835 | -1000000
9 | 19 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.4004 | 0 | 5.5974 | 12.8287 | 0 | 0 | 0 | 4.8 | 129.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10638 | 0 | 10638 | 260414 | 0 | 63 | 64 | 260414 | -1000000
9 | 19 | 6 | 2 | 48.9786 | 0 | 140.608 | 0 | 47.3789 | 0 | 6.332 | 22.2559 | 0 | 0 | 0 | 2.4 | 267.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28501.8 | 0 | 28501.8 | 935668 | -7642.4 | 62 | 62 | 935668 | -1007642.4
9 | 19 | 7 | 2 | 48.3347 | 0 | 168.222 | 0 | 57.5301 | 0 | 6.332 | 21.9054 | 0 | 0 | 0 | 0.8 | 303.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31246.2 | 0 | 31246.2 | 1049200 | -20559.6 | 63 | 64 | 1049200 | -1020559.6
9 | 19 | 8 | 2 | 40.0424 | 0 | 173.795 | 0 | 56.7211 | 0 | 6.332 | 21.9874 | 0 | 0 | 0 | 0 | 298.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39510.2 | 0 | 39510.2 | 1061340 | -20903 | 64 | 65 | 1061340 | -1020903
9 | 19 | 9 | 2 | 40.6792 | 0 | 172.186 | 0 | 59.5703 | 0 | 25.335 | 22.7114 | 0 | 0 | 0 | 0 | 320.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61500.1 | 0 | 61500.1 | 1089250 | -20853.3 | 64 | 67 | 1089250 | -1020853.3
9 | 19 | 10 | 2 | 41.178 | 0 | 163.102 | 0 | 69.4991 | 0 | 25.335 | 22.7222 | 0 | 0 | 0 | 0 | 321.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62875.1 | 0 | 62875.1 | 1199380 | -17562.8 | 66 | 71 | 1199380 | -1017562.8
9 | 19 | 11 | 2 | 40.7055 | 0 | 149.692 | 0 | 73.2673 | 0 | 25.335 | 22.3118 | 0 | 0 | 0 | 0 | 311.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62875.6 | 0 | 62875.6 | 1232660 | -20790.1 | 68 | 74 | 1232660 | -1020790.1
9 | 19 | 12 | 2 | 39.7567 | 0 | 150.207 | 0 | 86.1879 | 0 | 25.335 | 21.4246 | 0 | 0 | 0 | 0 | 322.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62877.1 | 0 | 62877.1 | 1405220 | -42745 | 69 | 78 | 1405220 | -1042745
9 | 19 | 13 | 2 | 41.2898 | 0 | 165.698 | 0 | 91.1125 | 0 | 25.335 | 22.584 | 0 | 0 | 0 | 0 | 346.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62878.9 | 0 | 62878.9 | 1508430 | -23926 | 70 | 79 | 1508430 | -1023926
9 | 19 | 14 | 2 | 40.6868 | 0 | 172.702 | 0 | 95.6118 | 0 | 25.335 | 22.8853 | 0 | 0 | 0 | 0 | 357.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61505.7 | 0 | 61505.7 | 1573760 | -20172.8 | 71 | 80 | 1573760 | -1020172.8
9 | 19 | 15 | 2 | 40.5947 | 0 | 173.986 | 0 | 101.998 | 0 | 25.335 | 22.6251 | 0 | 0 | 0 | 0 | 364.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56009.5 | 0 | 56009.5 | 1681080 | -30547.4 | 72 | 81 | 1681080 | -1030547.4
9 | 19 | 16 | 2 | 40.3495 | 0 | 169.782 | 0 | 94.8073 | 0 | 25.335 | 23.4405 | 0 | 0 | 0 | 1.2 | 354.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46390.3 | 0 | 46390.3 | 1598060 | -16845.9 | 71 | 80 | 1598060 | -1016845.9
9 | 19 | 17 | 2 | 35.7189 | 0 | 152.497 | 0 | 82.5413 | 0 | 25.335 | 23.1418 | 0 | 0 | 0 | 4.8 | 324.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35396.7 | 0 | 35396.7 | 1432570 | -13988 | 70 | 78 | 1432570 | -1013988
9 | 19 | 18 | 2 | 26.4042 | 0 | 93.4203 | 0 | 54.2352 | 0 | 25.335 | 21.7312 | 0 | 0 | 0 | 7.2 | 228.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21654.5 | 0 | 21654.5 | 954659 | -9904.96 | 69 | 77 | 954659 | -1009904.96
9 | 19 | 19 | 2 | 24.2047 | 0 | 62.7906 | 0 | 11.1493 | 0 | 11.8749 | 8.818 | 0 | 0 | 0 | 7.2 | 126.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15470.4 | 0 | 15470.4 | 193665 | 0 | 69 | 76 | 193665 | -1000000
9 | 19 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 9.2849 | 0 | 5.5073 | 8.818 | 0 | 0 | 0 | 7.2 | 104.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14783.5 | 0 | 14783.5 | 173278 | 0 | 69 | 75 | 173278 | -1000000
9 | 19 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 8.2903 | 0 | 5.4873 | 8.818 | 0 | 0 | 0 | 7.2 | 92.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9273.28 | 0 | 9273.28 | 160051 | 0 | 69 | 74 | 160051 | -1000000
9 | 19 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.7003 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 6.4 | 83.9297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9050.39 | 0 | 9050.39 | 149113 | 0 | 69 | 73 | 149113 | -1000000
9 | 19 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.7257 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 5.6 | 80.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7893.47 | 0 | 7893.47 | 144114 | 0 | 69 | 73 | 144114 | -1000000
9 | 19 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 7.3279 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 4.8 | 79.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7892.53 | 0 | 7892.53 | 142596 | 0 | 69 | 72 | 142596 | -1000000
9 | 20 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.5587 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 79.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7891.76 | 0 | 7891.76 | 141715 | 0 | 69 | 72 | 141715 | -1000000
9 | 20 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.2031 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 4.8 | 79.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7891.02 | 0 | 7891.02 | 140936 | 0 | 69 | 71 | 140936 | -1000000
9 | 20 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.4401 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 4.8 | 79.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7890.3 | 0 | 7890.3 | 140200 | 0 | 69 | 71 | 140200 | -1000000
9 | 20 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 7.6073 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 83.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8741.59 | 0 | 8741.59 | 143714 | 0 | 69 | 71 | 143714 | -1000000
9 | 20 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.7854 | 0 | 5.7865 | 12.8287 | 0 | 0 | 0 | 4.8 | 132.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10637.3 | 0 | 10637.3 | 286437 | 0 | 69 | 72 | 286437 | -1000000
9 | 20 | 6 | 3 | 48.9658 | 0 | 140.608 | 0 | 71.971 | 0 | 6.332 | 23.8681 | 0 | 0 | 0 | 2.4 | 294.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28500.7 | 0 | 28500.7 | 1375990 | -4649.42 | 69 | 72 | 1375990 | -1004649.42
9 | 20 | 7 | 3 | 42.3601 | 0 | 168.222 | 0 | 81.1706 | 0 | 6.332 | 23.5084 | 0 | 0 | 0 | 0.8 | 322.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31244.6 | 0 | 31244.6 | 1462700 | -21717.8 | 70 | 73 | 1462700 | -1021717.8
9 | 20 | 8 | 3 | 39.7817 | 0 | 173.795 | 0 | 78.8865 | 0 | 25.335 | 23.5743 | 0 | 0 | 0 | 0 | 341.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39510.8 | 0 | 39510.8 | 1406790 | -22097.1 | 70 | 74 | 1406790 | -1022097.1
9 | 20 | 9 | 3 | 40.6349 | 0 | 172.186 | 0 | 86.0064 | 0 | 25.335 | 23.3146 | 0 | 0 | 0 | 0 | 347.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61501 | 0 | 61501 | 1448720 | -22509.3 | 70 | 75 | 1448720 | -1022509.3
9 | 20 | 10 | 3 | 41.1517 | 0 | 163.102 | 0 | 91.0443 | 0 | 25.335 | 23.5023 | 0 | 0 | 0 | 0 | 344.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62875.9 | 0 | 62875.9 | 1538380 | -21500.6 | 71 | 78 | 1538380 | -1021500.6
9 | 20 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 87.8907 | 0 | 25.335 | 22.7215 | 0 | 0 | 0 | 0 | 326.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62878 | 0 | 62878 | 1472020 | -23087.7 | 72 | 81 | 1472020 | -1023087.7
9 | 20 | 12 | 3 | 39.7554 | 0 | 150.207 | 0 | 103.846 | 0 | 25.335 | 22.0129 | 0 | 0 | 0 | 0 | 341.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62879.2 | 0 | 62879.2 | 1628030 | -38581.7 | 73 | 84 | 1628030 | -1038581.7
9 | 20 | 13 | 3 | 41.2827 | 0 | 165.698 | 0 | 100.097 | 0 | 25.335 | 23.5281 | 0 | 0 | 0 | 0 | 355.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.3 | 0 | 62880.3 | 1650040 | -15685 | 73 | 81 | 1650040 | -1015685
9 | 20 | 14 | 3 | 40.659 | 0 | 172.702 | 0 | 97.5363 | 0 | 25.335 | 23.1007 | 0 | 0 | 0 | 0 | 359.333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61506.9 | 0 | 61506.9 | 1606620 | -21129 | 72 | 78 | 1606620 | -1021129
9 | 20 | 15 | 3 | 40.5711 | 0 | 173.986 | 0 | 94.9672 | 0 | 25.335 | 23.1125 | 0 | 0 | 0 | 0 | 357.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56010.2 | 0 | 56010.2 | 1571190 | -23237.9 | 71 | 75 | 1571190 | -1023237.9
9 | 20 | 16 | 3 | 40.3391 | 0 | 169.782 | 0 | 83.7045 | 0 | 25.335 | 23.0563 | 0 | 0 | 0 | 1.2 | 343.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46390.5 | 0 | 46390.5 | 1451860 | -23553.2 | 69 | 72 | 1451860 | -1023553.2
9 | 20 | 17 | 3 | 36.2127 | 0 | 152.497 | 0 | 69.3892 | 0 | 25.335 | 23.0055 | 0 | 0 | 0 | 4.8 | 311.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35396.5 | 0 | 35396.5 | 1255830 | -20798.9 | 68 | 70 | 1255830 | -1020798.9
9 | 20 | 18 | 3 | 32.8051 | 0 | 93.4203 | 0 | 43.0377 | 0 | 25.335 | 20.6156 | 0 | 0 | 0 | 7.2 | 222.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21654.2 | 0 | 21654.2 | 813979 | -17119.8 | 66 | 67 | 813979 | -1017119.8
9 | 20 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 10.3836 | 0 | 9.4757 | 8.818 | 0 | 0 | 0 | 7.2 | 122.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15469.9 | 0 | 15469.9 | 194425 | 0 | 64 | 65 | 194425 | -1000000
9 | 20 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.4757 | 0 | 5.4881 | 8.818 | 0 | 0 | 0 | 7.2 | 103.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14784.2 | 0 | 14784.2 | 173939 | 0 | 62 | 64 | 173939 | -1000000
9 | 20 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.4902 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9274.31 | 0 | 9274.31 | 160308 | 0 | 59 | 62 | 160308 | -1000000
9 | 20 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2066 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.49 | 0 | 9052.49 | 149432 | 0 | 59 | 61 | 149432 | -1000000
9 | 20 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.9288 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.34 | 0 | 7896.34 | 144276 | 0 | 58 | 59 | 144276 | -1000000
9 | 20 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 7.104 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.37 | 0 | 7896.37 | 142553 | 0 | 57 | 58 | 142553 | -1000000
9 | 21 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0491 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.5 | 0 | 7896.5 | 141361 | 0 | 55 | 56 | 141361 | -1000000
9 | 21 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 7.0019 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.75 | 0 | 7896.75 | 140330 | 0 | 53 | 54 | 140330 | -1000000
9 | 21 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9563 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.98 | 0 | 7896.98 | 139334 | 0 | 51 | 52 | 139334 | -1000000
9 | 21 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0838 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 4.8 | 82.8259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8748.99 | 0 | 8748.99 | 142188 | 0 | 50 | 52 | 142188 | -1000000
9 | 21 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 11.5242 | 0 | 5.5498 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10645.5 | 0 | 10645.5 | 241010 | 0 | 49 | 53 | 241010 | -1000000
9 | 21 | 6 | 4 | 48.9761 | 0 | 140.608 | 0 | 26.6315 | 0 | 6.332 | 20.1184 | 0 | 0 | 0 | 2.4 | 245.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28509.7 | 0 | 28509.7 | 502348 | -11249 | 49 | 53 | 502348 | -1011249
9 | 21 | 7 | 4 | 42.0204 | 0 | 168.222 | 0 | 31.115 | 0 | 6.332 | 20.0445 | 0 | 0 | 0 | 0.8 | 268.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31254.4 | 0 | 31254.4 | 572417 | -32966.7 | 48 | 54 | 572417 | -1032966.7
9 | 21 | 8 | 4 | 40.0387 | 0 | 173.795 | 0 | 33.1631 | 0 | 25.335 | 20.3905 | 0 | 0 | 0 | 0 | 292.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39515.3 | 0 | 39515.3 | 626784 | -33923.5 | 48 | 55 | 626784 | -1033923.5
9 | 21 | 9 | 4 | 40.7806 | 0 | 172.186 | 0 | 35.684 | 0 | 25.335 | 20.7904 | 0 | 0 | 0 | 0 | 294.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61504.1 | 0 | 61504.1 | 668835 | -31617 | 47 | 56 | 668835 | -1031617
9 | 21 | 10 | 4 | 41.1614 | 0 | 163.102 | 0 | 36.1583 | 0 | 25.335 | 21.074 | 0 | 0 | 0 | 0 | 286.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62880.1 | 0 | 62880.1 | 682395 | -27741 | 48 | 57 | 682395 | -1027741
9 | 21 | 11 | 4 | 40.7055 | 0 | 149.692 | 0 | 36.2619 | 0 | 25.335 | 20.9957 | 0 | 0 | 0 | 0 | 272.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62881.2 | 0 | 62881.2 | 686274 | -27774.5 | 48 | 58 | 686274 | -1027774.5
9 | 21 | 12 | 4 | 39.7703 | 0 | 150.207 | 0 | 39.0392 | 0 | 25.335 | 20.473 | 0 | 0 | 0 | 0 | 274.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882 | 0 | 62882 | 731135 | -44878.5 | 48 | 59 | 731135 | -1044878.5
9 | 21 | 13 | 4 | 41.3079 | 0 | 165.698 | 0 | 41.7134 | 0 | 25.335 | 21.3719 | 0 | 0 | 0 | 0 | 295.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62882.8 | 0 | 62882.8 | 774841 | -26173.1 | 49 | 60 | 774841 | -1026173.1
9 | 21 | 14 | 4 | 40.6965 | 0 | 172.702 | 0 | 44.1167 | 0 | 25.335 | 21.4499 | 0 | 0 | 0 | 0 | 304.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61509 | 0 | 61509 | 813840 | -25463.4 | 49 | 60 | 813840 | -1025463.4
9 | 21 | 15 | 4 | 40.5982 | 0 | 173.986 | 0 | 45.6268 | 0 | 25.335 | 21.5366 | 0 | 0 | 0 | 0 | 307.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56012.5 | 0 | 56012.5 | 837170 | -26421.2 | 49 | 61 | 837170 | -1026421.2
9 | 21 | 16 | 4 | 40.351 | 0 | 169.782 | 0 | 40.7738 | 0 | 25.335 | 21.3905 | 0 | 0 | 0 | 1.2 | 298.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46393.1 | 0 | 46393.1 | 774233 | -26952 | 49 | 59 | 774233 | -1026952
9 | 21 | 17 | 4 | 35.8992 | 0 | 152.497 | 0 | 33.7066 | 0 | 25.335 | 20.8729 | 0 | 0 | 0 | 4.8 | 273.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35399.2 | 0 | 35399.2 | 646809 | -24766.5 | 48 | 58 | 646809 | -1024766.5
9 | 21 | 18 | 4 | 26.9281 | 0 | 93.4203 | 0 | 21.4459 | 0 | 25.335 | 19.3158 | 0 | 0 | 0 | 7.2 | 193.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21656.5 | 0 | 21656.5 | 409768 | -24094.2 | 47 | 56 | 409768 | -1024094.2
9 | 21 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 10.4255 | 0 | 9.059 | 8.818 | 0 | 0 | 0 | 7.2 | 122.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15472.3 | 0 | 15472.3 | 192182 | 0 | 46 | 53 | 192182 | -1000000
9 | 21 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 9.2991 | 0 | 7.9888 | 8.818 | 0 | 0 | 0 | 7.2 | 106.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14787.2 | 0 | 14787.2 | 172354 | 0 | 45 | 50 | 172354 | -1000000
9 | 21 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 8.5999 | 0 | 7.4538 | 8.818 | 0 | 0 | 0 | 7.2 | 94.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9279.8 | 0 | 9279.8 | 158765 | 0 | 44 | 47 | 158765 | -1000000
9 | 21 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 8.0061 | 0 | 7.0639 | 8.818 | 0 | 0 | 0 | 6.4 | 85.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9059.4 | 0 | 9059.4 | 147422 | 0 | 43 | 45 | 147422 | -1000000
9 | 21 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.7501 | 0 | 6.9071 | 8.818 | 0 | 0 | 0 | 5.6 | 81.9331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7904.61 | 0 | 7904.61 | 142395 | 0 | 42 | 44 | 142395 | -1000000
9 | 21 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.6634 | 0 | 6.8562 | 8.818 | 0 | 0 | 0 | 4.8 | 81.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7905.76 | 0 | 7905.76 | 140712 | 0 | 41 | 42 | 140712 | -1000000
9 | 22 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.6117 | 0 | 6.8263 | 8.818 | 0 | 0 | 0 | 4.8 | 81.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7906.55 | 0 | 7906.55 | 139686 | 0 | 41 | 41 | 139686 | -1000000
9 | 22 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.5525 | 0 | 6.7926 | 8.818 | 0 | 0 | 0 | 4.8 | 81.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.43 | 0 | 7907.43 | 138498 | 0 | 40 | 41 | 138498 | -1000000
9 | 22 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 7.5147 | 0 | 6.7713 | 8.818 | 0 | 0 | 0 | 4.8 | 81.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.26 | 0 | 7908.26 | 137747 | 0 | 40 | 40 | 137747 | -1000000
9 | 22 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 7.6364 | 0 | 6.8405 | 8.818 | 0 | 0 | 0 | 4.8 | 84.7394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8761.08 | 0 | 8761.08 | 140241 | 0 | 40 | 40 | 140241 | -1000000
9 | 22 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.156 | 0 | 10.3025 | 12.9754 | 0 | 0 | 0 | 4.8 | 133.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10658.2 | 0 | 10658.2 | 211977 | -3432.16 | 39 | 39 | 211977 | -1003432.16
9 | 22 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 20.2957 | 0 | 6.33 | 19.0363 | 0 | 0 | 0 | 2.4 | 237.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28523.2 | 0 | 28523.2 | 331430 | -36323.3 | 39 | 39 | 331430 | -1036323.3
9 | 22 | 7 | 5 | 47.5109 | 0 | 168.222 | 0 | 30.9234 | 0 | 25.335 | 19.1508 | 0 | 0 | 0 | 0.8 | 291.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31268.4 | 0 | 31268.4 | 455132 | -122665 | 41 | 41 | 455132 | -1122665
9 | 22 | 8 | 5 | 39.8765 | 0 | 173.795 | 0 | 31.2696 | 0 | 25.335 | 19.1591 | 0 | 0 | 0 | 0 | 289.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39523 | 0 | 39523 | 499963 | -113621 | 43 | 43 | 499963 | -1113621
9 | 22 | 9 | 5 | 40.6339 | 0 | 172.186 | 0 | 35.4242 | 0 | 25.335 | 19.2548 | 0 | 0 | 0 | 0 | 292.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61510.8 | 0 | 61510.8 | 558153 | -106537 | 45 | 45 | 558153 | -1106537
9 | 22 | 10 | 5 | 41.153 | 0 | 163.102 | 0 | 32.0191 | 0 | 25.335 | 19.6184 | 0 | 0 | 0 | 0 | 281.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62885.4 | 0 | 62885.4 | 534161 | -59242.9 | 48 | 50 | 534161 | -1059242.9
9 | 22 | 11 | 5 | 40.7055 | 0 | 149.692 | 0 | 30.7333 | 0 | 25.335 | 19.9998 | 0 | 0 | 0 | 0 | 266.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62885.3 | 0 | 62885.3 | 545427 | -27945.9 | 49 | 56 | 545427 | -1027945.9
9 | 22 | 12 | 5 | 39.7638 | 0 | 150.207 | 0 | 38.1662 | 0 | 25.335 | 20.2159 | 0 | 0 | 0 | 0 | 273.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62885.1 | 0 | 62885.1 | 656749 | -37745.7 | 51 | 61 | 656749 | -1037745.7
9 | 22 | 13 | 5 | 41.2885 | 0 | 165.698 | 0 | 40.9355 | 0 | 20.5939 | 21.2561 | 0 | 0 | 0 | 0 | 289.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62885.8 | 0 | 62885.8 | 724919 | -20002.6 | 52 | 62 | 724919 | -1020002.6
9 | 22 | 14 | 5 | 40.6776 | 0 | 172.702 | 0 | 43.77 | 0 | 25.335 | 21.3461 | 0 | 0 | 0 | 0 | 303.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61512.4 | 0 | 61512.4 | 789840 | -18839.3 | 52 | 63 | 789840 | -1018839.3
9 | 22 | 15 | 5 | 40.5811 | 0 | 173.986 | 0 | 46.3373 | 0 | 25.335 | 21.4727 | 0 | 0 | 0 | 0 | 307.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56015.6 | 0 | 56015.6 | 839407 | -20543.4 | 53 | 64 | 839407 | -1020543.4
9 | 22 | 16 | 5 | 40.3386 | 0 | 169.782 | 0 | 41.046 | 0 | 25.335 | 21.3439 | 0 | 0 | 0 | 1.2 | 299.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46396 | 0 | 46396 | 775865 | -20906 | 52 | 62 | 775865 | -1020906
9 | 22 | 17 | 5 | 35.5496 | 0 | 152.497 | 0 | 33.0033 | 0 | 25.335 | 20.7249 | 0 | 0 | 0 | 4.8 | 271.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35402 | 0 | 35402 | 644495 | -19360.5 | 52 | 60 | 644495 | -1019360.5
9 | 22 | 18 | 5 | 27.6644 | 0 | 93.4203 | 0 | 21.0258 | 0 | 25.335 | 19.2266 | 0 | 0 | 0 | 7.2 | 193.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21659.2 | 0 | 21659.2 | 402080 | -18416 | 51 | 58 | 402080 | -1018416
9 | 22 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 10.3959 | 0 | 9.018 | 8.818 | 0 | 0 | 0 | 7.2 | 122.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15475.2 | 0 | 15475.2 | 191387 | 0 | 50 | 55 | 191387 | -1000000
9 | 22 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 9.0719 | 0 | 7.8957 | 8.818 | 0 | 0 | 0 | 7.2 | 106.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14790 | 0 | 14790 | 171457 | 0 | 48 | 51 | 171457 | -1000000
9 | 22 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.9964 | 0 | 7.2773 | 8.818 | 0 | 0 | 0 | 7.2 | 94.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9282.9 | 0 | 9282.9 | 157860 | 0 | 46 | 48 | 157860 | -1000000
9 | 22 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.305 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9062.52 | 0 | 9062.52 | 146797 | 0 | 46 | 47 | 146797 | -1000000
9 | 22 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.0678 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.77 | 0 | 7907.77 | 141706 | 0 | 45 | 47 | 141706 | -1000000
9 | 22 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.981 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.05 | 0 | 7909.05 | 139860 | 0 | 44 | 46 | 139860 | -1000000
9 | 23 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.0975 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7910.33 | 0 | 7910.33 | 138969 | -6292.55 | 45 | 46 | 138969 | -1006292.55
9 | 23 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8876 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.23 | 0 | 7912.23 | 137827 | 0 | 45 | 45 | 137827 | -1000000
9 | 23 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.853 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.5077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.82 | 0 | 7913.82 | 137076 | -1840.85 | 45 | 45 | 137076 | -1001840.85
9 | 23 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8055 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.45 | 0 | 7915.45 | 136032 | 0 | 45 | 45 | 136032 | -1000000
9 | 23 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7669 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7916.82 | 0 | 7916.82 | 135192 | 0 | 44 | 44 | 135192 | -1000000
9 | 23 | 6 | 6 | 6.3798 | 0 | 42.7453 | 0 | 9.1078 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 2.4 | 79.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.25 | 0 | 7918.25 | 141145 | -5519.84 | 44 | 44 | 141145 | -1005519.84
9 | 23 | 7 | 6 | 5.0887 | 0 | 42.7453 | 0 | 13.3572 | 0 | 5.9391 | 18.8896 | 0 | 0 | 0 | 0.8 | 86.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.27 | 0 | 7919.27 | 183539 | -77393.9 | 46 | 47 | 183539 | -1077393.9
9 | 23 | 8 | 6 | 4.9881 | 0 | 42.7453 | 0 | 17.1502 | 0 | 14.6077 | 18.8896 | 0 | 0 | 0 | 0 | 98.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.18 | 0 | 7920.18 | 222907 | -165761 | 49 | 51 | 222907 | -1165761
9 | 23 | 9 | 6 | 5.4929 | 0 | 42.7453 | 0 | 17.5738 | 0 | 6.0558 | 18.8896 | 0 | 0 | 0 | 0 | 90.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.78 | 0 | 7925.78 | 224082 | -124236 | 51 | 54 | 224082 | -1124236
9 | 23 | 10 | 6 | 5.4716 | 0 | 42.7453 | 0 | 16.827 | 0 | 6.0415 | 18.8896 | 0 | 0 | 0 | 0 | 89.9749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7926.51 | 0 | 7926.51 | 226791 | -83349.4 | 53 | 58 | 226791 | -1083349.4
9 | 23 | 11 | 6 | 5.4689 | 0 | 42.7453 | 0 | 18.6812 | 0 | 6.1927 | 18.8896 | 0 | 0 | 0 | 0 | 91.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.6 | 0 | 7927.6 | 259291 | -59770.1 | 55 | 63 | 259291 | -1059770.1
9 | 23 | 12 | 6 | 5.4715 | 0 | 42.7453 | 0 | 23.8674 | 0 | 6.332 | 18.8959 | 0 | 0 | 0 | 0 | 97.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.07 | 0 | 7928.07 | 336980 | -58547.9 | 57 | 67 | 336980 | -1058547.9
9 | 23 | 13 | 6 | 5.4777 | 0 | 42.7453 | 0 | 26.5331 | 0 | 6.332 | 18.9653 | 0 | 0 | 0 | 0 | 100.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.45 | 0 | 7928.45 | 386702 | -57688.1 | 58 | 68 | 386702 | -1057688.1
9 | 23 | 14 | 6 | 5.4786 | 0 | 42.7453 | 0 | 10.691 | 0 | 9.8033 | 12.8287 | 0 | 0 | 0 | 0 | 81.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.7 | 0 | 7928.7 | 177408 | 0 | 58 | 69 | 177408 | -1000000
9 | 23 | 15 | 6 | 5.4799 | 0 | 42.7453 | 0 | 10.3914 | 0 | 9.5381 | 12.8287 | 0 | 0 | 0 | 0 | 80.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7928.91 | 0 | 7928.91 | 174736 | 0 | 59 | 70 | 174736 | -1000000
9 | 23 | 16 | 6 | 5.4792 | 0 | 42.7453 | 0 | 9.2192 | 0 | 8.2994 | 12.8287 | 0 | 0 | 0 | 1.2 | 79.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.28 | 0 | 7925.28 | 174994 | 0 | 58 | 68 | 174994 | -1000000
9 | 23 | 17 | 6 | 5.4992 | 0 | 42.7453 | 0 | 6.814 | 0 | 6.5273 | 8.818 | 0 | 0 | 0 | 4.8 | 75.2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7922.36 | 0 | 7922.36 | 130033 | 0 | 58 | 66 | 130033 | -1000000
9 | 23 | 18 | 6 | 8.0549 | 0 | 42.7453 | 0 | 6.2007 | 0 | 6.341 | 8.818 | 0 | 0 | 0 | 7.2 | 79.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920.75 | 0 | 7920.75 | 129709 | 0 | 57 | 64 | 129709 | -1000000
9 | 23 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3556 | 0 | 5.4842 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.52 | 0 | 7919.52 | 129606 | 0 | 57 | 63 | 129606 | -1000000
9 | 23 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3102 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 7.2 | 79.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.05 | 0 | 7919.05 | 129363 | 0 | 57 | 62 | 129363 | -1000000
9 | 23 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.2656 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 7.2 | 79.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.89 | 0 | 7918.89 | 129123 | 0 | 57 | 61 | 129123 | -1000000
9 | 23 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.5165 | 0 | 5.4833 | 8.818 | 0 | 0 | 0 | 6.4 | 78.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7918.95 | 0 | 7918.95 | 128972 | 0 | 58 | 61 | 128972 | -1000000
9 | 23 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.2122 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 5.6 | 77.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.06 | 0 | 7919.06 | 128674 | 0 | 58 | 60 | 128674 | -1000000
9 | 23 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.4511 | 0 | 5.4843 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3109.71 | 0 | 3109.71 | 128287 | 0 | 58 | 60 | 128287 | -1000000
9 | 24 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4383 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3109.89 | 0 | 3109.89 | 128009 | 0 | 58 | 60 | 128009 | -1000000
9 | 24 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4333 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3110.28 | 0 | 3110.28 | 127902 | 0 | 59 | 59 | 127902 | -1000000
9 | 24 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4181 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3110.65 | 0 | 3110.65 | 127565 | 0 | 59 | 59 | 127565 | -1000000
9 | 24 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.4069 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3111.02 | 0 | 3111.02 | 127322 | 0 | 59 | 59 | 127322 | -1000000
9 | 24 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.395 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 4.8 | 73.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3111.42 | 0 | 3111.42 | 127062 | 0 | 59 | 60 | 127062 | -1000000
9 | 24 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3862 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 2.4 | 70.9398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3111.84 | 0 | 3111.84 | 126869 | 0 | 59 | 60 | 126869 | -1000000
9 | 24 | 7 | 7 | 4.7714 | 0 | 42.7453 | 0 | 6.6739 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 0.8 | 69.2905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.25 | 0 | 3112.25 | 126786 | 0 | 60 | 61 | 126786 | -1000000
9 | 24 | 8 | 7 | 4.4049 | 0 | 42.7453 | 0 | 6.4059 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 0 | 67.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.61 | 0 | 3112.61 | 126564 | 0 | 60 | 61 | 126564 | -1000000
9 | 24 | 9 | 7 | 4.7557 | 0 | 42.7453 | 0 | 6.6967 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 0 | 68.4972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.95 | 0 | 3112.95 | 126508 | 0 | 61 | 62 | 126508 | -1000000
9 | 24 | 10 | 7 | 4.648 | 0 | 42.7453 | 0 | 6.7303 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 0 | 68.4225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3113.17 | 0 | 3113.17 | 126449 | 0 | 62 | 63 | 126449 | -1000000
9 | 24 | 11 | 7 | 4.511 | 0 | 42.7453 | 0 | 7.0616 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 0 | 68.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3113.2 | 0 | 3113.2 | 126302 | 0 | 63 | 65 | 126302 | -1000000
9 | 24 | 12 | 7 | 4.4315 | 0 | 42.7453 | 0 | 6.8381 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 0 | 68.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.93 | 0 | 3112.93 | 126344 | 0 | 65 | 66 | 126344 | -1000000
9 | 24 | 13 | 7 | 4.1491 | 0 | 42.7453 | 0 | 7.4901 | 0 | 6.2677 | 8.818 | 0 | 0 | 0 | 0 | 69.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.56 | 0 | 3112.56 | 126221 | 0 | 66 | 69 | 126221 | -1000000
9 | 24 | 14 | 7 | 4.1494 | 0 | 42.7453 | 0 | 9.7354 | 0 | 9.2459 | 12.8287 | 0 | 0 | 0 | 0 | 78.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3111.94 | 0 | 3111.94 | 167025 | 0 | 67 | 71 | 167025 | -1000000
9 | 24 | 15 | 7 | 4.1496 | 0 | 42.7453 | 0 | 11.1312 | 0 | 11.1106 | 12.8287 | 0 | 0 | 0 | 0 | 81.9654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3111.19 | 0 | 3111.19 | 178604 | 0 | 68 | 74 | 178604 | -1000000
9 | 24 | 16 | 7 | 4.1505 | 0 | 42.7453 | 0 | 6.482 | 0 | 6.5918 | 8.818 | 0 | 0 | 0 | 1.2 | 69.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3110.17 | 0 | 3110.17 | 126053 | 0 | 67 | 72 | 126053 | -1000000
9 | 24 | 17 | 7 | 4.1554 | 0 | 42.7453 | 0 | 6.4809 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 72.4803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3108.82 | 0 | 3108.82 | 126089 | 0 | 67 | 71 | 126089 | -1000000
9 | 24 | 18 | 7 | 5.6109 | 0 | 42.7453 | 0 | 6.1331 | 0 | 5.4844 | 8.818 | 0 | 0 | 0 | 7.2 | 75.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3107.74 | 0 | 3107.74 | 126037 | 0 | 66 | 69 | 126037 | -1000000
9 | 24 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.0631 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 7.2 | 76.9757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.68 | 0 | 3106.68 | 126045 | 0 | 66 | 67 | 126045 | -1000000
9 | 24 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2894 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.1 | 0 | 3106.1 | 125948 | 0 | 65 | 66 | 125948 | -1000000
9 | 24 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.9521 | 0 | 5.4886 | 8.818 | 0 | 0 | 0 | 7.2 | 76.8674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.78 | 0 | 3105.78 | 125831 | 0 | 64 | 64 | 125831 | -1000000
9 | 24 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.1725 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 6.4 | 76.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.64 | 0 | 3105.64 | 125662 | 0 | 63 | 63 | 125662 | -1000000
9 | 24 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.4325 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 5.6 | 75.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3105.57 | 0 | 3105.57 | 125649 | 0 | 63 | 63 | 125649 | -1000000
9 | 24 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.1442 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.12 | 0 | 7915.12 | 125774 | 0 | 62 | 62 | 125774 | -1000000
9 | 25 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.4063 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.22 | 0 | 7915.22 | 125835 | 0 | 62 | 62 | 125835 | -1000000
9 | 25 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.4033 | 0 | 5.484 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.5 | 0 | 7914.5 | 125768 | 0 | 62 | 62 | 125768 | -1000000
9 | 25 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.3998 | 0 | 5.4841 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.23 | 0 | 7914.23 | 125691 | 0 | 62 | 62 | 125691 | -1000000
9 | 25 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.2721 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 82.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8765.97 | 0 | 8765.97 | 129328 | 0 | 61 | 61 | 129328 | -1000000
9 | 25 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 11.3258 | 0 | 5.545 | 12.8287 | 0 | 0 | 0 | 4.8 | 128.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10662.1 | 0 | 10662.1 | 235485 | 0 | 61 | 61 | 235485 | -1000000
9 | 25 | 6 | 1 | 49.0171 | 0 | 140.608 | 0 | 40.7825 | 0 | 6.332 | 20.3541 | 0 | 0 | 0 | 2.4 | 259.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28525.9 | 0 | 28525.9 | 682354 | -13258.3 | 60 | 60 | 682354 | -1013258.3
9 | 25 | 7 | 1 | 48.843 | 0 | 168.222 | 0 | 48.9257 | 0 | 6.332 | 20.3228 | 0 | 0 | 0 | 0.8 | 293.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31270.2 | 0 | 31270.2 | 809792 | -16078.3 | 61 | 61 | 809792 | -1016078.3
9 | 25 | 8 | 1 | 40.9132 | 0 | 173.795 | 0 | 48.6953 | 0 | 6.332 | 20.2529 | 0 | 0 | 0 | 0 | 289.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39525.1 | 0 | 39525.1 | 840922 | -13931 | 62 | 62 | 840922 | -1013931
9 | 25 | 9 | 1 | 41.6083 | 0 | 172.186 | 0 | 48.1658 | 0 | 6.332 | 20.5374 | 0 | 0 | 0 | 0 | 288.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61512.7 | 0 | 61512.7 | 861521 | -12674.3 | 62 | 63 | 861521 | -1012674.3
9 | 25 | 10 | 1 | 42.0752 | 0 | 163.102 | 0 | 46.7115 | 0 | 6.332 | 20.5434 | 0 | 0 | 0 | 0 | 278.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62887.1 | 0 | 62887.1 | 861803 | -11980.7 | 62 | 62 | 861803 | -1011980.7
9 | 25 | 11 | 1 | 41.3338 | 0 | 149.692 | 0 | 41.3018 | 0 | 6.332 | 20.4312 | 0 | 0 | 0 | 0 | 259.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62887 | 0 | 62887 | 777431 | -9755.11 | 62 | 62 | 777431 | -1009755.11
9 | 25 | 12 | 1 | 39.9718 | 0 | 150.207 | 0 | 37.6597 | 0 | 6.332 | 20.3222 | 0 | 0 | 0 | 0 | 254.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62887.2 | 0 | 62887.2 | 734446 | -9667.25 | 61 | 61 | 734446 | -1009667.25
9 | 25 | 13 | 1 | 41.8872 | 0 | 165.698 | 0 | 46.4459 | 0 | 6.332 | 20.6871 | 0 | 0 | 0 | 0 | 281.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62887.5 | 0 | 62887.5 | 867941 | -13125.5 | 62 | 62 | 867941 | -1013125.5
9 | 25 | 14 | 1 | 41.1465 | 0 | 172.702 | 0 | 49.7221 | 0 | 6.332 | 21.0825 | 0 | 0 | 0 | 0 | 290.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61513.3 | 0 | 61513.3 | 911001 | -14850.9 | 62 | 64 | 911001 | -1014850.9
9 | 25 | 15 | 1 | 41.1539 | 0 | 173.986 | 0 | 53.6508 | 0 | 6.332 | 21.4812 | 0 | 0 | 0 | 0 | 296.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56015.9 | 0 | 56015.9 | 986185 | -15507.3 | 63 | 65 | 986185 | -1015507.3
9 | 25 | 16 | 1 | 41.6415 | 0 | 169.782 | 0 | 53.4023 | 0 | 6.332 | 21.1077 | 0 | 0 | 0 | 1.2 | 293.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46395.7 | 0 | 46395.7 | 988865 | -15421.5 | 63 | 65 | 988865 | -1015421.5
9 | 25 | 17 | 1 | 37.8732 | 0 | 152.497 | 0 | 47.7199 | 0 | 6.332 | 20.7008 | 0 | 0 | 0 | 4.8 | 269.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35401.6 | 0 | 35401.6 | 907835 | -12727.4 | 64 | 65 | 907835 | -1012727.4
9 | 25 | 18 | 1 | 31.8694 | 0 | 93.4203 | 0 | 31.2942 | 0 | 6.332 | 19.4973 | 0 | 0 | 0 | 7.2 | 189.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21659.5 | 0 | 21659.5 | 614762 | -9540.12 | 64 | 65 | 614762 | -1009540.12
9 | 25 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 9.0878 | 0 | 5.4913 | 8.818 | 0 | 0 | 0 | 7.2 | 117.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15476.3 | 0 | 15476.3 | 186950 | 0 | 63 | 63 | 186950 | -1000000
9 | 25 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.0641 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 7.2 | 102.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14790.9 | 0 | 14790.9 | 167019 | 0 | 62 | 62 | 167019 | -1000000
9 | 25 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.1102 | 0 | 5.4795 | 8.818 | 0 | 0 | 0 | 7.2 | 91.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9283.21 | 0 | 9283.21 | 153725 | 0 | 60 | 60 | 153725 | -1000000
9 | 25 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.1313 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9062.15 | 0 | 9062.15 | 143002 | 0 | 59 | 59 | 143002 | -1000000
9 | 25 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.9015 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 79.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7906.6 | 0 | 7906.6 | 138068 | 0 | 57 | 57 | 138068 | -1000000
9 | 25 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.8346 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.05 | 0 | 7907.05 | 136663 | 0 | 56 | 56 | 136663 | -1000000
9 | 26 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7983 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 78.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.49 | 0 | 7907.49 | 135878 | 0 | 55 | 55 | 135878 | -1000000
9 | 26 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7641 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.01 | 0 | 7908.01 | 135131 | 0 | 54 | 54 | 135131 | -1000000
9 | 26 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7334 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7908.51 | 0 | 7908.51 | 134461 | 0 | 53 | 53 | 134461 | -1000000
9 | 26 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.8685 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8761.05 | 0 | 8761.05 | 137478 | 0 | 52 | 52 | 137478 | -1000000
9 | 26 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.9787 | 0 | 5.9537 | 12.8287 | 0 | 0 | 0 | 4.8 | 130.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10658 | 0 | 10658 | 208081 | -2064.17 | 51 | 52 | 208081 | -1002064.17
9 | 26 | 6 | 2 | 49.0171 | 0 | 140.608 | 0 | 23.547 | 0 | 6.332 | 19.5578 | 0 | 0 | 0 | 2.4 | 241.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28522.8 | 0 | 28522.8 | 386863 | -20952.5 | 50 | 51 | 386863 | -1020952.5
9 | 26 | 7 | 2 | 49.3903 | 0 | 168.222 | 0 | 27.6472 | 0 | 6.332 | 19.2469 | 0 | 0 | 0 | 0.8 | 271.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31268.1 | 0 | 31268.1 | 470414 | -45141.4 | 49 | 50 | 470414 | -1045141.4
9 | 26 | 8 | 2 | 41.3192 | 0 | 173.795 | 0 | 29.0218 | 0 | 6.332 | 19.211 | 0 | 0 | 0 | 0 | 269.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39523.5 | 0 | 39523.5 | 514779 | -68904.1 | 48 | 49 | 514779 | -1068904.1
9 | 26 | 9 | 2 | 41.4957 | 0 | 172.186 | 0 | 28.8837 | 0 | 25.335 | 19.2154 | 0 | 0 | 0 | 0 | 287.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61511.3 | 0 | 61511.3 | 505426 | -74895.6 | 46 | 48 | 505426 | -1074895.6
9 | 26 | 10 | 2 | 41.7772 | 0 | 163.102 | 0 | 27.817 | 0 | 25.335 | 19.237 | 0 | 0 | 0 | 0 | 277.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62886 | 0 | 62886 | 491270 | -62179.1 | 47 | 49 | 491270 | -1062179.1
9 | 26 | 11 | 2 | 41.1014 | 0 | 149.692 | 0 | 27.3886 | 0 | 25.335 | 19.1134 | 0 | 0 | 0 | 0 | 262.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62886.2 | 0 | 62886.2 | 484686 | -67844.5 | 47 | 50 | 484686 | -1067844.5
9 | 26 | 12 | 2 | 39.8448 | 0 | 150.207 | 0 | 24.976 | 0 | 25.335 | 19.1181 | 0 | 0 | 0 | 0 | 259.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62886.6 | 0 | 62886.6 | 458956 | -57089.6 | 47 | 51 | 458956 | -1057089.6
9 | 26 | 13 | 2 | 41.6324 | 0 | 165.698 | 0 | 29.5047 | 0 | 25.335 | 19.2544 | 0 | 0 | 0 | 0 | 281.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62887.1 | 0 | 62887.1 | 522255 | -61496.2 | 47 | 51 | 522255 | -1061496.2
9 | 26 | 14 | 2 | 40.9063 | 0 | 172.702 | 0 | 28.6336 | 0 | 25.335 | 19.4366 | 0 | 0 | 0 | 0 | 287.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61513.1 | 0 | 61513.1 | 530973 | -49820.7 | 47 | 51 | 530973 | -1049820.7
9 | 26 | 15 | 2 | 41.0636 | 0 | 173.986 | 0 | 28.0795 | 0 | 25.335 | 19.6246 | 0 | 0 | 0 | 0 | 288.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56015.8 | 0 | 56015.8 | 518294 | -38513.3 | 47 | 51 | 518294 | -1038513.3
9 | 26 | 16 | 2 | 41.5518 | 0 | 169.782 | 0 | 26.8539 | 0 | 25.335 | 19.5525 | 0 | 0 | 0 | 1.2 | 284.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46395.7 | 0 | 46395.7 | 509553 | -37364.2 | 47 | 51 | 509553 | -1037364.2
9 | 26 | 17 | 2 | 37.8732 | 0 | 152.497 | 0 | 23.4406 | 0 | 25.335 | 19.2015 | 0 | 0 | 0 | 4.8 | 263.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35401.7 | 0 | 35401.7 | 442873 | -49552.6 | 46 | 50 | 442873 | -1049552.6
9 | 26 | 18 | 2 | 31.9477 | 0 | 93.4203 | 0 | 20.4871 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 7.2 | 197.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21659.8 | 0 | 21659.8 | 362416 | -86688.8 | 46 | 50 | 362416 | -1086688.8
9 | 26 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.8234 | 0 | 8.7048 | 8.818 | 0 | 0 | 0 | 7.2 | 121.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15476.8 | 0 | 15476.8 | 188855 | 0 | 46 | 50 | 188855 | -1000000
9 | 26 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.3357 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 7.2 | 103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14791.7 | 0 | 14791.7 | 169215 | 0 | 45 | 49 | 169215 | -1000000
9 | 26 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.7212 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9286.72 | 0 | 9286.72 | 155870 | 0 | 45 | 49 | 155870 | -1000000
9 | 26 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.2123 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9066.95 | 0 | 9066.95 | 144769 | 0 | 45 | 49 | 144769 | -1000000
9 | 26 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 9.3007 | 0 | 5.897 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.7 | 0 | 7912.7 | 139836 | -6617.86 | 44 | 48 | 139836 | -1006617.86
9 | 26 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.9096 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.12 | 0 | 7914.12 | 138303 | 0 | 44 | 48 | 138303 | -1000000
9 | 27 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8662 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.42 | 0 | 7915.42 | 137361 | -1516.14 | 43 | 46 | 137361 | -1001516.14
9 | 27 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8291 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7916.78 | 0 | 7916.78 | 136553 | 0 | 43 | 44 | 136553 | -1000000
9 | 27 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7868 | 0 | 5.8995 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7917.92 | 0 | 7917.92 | 135626 | -2709.45 | 42 | 42 | 135626 | -1002709.45
9 | 27 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9028 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8771.24 | 0 | 8771.24 | 138221 | 0 | 41 | 42 | 138221 | -1000000
9 | 27 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 9.3142 | 0 | 5.9106 | 12.9754 | 0 | 0 | 0 | 4.8 | 127.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10668.8 | 0 | 10668.8 | 191858 | -4027.65 | 41 | 41 | 191858 | -1004027.65
9 | 27 | 6 | 3 | 49.0171 | 0 | 140.608 | 0 | 21.3028 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 238.696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28534.2 | 0 | 28534.2 | 329854 | -70757.8 | 41 | 41 | 329854 | -1070757.8
9 | 27 | 7 | 3 | 45.728 | 0 | 168.222 | 0 | 32.1212 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31279.6 | 0 | 31279.6 | 463474 | -161721 | 43 | 44 | 463474 | -1161721
9 | 27 | 8 | 3 | 39.9619 | 0 | 173.795 | 0 | 31.5388 | 0 | 6.332 | 19.0564 | 0 | 0 | 0 | 0 | 270.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39529.5 | 0 | 39529.5 | 493046 | -125490 | 45 | 46 | 493046 | -1125490
9 | 27 | 9 | 3 | 40.6858 | 0 | 172.186 | 0 | 31.7319 | 0 | 6.332 | 19.0913 | 0 | 0 | 0 | 0 | 270.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61516.9 | 0 | 61516.9 | 505595 | -101712 | 46 | 49 | 505595 | -1101712
9 | 27 | 10 | 3 | 41.1823 | 0 | 163.102 | 0 | 30.3369 | 0 | 6.332 | 19.1767 | 0 | 0 | 0 | 0 | 260.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62890.9 | 0 | 62890.9 | 492523 | -60188 | 48 | 52 | 492523 | -1060188
9 | 27 | 11 | 3 | 40.7055 | 0 | 149.692 | 0 | 29.5518 | 0 | 25.335 | 19.2708 | 0 | 0 | 0 | 0 | 264.555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62890.4 | 0 | 62890.4 | 506905 | -52044.1 | 50 | 54 | 506905 | -1052044.1
9 | 27 | 12 | 3 | 39.7782 | 0 | 150.207 | 0 | 30.5768 | 0 | 25.335 | 19.6602 | 0 | 0 | 0 | 0 | 265.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62890.2 | 0 | 62890.2 | 541935 | -40160.2 | 51 | 57 | 541935 | -1040160.2
9 | 27 | 13 | 3 | 41.2981 | 0 | 165.698 | 0 | 34.0546 | 0 | 8.9174 | 20.973 | 0 | 0 | 0 | 0 | 270.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62890.3 | 0 | 62890.3 | 621373 | -15389.9 | 52 | 59 | 621373 | -1015389.9
9 | 27 | 14 | 3 | 40.7006 | 0 | 172.702 | 0 | 38.6741 | 0 | 25.335 | 21.1384 | 0 | 0 | 0 | 0 | 298.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61516.1 | 0 | 61516.1 | 712843 | -13946 | 53 | 61 | 712843 | -1013946
9 | 27 | 15 | 3 | 40.5936 | 0 | 173.986 | 0 | 43.6749 | 0 | 25.335 | 21.1922 | 0 | 0 | 0 | 0 | 304.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56019 | 0 | 56019 | 790628 | -17751.4 | 54 | 63 | 790628 | -1017751.4
9 | 27 | 16 | 3 | 40.3458 | 0 | 169.782 | 0 | 38.2121 | 0 | 25.335 | 21.0463 | 0 | 0 | 0 | 1.2 | 295.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46398.9 | 0 | 46398.9 | 731694 | -15842.3 | 54 | 61 | 731694 | -1015842.3
9 | 27 | 17 | 3 | 35.6252 | 0 | 152.497 | 0 | 30.7561 | 0 | 25.335 | 20.4313 | 0 | 0 | 0 | 4.8 | 269.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35404.8 | 0 | 35404.8 | 604696 | -14661.9 | 53 | 60 | 604696 | -1014661.9
9 | 27 | 18 | 3 | 29.6671 | 0 | 93.4203 | 0 | 18.7093 | 0 | 6.332 | 19.131 | 0 | 0 | 0 | 7.2 | 174.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21661.8 | 0 | 21661.8 | 376490 | -16109.1 | 53 | 58 | 376490 | -1016109.1
9 | 27 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.4339 | 0 | 5.4944 | 8.818 | 0 | 0 | 0 | 7.2 | 117.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15478.5 | 0 | 15478.5 | 190487 | 0 | 53 | 57 | 190487 | -1000000
9 | 27 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.3966 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 7.2 | 103.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14793.2 | 0 | 14793.2 | 170543 | 0 | 52 | 56 | 170543 | -1000000
9 | 27 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.7839 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9287.04 | 0 | 9287.04 | 157242 | 0 | 52 | 55 | 157242 | -1000000
9 | 27 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2735 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9066.81 | 0 | 9066.81 | 146106 | 0 | 52 | 55 | 146106 | -1000000
9 | 27 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.045 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.02 | 0 | 7912.02 | 141208 | 0 | 52 | 55 | 141208 | -1000000
9 | 27 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.9707 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.01 | 0 | 7913.01 | 139639 | 0 | 52 | 55 | 139639 | -1000000
9 | 28 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9321 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7913.86 | 0 | 7913.86 | 138807 | 0 | 53 | 56 | 138807 | -1000000
9 | 28 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8979 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.63 | 0 | 7914.63 | 138058 | 0 | 54 | 56 | 138058 | -1000000
9 | 28 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8622 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.28 | 0 | 7915.28 | 137278 | 0 | 55 | 57 | 137278 | -1000000
9 | 28 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 7.0033 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 4.8 | 82.7458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8767.83 | 0 | 8767.83 | 140430 | 0 | 56 | 58 | 140430 | -1000000
9 | 28 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 9.1156 | 0 | 5.4895 | 8.818 | 0 | 0 | 0 | 4.8 | 122.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10664.7 | 0 | 10664.7 | 187401 | 0 | 57 | 59 | 187401 | -1000000
9 | 28 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 39.8497 | 0 | 6.332 | 19.4651 | 0 | 0 | 0 | 2.4 | 257.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28529.2 | 0 | 28529.2 | 485544 | -30218 | 59 | 60 | 485544 | -1030218
9 | 28 | 7 | 4 | 49.9907 | 0 | 168.222 | 0 | 33.4753 | 0 | 6.332 | 19.3475 | 0 | 0 | 0 | 0.8 | 278.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31274.1 | 0 | 31274.1 | 706763 | -16660 | 60 | 61 | 706763 | -1016660
9 | 28 | 8 | 4 | 40.4454 | 0 | 173.795 | 0 | 37.0704 | 0 | 6.332 | 19.3931 | 0 | 0 | 0 | 0 | 277.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39527 | 0 | 39527 | 775572 | -20281.6 | 62 | 62 | 775572 | -1020281.6
9 | 28 | 9 | 4 | 42.8181 | 0 | 172.186 | 0 | 40.0502 | 0 | 10.9225 | 19.5417 | 0 | 0 | 0 | 0 | 285.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61514.3 | 0 | 61514.3 | 832800 | -17667.1 | 63 | 63 | 832800 | -1017667.1
9 | 28 | 10 | 4 | 41.604 | 0 | 163.102 | 0 | 50.735 | 0 | 7.0656 | 19.8652 | 0 | 0 | 0 | 0 | 282.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62888.5 | 0 | 62888.5 | 884587 | -16038.6 | 64 | 64 | 884587 | -1016038.6
9 | 28 | 11 | 4 | 41.1688 | 0 | 149.692 | 0 | 43.5868 | 0 | 25.335 | 19.8119 | 0 | 0 | 0 | 0 | 279.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62888.3 | 0 | 62888.3 | 801302 | -12947.4 | 64 | 64 | 801302 | -1012947.4
9 | 28 | 12 | 4 | 39.9938 | 0 | 150.207 | 0 | 45.4414 | 0 | 25.335 | 19.7925 | 0 | 0 | 0 | 0 | 280.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62888.3 | 0 | 62888.3 | 831602 | -11817.2 | 65 | 65 | 831602 | -1011817.2
9 | 28 | 13 | 4 | 41.5043 | 0 | 165.698 | 0 | 45.5724 | 0 | 25.335 | 20.2977 | 0 | 0 | 0 | 0 | 298.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62888.5 | 0 | 62888.5 | 859228 | -16794.7 | 62 | 62 | 859228 | -1016794.7
9 | 28 | 14 | 4 | 40.9819 | 0 | 172.702 | 0 | 40.7761 | 0 | 25.335 | 20.3377 | 0 | 0 | 0 | 0 | 300.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61514.2 | 0 | 61514.2 | 772496 | -21138.6 | 58 | 59 | 772496 | -1021138.6
9 | 28 | 15 | 4 | 41.4491 | 0 | 173.986 | 0 | 37.4811 | 0 | 25.335 | 20.1563 | 0 | 0 | 0 | 0 | 298.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56016.7 | 0 | 56016.7 | 704747 | -24233.6 | 55 | 56 | 704747 | -1024233.6
9 | 28 | 16 | 4 | 40.6877 | 0 | 169.782 | 0 | 33.6554 | 0 | 25.335 | 19.9161 | 0 | 0 | 0 | 1.2 | 290.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46396.5 | 0 | 46396.5 | 651055 | -26201.8 | 53 | 55 | 651055 | -1026201.8
9 | 28 | 17 | 4 | 36.4116 | 0 | 152.497 | 0 | 25.2239 | 0 | 25.335 | 19.4759 | 0 | 0 | 0 | 4.8 | 263.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35402.5 | 0 | 35402.5 | 492535 | -27493.3 | 50 | 53 | 492535 | -1027493.3
9 | 28 | 18 | 4 | 31.3732 | 0 | 93.4203 | 0 | 18.952 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 7.2 | 195.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21660.6 | 0 | 21660.6 | 362604 | -58290.2 | 48 | 52 | 362604 | -1058290.2
9 | 28 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.4272 | 0 | 5.4943 | 8.818 | 0 | 0 | 0 | 7.2 | 117.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15477.5 | 0 | 15477.5 | 190572 | 0 | 47 | 51 | 190572 | -1000000
9 | 28 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.4134 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 7.2 | 103.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14792.4 | 0 | 14792.4 | 170917 | 0 | 46 | 49 | 170917 | -1000000
9 | 28 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7899 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9286.84 | 0 | 9286.84 | 157370 | 0 | 45 | 48 | 157370 | -1000000
9 | 28 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.2814 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9067.06 | 0 | 9067.06 | 146281 | 0 | 45 | 46 | 146281 | -1000000
9 | 28 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 9.4689 | 0 | 5.8973 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7912.81 | 0 | 7912.81 | 141167 | -6975.71 | 44 | 45 | 141167 | -1006975.71
9 | 28 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9628 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7914.38 | 0 | 7914.38 | 139463 | 0 | 43 | 43 | 139463 | -1000000
9 | 29 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.3386 | 0 | 5.8986 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.95 | 0 | 7915.95 | 138386 | -11911 | 42 | 42 | 138386 | -1011911
9 | 29 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.861 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7917.63 | 0 | 7917.63 | 137245 | 0 | 40 | 41 | 137245 | -1000000
9 | 29 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.9692 | 0 | 5.9002 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.6775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.19 | 0 | 7919.19 | 136488 | -15675.4 | 39 | 40 | 136488 | -1015675.4
9 | 29 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9405 | 0 | 5.8985 | 12.9754 | 0 | 0 | 0 | 4.8 | 87.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8772.9 | 0 | 8772.9 | 139047 | -4093.23 | 38 | 39 | 139047 | -1004093.23
9 | 29 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 11.9406 | 0 | 5.934 | 12.9754 | 0 | 0 | 0 | 4.8 | 129.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10670.9 | 0 | 10670.9 | 197877 | -10085.3 | 38 | 38 | 197877 | -1010085.3
9 | 29 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 21.0245 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 238.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28536.7 | 0 | 28536.7 | 330167 | -127794 | 37 | 37 | 330167 | -1127794
9 | 29 | 7 | 5 | 44.5137 | 0 | 168.222 | 0 | 27.9479 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 266.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31282.8 | 0 | 31282.8 | 423228 | -197223 | 39 | 40 | 423228 | -1197223
9 | 29 | 8 | 5 | 39.995 | 0 | 173.795 | 0 | 31.9095 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39531.4 | 0 | 39531.4 | 465876 | -162178 | 41 | 43 | 465876 | -1162178
9 | 29 | 9 | 5 | 40.6618 | 0 | 172.186 | 0 | 35.4128 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61519.4 | 0 | 61519.4 | 494765 | -146227 | 43 | 46 | 494765 | -1146227
9 | 29 | 10 | 5 | 41.177 | 0 | 163.102 | 0 | 33.8014 | 0 | 6.332 | 19.1114 | 0 | 0 | 0 | 0 | 263.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62893.6 | 0 | 62893.6 | 462281 | -111209 | 43 | 47 | 462281 | -1111209
9 | 29 | 11 | 5 | 40.7382 | 0 | 149.692 | 0 | 33.5215 | 0 | 6.332 | 19.0745 | 0 | 0 | 0 | 0 | 249.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62893 | 0 | 62893 | 475057 | -102794 | 43 | 49 | 475057 | -1102794
9 | 29 | 12 | 5 | 39.7977 | 0 | 150.207 | 0 | 29.2134 | 0 | 6.332 | 19.0491 | 0 | 0 | 0 | 0 | 244.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62892 | 0 | 62892 | 438491 | -84119.2 | 43 | 50 | 438491 | -1084119.2
9 | 29 | 13 | 5 | 41.8487 | 0 | 165.698 | 0 | 31.6787 | 0 | 25.335 | 19.0853 | 0 | 0 | 0 | 0 | 283.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62892.1 | 0 | 62892.1 | 495930 | -89706.4 | 42 | 50 | 495930 | -1089706.4
9 | 29 | 14 | 5 | 41.0473 | 0 | 172.702 | 0 | 30.5956 | 0 | 25.335 | 19.1357 | 0 | 0 | 0 | 0 | 288.815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61517.8 | 0 | 61517.8 | 506890 | -79562 | 42 | 50 | 506890 | -1079562
9 | 29 | 15 | 5 | 40.927 | 0 | 173.986 | 0 | 29.1277 | 0 | 25.335 | 19.1693 | 0 | 0 | 0 | 0 | 288.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56020.3 | 0 | 56020.3 | 497013 | -66092.6 | 42 | 50 | 497013 | -1066092.6
9 | 29 | 16 | 5 | 40.6062 | 0 | 169.782 | 0 | 27.8257 | 0 | 25.335 | 19.1543 | 0 | 0 | 0 | 1.2 | 283.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46400.1 | 0 | 46400.1 | 490449 | -71518.1 | 42 | 49 | 490449 | -1071518.1
9 | 29 | 17 | 5 | 37.0909 | 0 | 152.497 | 0 | 25.6429 | 0 | 25.335 | 19.0539 | 0 | 0 | 0 | 4.8 | 264.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35405.9 | 0 | 35405.9 | 433633 | -87997.3 | 41 | 48 | 433633 | -1087997.3
9 | 29 | 18 | 5 | 32.0077 | 0 | 93.4203 | 0 | 25.3622 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 183.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21663.8 | 0 | 21663.8 | 362335 | -151485 | 41 | 47 | 362335 | -1151485
9 | 29 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.3613 | 0 | 5.4932 | 8.818 | 0 | 0 | 0 | 7.2 | 117.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15480.7 | 0 | 15480.7 | 189110 | 0 | 40 | 46 | 189110 | -1000000
9 | 29 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.3545 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 7.2 | 103.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14795.6 | 0 | 14795.6 | 169630 | 0 | 39 | 44 | 169630 | -1000000
9 | 29 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 10.5269 | 0 | 5.9032 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9292.08 | 0 | 9292.08 | 156158 | -7494.43 | 39 | 43 | 156158 | -1007494.43
9 | 29 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.2116 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9072.94 | 0 | 9072.94 | 144747 | 0 | 38 | 43 | 144747 | -1000000
9 | 29 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 10.8884 | 0 | 5.9006 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.2223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.39 | 0 | 7919.39 | 140025 | -13800.5 | 38 | 42 | 140025 | -1013800.5
9 | 29 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.8973 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 75.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7921.5 | 0 | 7921.5 | 138026 | 0 | 38 | 42 | 138026 | -1000000
9 | 30 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.3295 | 0 | 5.9018 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7923.33 | 0 | 7923.33 | 136988 | -17198.2 | 37 | 40 | 136988 | -1017198.2
9 | 30 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8014 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.91 | 0 | 7925.91 | 135943 | -5035.88 | 35 | 39 | 135943 | -1005035.88
9 | 30 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8531 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.5078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7927.97 | 0 | 7927.97 | 137110 | -12645.4 | 34 | 37 | 137110 | -1012645.4
9 | 30 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7205 | 0 | 5.9 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.22 | 0 | 7930.22 | 134140 | -11229.1 | 33 | 35 | 134140 | -1011229.1
9 | 30 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.2499 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.4 | 0 | 7932.4 | 133306 | -14699.7 | 32 | 34 | 133306 | -1014699.7
9 | 30 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.3116 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 2.4 | 79.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7934.71 | 0 | 7934.71 | 132465 | -15894.2 | 31 | 32 | 132465 | -1015894.2
9 | 30 | 7 | 6 | 5.4604 | 0 | 42.7453 | 20.4902 | 0 | 0 | 6.1893 | 18.8896 | 0 | 0 | 0 | 0.8 | 94.5747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7937.08 | 0 | 7937.08 | 149307 | -399376 | 33 | 35 | 149307 | -1399376
9 | 30 | 8 | 6 | 4.9698 | 0 | 42.7453 | 20.0066 | 0 | 0 | 6.1864 | 18.8896 | 0 | 0 | 0 | 0 | 92.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7939.22 | 0 | 7939.22 | 186702 | -370666 | 35 | 39 | 186702 | -1370666
9 | 30 | 9 | 6 | 5.4973 | 0 | 42.7453 | 17.2958 | 0 | 0 | 6.0502 | 18.8896 | 0 | 0 | 0 | 0 | 90.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7942.72 | 0 | 7942.72 | 196047 | -317471 | 37 | 42 | 196047 | -1317471
9 | 30 | 10 | 6 | 5.4757 | 0 | 42.7453 | 14.9529 | 0 | 0 | 5.9769 | 18.8896 | 0 | 0 | 0 | 0 | 88.0404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7942.03 | 0 | 7942.03 | 197581 | -275559 | 39 | 45 | 197581 | -1275559
9 | 30 | 11 | 6 | 5.4721 | 0 | 42.7453 | 0 | 14.6935 | 0 | 11.7596 | 18.8896 | 0 | 0 | 0 | 0 | 93.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.22 | 0 | 7943.22 | 199074 | -246299 | 40 | 47 | 199074 | -1246299
9 | 30 | 12 | 6 | 5.9435 | 0 | 42.7453 | 0 | 14.9283 | 0 | 11.8158 | 18.8896 | 0 | 0 | 0 | 0 | 94.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.95 | 0 | 7943.95 | 196289 | -224198 | 41 | 50 | 196289 | -1224198
9 | 30 | 13 | 6 | 5.6397 | 0 | 42.7453 | 0 | 15.1656 | 0 | 11.9389 | 18.8896 | 0 | 0 | 0 | 0 | 94.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7944.7 | 0 | 7944.7 | 195212 | -197429 | 42 | 52 | 195212 | -1197429
9 | 30 | 14 | 6 | 6.0387 | 0 | 42.7453 | 0 | 7.4402 | 0 | 6.6155 | 8.818 | 0 | 0 | 0 | 0 | 71.6576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.32 | 0 | 7945.32 | 128257 | 0 | 44 | 53 | 128257 | -1000000
9 | 30 | 15 | 6 | 6.2009 | 0 | 42.7453 | 0 | 7.3335 | 0 | 6.5723 | 8.818 | 0 | 0 | 0 | 0 | 71.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7946.09 | 0 | 7946.09 | 127970 | 0 | 45 | 55 | 127970 | -1000000
9 | 30 | 16 | 6 | 5.5661 | 0 | 42.7453 | 0 | 8.1149 | 0 | 5.898 | 12.8287 | 0 | 0 | 0 | 1.2 | 76.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.52 | 0 | 7945.52 | 127741 | -5519.05 | 45 | 55 | 127741 | -1005519.05
9 | 30 | 17 | 6 | 6.0838 | 0 | 42.7453 | 0 | 6.9859 | 0 | 6.5007 | 8.818 | 0 | 0 | 0 | 4.8 | 75.9338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.63 | 0 | 7945.63 | 127586 | 0 | 46 | 54 | 127586 | -1000000
9 | 30 | 18 | 6 | 8.3952 | 0 | 42.7453 | 0 | 6.8094 | 0 | 6.8814 | 12.8287 | 0 | 0 | 0 | 7.2 | 84.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7945.78 | 0 | 7945.78 | 127216 | -873.571 | 46 | 54 | 127216 | -1000873.571
9 | 30 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4004 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7946.12 | 0 | 7946.12 | 127183 | 0 | 48 | 54 | 127183 | -1000000
9 | 30 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3797 | 0 | 5.9032 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7946.6 | 0 | 7946.6 | 126723 | -1350.41 | 48 | 55 | 126723 | -1001350.41
9 | 30 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3749 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7947.37 | 0 | 7947.37 | 126625 | 0 | 49 | 55 | 126625 | -1000000
9 | 30 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4155 | 0 | 5.9028 | 12.8287 | 0 | 0 | 0 | 6.4 | 83.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.05 | 0 | 7948.05 | 127530 | -1609.17 | 50 | 55 | 127530 | -1001609.17
9 | 30 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3493 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 5.6 | 77.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.81 | 0 | 7948.81 | 126040 | 0 | 50 | 55 | 126040 | -1000000
9 | 30 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.3481 | 0 | 5.9035 | 12.8287 | 0 | 0 | 0 | 4.8 | 77.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3139.89 | 0 | 3139.89 | 126040 | -1736.74 | 50 | 56 | 126040 | -1001736.74
10 | 1 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3251 | 0 | 5.4856 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.05 | 0 | 3251.05 | 125528 | 0 | 51 | 56 | 125528 | -1000000
10 | 1 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3087 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.79 | 0 | 3251.79 | 125171 | 0 | 51 | 57 | 125171 | -1000000
10 | 1 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3041 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3252.54 | 0 | 3252.54 | 125074 | 0 | 51 | 57 | 125074 | -1000000
10 | 1 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.1184 | 0 | 5.8984 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.24 | 0 | 3253.24 | 124882 | -8166.55 | 51 | 57 | 124882 | -1008166.55
10 | 1 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2822 | 0 | 5.4861 | 8.818 | 0 | 0 | 0 | 4.8 | 73.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.88 | 0 | 3253.88 | 124592 | 0 | 50 | 56 | 124592 | -1000000
10 | 1 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2732 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 2.4 | 70.8281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3254.5 | 0 | 3254.5 | 124398 | 0 | 49 | 56 | 124398 | -1000000
10 | 1 | 7 | 7 | 4.3554 | 0 | 42.7453 | 0 | 6.277 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 0.8 | 68.4819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.19 | 0 | 3255.19 | 124485 | 0 | 50 | 57 | 124485 | -1000000
10 | 1 | 8 | 7 | 3.8254 | 0 | 42.7453 | 0 | 8.136 | 0 | 5.8985 | 12.8287 | 0 | 0 | 0 | 0 | 73.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.81 | 0 | 3255.81 | 124340 | -8570.4 | 51 | 59 | 124340 | -1008570.4
10 | 1 | 9 | 7 | 4.1675 | 0 | 42.7453 | 0 | 6.8491 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 0 | 68.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.49 | 0 | 3256.49 | 124192 | 0 | 52 | 62 | 124192 | -1000000
10 | 1 | 10 | 7 | 4.1486 | 0 | 42.7453 | 0 | 7.5493 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 0 | 68.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.4 | 0 | 3256.4 | 124574 | 0 | 56 | 66 | 124574 | -1000000
10 | 1 | 11 | 7 | 4.1444 | 0 | 42.7453 | 0 | 8.575 | 0 | 5.9068 | 12.8287 | 0 | 0 | 0 | 0 | 74.2002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.51 | 0 | 3255.51 | 142457 | -825.022 | 58 | 70 | 142457 | -1000825.022
10 | 1 | 12 | 7 | 4.1479 | 0 | 42.7453 | 0 | 9.1264 | 0 | 5.5013 | 12.8287 | 0 | 0 | 0 | 0 | 74.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.85 | 0 | 3253.85 | 156065 | -0.0030222 | 60 | 73 | 156065 | -1000000.003
10 | 1 | 13 | 7 | 4.1494 | 0 | 42.7453 | 0 | 8.6494 | 0 | 5.492 | 12.8287 | 0 | 0 | 0 | 0 | 73.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3252.28 | 0 | 3252.28 | 163100 | 0 | 60 | 73 | 163100 | -1000000
10 | 1 | 14 | 7 | 4.151 | 0 | 42.7453 | 0 | 8.6868 | 0 | 5.4919 | 12.8287 | 0 | 0 | 0 | 0 | 73.9036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.67 | 0 | 3250.67 | 170549 | 0 | 61 | 72 | 170549 | -1000000
10 | 1 | 15 | 7 | 4.1507 | 0 | 42.7453 | 0 | 9.1719 | 0 | 5.5023 | 12.8287 | 0 | 0 | 0 | 0 | 74.3989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.07 | 0 | 3249.07 | 167953 | 0 | 61 | 73 | 167953 | -1000000
10 | 1 | 16 | 7 | 4.1524 | 0 | 42.7453 | 0 | 6.4756 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 1.2 | 68.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.29 | 0 | 3247.29 | 124462 | 0 | 61 | 72 | 124462 | -1000000
10 | 1 | 17 | 7 | 4.1996 | 0 | 42.7453 | 0 | 6.3982 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 72.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.77 | 0 | 3245.77 | 124385 | 0 | 60 | 71 | 124385 | -1000000
10 | 1 | 18 | 7 | 6.1367 | 0 | 42.7453 | 0 | 6.3663 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 7.2 | 76.7481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.52 | 0 | 3244.52 | 124508 | 0 | 60 | 70 | 124508 | -1000000
10 | 1 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.3302 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3243.43 | 0 | 3243.43 | 124529 | 0 | 60 | 69 | 124529 | -1000000
10 | 1 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2952 | 0 | 5.4831 | 8.818 | 0 | 0 | 0 | 7.2 | 77.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.84 | 0 | 3242.84 | 124562 | 0 | 60 | 68 | 124562 | -1000000
10 | 1 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2576 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 7.2 | 77.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.35 | 0 | 3242.35 | 124527 | 0 | 60 | 67 | 124527 | -1000000
10 | 1 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.5217 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 6.4 | 76.6298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242 | 0 | 3242 | 124475 | 0 | 60 | 67 | 124475 | -1000000
10 | 1 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 5.0437 | 0 | 5.5064 | 8.818 | 0 | 0 | 0 | 5.6 | 74.3767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3241.65 | 0 | 3241.65 | 124397 | 0 | 59 | 62 | 124397 | -1000000
10 | 1 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 5.772 | 0 | 5.4933 | 8.818 | 0 | 0 | 0 | 4.8 | 78.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.69 | 0 | 8308.69 | 124665 | 0 | 59 | 60 | 124665 | -1000000
10 | 2 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.256 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.43 | 0 | 8308.43 | 124014 | 0 | 54 | 55 | 124014 | -1000000
10 | 2 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2575 | 0 | 5.4864 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.66 | 0 | 8307.66 | 124058 | 0 | 53 | 53 | 124058 | -1000000
10 | 2 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2505 | 0 | 5.4865 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.55 | 0 | 8307.55 | 123900 | 0 | 52 | 52 | 123900 | -1000000
10 | 2 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 6.4136 | 0 | 5.4847 | 8.818 | 0 | 0 | 0 | 4.8 | 82.1607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9205.36 | 0 | 9205.36 | 127533 | 0 | 52 | 52 | 127533 | -1000000
10 | 2 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 8.5302 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 121.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11203.8 | 0 | 11203.8 | 174584 | 0 | 51 | 51 | 174584 | -1000000
10 | 2 | 6 | 1 | 49.0171 | 0 | 140.608 | 0 | 24.0945 | 0 | 6.332 | 19.0949 | 0 | 0 | 0 | 2.4 | 241.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30025.6 | 0 | 30025.6 | 320246 | -49343.3 | 50 | 51 | 320246 | -1049343.3
10 | 2 | 7 | 1 | 46.4645 | 0 | 168.222 | 0 | 28.3455 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 269.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32917.5 | 0 | 32917.5 | 434939 | -68947.5 | 50 | 51 | 434939 | -1068947.5
10 | 2 | 8 | 1 | 39.9997 | 0 | 173.795 | 0 | 29.4799 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41605 | 0 | 41605 | 489021 | -61092 | 50 | 54 | 489021 | -1061092
10 | 2 | 9 | 1 | 40.7273 | 0 | 172.186 | 0 | 32.4702 | 0 | 6.332 | 19.4564 | 0 | 0 | 0 | 0 | 271.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64770.1 | 0 | 64770.1 | 521393 | -31177.8 | 50 | 57 | 521393 | -1031177.8
10 | 2 | 10 | 1 | 41.1979 | 0 | 163.102 | 0 | 35.4236 | 0 | 6.332 | 19.8515 | 0 | 0 | 0 | 0 | 265.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66216.8 | 0 | 66216.8 | 560947 | -30560.7 | 50 | 59 | 560947 | -1030560.7
10 | 2 | 11 | 1 | 40.7089 | 0 | 149.692 | 0 | 36.969 | 0 | 6.332 | 19.9717 | 0 | 0 | 0 | 0 | 253.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66215.6 | 0 | 66215.6 | 605885 | -28536.2 | 50 | 62 | 605885 | -1028536.2
10 | 2 | 12 | 1 | 39.7922 | 0 | 150.207 | 0 | 40.2485 | 0 | 6.332 | 19.7444 | 0 | 0 | 0 | 0 | 256.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66215.3 | 0 | 66215.3 | 672704 | -45683.2 | 49 | 63 | 672704 | -1045683.2
10 | 2 | 13 | 1 | 41.3 | 0 | 165.698 | 0 | 43.6139 | 0 | 6.332 | 20.5381 | 0 | 0 | 0 | 0 | 277.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66215.3 | 0 | 66215.3 | 742721 | -26204.3 | 50 | 65 | 742721 | -1026204.3
10 | 2 | 14 | 1 | 40.6863 | 0 | 172.702 | 0 | 39.5575 | 0 | 6.332 | 20.8901 | 0 | 0 | 0 | 0 | 280.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64767.4 | 0 | 64767.4 | 738741 | -15163.5 | 49 | 63 | 738741 | -1015163.5
10 | 2 | 15 | 1 | 40.5943 | 0 | 173.986 | 0 | 41.7752 | 0 | 6.332 | 20.7856 | 0 | 0 | 0 | 0 | 283.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58975.6 | 0 | 58975.6 | 766243 | -22471.2 | 49 | 63 | 766243 | -1022471.2
10 | 2 | 16 | 1 | 40.3541 | 0 | 169.782 | 0 | 37.1093 | 0 | 6.332 | 21.2507 | 0 | 0 | 0 | 1.2 | 276.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48839.7 | 0 | 48839.7 | 702456 | -9892.57 | 48 | 63 | 702456 | -1009892.57
10 | 2 | 17 | 1 | 35.9511 | 0 | 152.497 | 0 | 30.6473 | 0 | 6.332 | 20.7379 | 0 | 0 | 0 | 4.8 | 250.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37255.9 | 0 | 37255.9 | 593223 | -8824.12 | 49 | 63 | 593223 | -1008824.12
10 | 2 | 18 | 1 | 31.2867 | 0 | 93.4203 | 0 | 18.1587 | 0 | 6.332 | 19.2255 | 0 | 0 | 0 | 7.2 | 175.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22776.2 | 0 | 22776.2 | 371283 | -8626.7 | 48 | 60 | 371283 | -1008626.7
10 | 2 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 9.1959 | 0 | 5.4906 | 8.818 | 0 | 0 | 0 | 7.2 | 117.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16260.3 | 0 | 16260.3 | 185275 | 0 | 47 | 58 | 185275 | -1000000
10 | 2 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.1795 | 0 | 5.4803 | 8.818 | 0 | 0 | 0 | 7.2 | 103.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15537.6 | 0 | 15537.6 | 165800 | 0 | 47 | 57 | 165800 | -1000000
10 | 2 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.5636 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9738.31 | 0 | 9738.31 | 152418 | 0 | 46 | 55 | 152418 | -1000000
10 | 2 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 7.0656 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9506.3 | 0 | 9506.3 | 141560 | 0 | 46 | 55 | 141560 | -1000000
10 | 2 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.8475 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8289.83 | 0 | 8289.83 | 136891 | 0 | 46 | 55 | 136891 | -1000000
10 | 2 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.7774 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 78.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8290.82 | 0 | 8290.82 | 135409 | 0 | 45 | 53 | 135409 | -1000000
10 | 3 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7457 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.73 | 0 | 8291.73 | 134730 | 0 | 45 | 51 | 134730 | -1000000
10 | 3 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7099 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8292.54 | 0 | 8292.54 | 133943 | 0 | 45 | 50 | 133943 | -1000000
10 | 3 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.7669 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8293.34 | 0 | 8293.34 | 133254 | -7008.5 | 45 | 50 | 133254 | -1007008.5
10 | 3 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.808 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9191.86 | 0 | 9191.86 | 136153 | 0 | 44 | 49 | 136153 | -1000000
10 | 3 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 8.9153 | 0 | 5.905 | 12.9754 | 0 | 0 | 0 | 4.8 | 126.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11190.8 | 0 | 11190.8 | 183012 | -1973.89 | 45 | 50 | 183012 | -1001973.89
10 | 3 | 6 | 2 | 49.0171 | 0 | 140.608 | 0 | 21.1788 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 238.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30013.2 | 0 | 30013.2 | 336948 | -42604.1 | 45 | 51 | 336948 | -1042604.1
10 | 3 | 7 | 2 | 46.5613 | 0 | 168.222 | 0 | 34.2919 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 275.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32905.9 | 0 | 32905.9 | 455666 | -89206.8 | 45 | 52 | 455666 | -1089206.8
10 | 3 | 8 | 2 | 40.2183 | 0 | 173.795 | 0 | 30.8076 | 0 | 6.332 | 19.0495 | 0 | 0 | 0 | 0 | 270.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41596.8 | 0 | 41596.8 | 496778 | -49836.5 | 47 | 56 | 496778 | -1049836.5
10 | 3 | 9 | 2 | 40.8555 | 0 | 172.186 | 0 | 34.1717 | 0 | 6.332 | 19.6916 | 0 | 0 | 0 | 0 | 273.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64762.3 | 0 | 64762.3 | 547920 | -21834.7 | 49 | 60 | 547920 | -1021834.7
10 | 3 | 10 | 2 | 41.2114 | 0 | 163.102 | 0 | 41.9914 | 0 | 6.332 | 20.0731 | 0 | 0 | 0 | 0 | 272.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66209.6 | 0 | 66209.6 | 685172 | -30299.1 | 50 | 65 | 685172 | -1030299.1
10 | 3 | 11 | 2 | 40.7203 | 0 | 149.692 | 0 | 45.6509 | 0 | 6.332 | 20.1828 | 0 | 0 | 0 | 0 | 262.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66208.8 | 0 | 66208.8 | 739065 | -31804.8 | 51 | 69 | 739065 | -1031804.8
10 | 3 | 12 | 2 | 39.8011 | 0 | 150.207 | 0 | 53.0042 | 0 | 6.332 | 19.9026 | 0 | 0 | 0 | 0 | 269.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66209.4 | 0 | 66209.4 | 835781 | -50791.5 | 52 | 71 | 835781 | -1050791.5
10 | 3 | 13 | 2 | 41.3114 | 0 | 165.698 | 0 | 54.2076 | 0 | 25.335 | 20.7726 | 0 | 0 | 0 | 0 | 307.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66209.6 | 0 | 66209.6 | 904780 | -31078.8 | 53 | 72 | 904780 | -1031078.8
10 | 3 | 14 | 2 | 40.7014 | 0 | 172.702 | 0 | 50.9897 | 0 | 25.335 | 21.2323 | 0 | 0 | 0 | 0 | 310.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64761.7 | 0 | 64761.7 | 909373 | -21081.4 | 53 | 70 | 909373 | -1021081.4
10 | 3 | 15 | 2 | 40.6052 | 0 | 173.986 | 0 | 52.7219 | 0 | 25.335 | 21.0748 | 0 | 0 | 0 | 0 | 313.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58970.2 | 0 | 58970.2 | 938302 | -27019.2 | 55 | 69 | 938302 | -1027019.2
10 | 3 | 16 | 2 | 40.3883 | 0 | 169.782 | 0 | 43.4013 | 0 | 25.335 | 21.9877 | 0 | 0 | 0 | 1.2 | 302.094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48834.7 | 0 | 48834.7 | 817955 | -7689.91 | 53 | 67 | 817955 | -1007689.91
10 | 3 | 17 | 2 | 36.19 | 0 | 152.497 | 0 | 33.2931 | 0 | 25.335 | 21.4178 | 0 | 0 | 0 | 4.8 | 273.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37251.1 | 0 | 37251.1 | 657685 | -7057.39 | 49 | 64 | 657685 | -1007057.39
10 | 3 | 18 | 2 | 31.1677 | 0 | 93.4203 | 0 | 19.7841 | 0 | 6.332 | 19.5181 | 0 | 0 | 0 | 7.2 | 177.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22771.7 | 0 | 22771.7 | 422327 | -6554.73 | 49 | 62 | 422327 | -1006554.73
10 | 3 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.2332 | 0 | 5.492 | 8.818 | 0 | 0 | 0 | 7.2 | 117.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16255.3 | 0 | 16255.3 | 189871 | 0 | 48 | 61 | 189871 | -1000000
10 | 3 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.1168 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 7.2 | 102.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15532.8 | 0 | 15532.8 | 170036 | 0 | 47 | 59 | 170036 | -1000000
10 | 3 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.7548 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9732.12 | 0 | 9732.12 | 156604 | 0 | 46 | 57 | 156604 | -1000000
10 | 3 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.2441 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9499.8 | 0 | 9499.8 | 145464 | 0 | 45 | 55 | 145464 | -1000000
10 | 3 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 7.0177 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8283.01 | 0 | 8283.01 | 140613 | 0 | 45 | 54 | 140613 | -1000000
10 | 3 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.9437 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8283.86 | 0 | 8283.86 | 139048 | 0 | 45 | 52 | 139048 | -1000000
10 | 4 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8904 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8284.74 | 0 | 8284.74 | 137888 | 0 | 43 | 48 | 137888 | -1000000
10 | 4 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8502 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.67 | 0 | 8285.67 | 137013 | 0 | 43 | 48 | 137013 | -1000000
10 | 4 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 9.5307 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8286.59 | 0 | 8286.59 | 136175 | -7837.88 | 42 | 45 | 136175 | -1007837.88
10 | 4 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9305 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9185.39 | 0 | 9185.39 | 138829 | 0 | 42 | 46 | 138829 | -1000000
10 | 4 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 9.0211 | 0 | 5.9063 | 12.9754 | 0 | 0 | 0 | 4.8 | 126.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11184.6 | 0 | 11184.6 | 185323 | -2305.97 | 42 | 45 | 185323 | -1002305.97
10 | 4 | 6 | 3 | 49.0171 | 0 | 140.608 | 0 | 20.8073 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 238.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30007.4 | 0 | 30007.4 | 335645 | -45979.6 | 44 | 48 | 335645 | -1045979.6
10 | 4 | 7 | 3 | 50.4689 | 0 | 168.222 | 0 | 32.6721 | 0 | 6.332 | 19.0372 | 0 | 0 | 0 | 0.8 | 277.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32900.4 | 0 | 32900.4 | 459119 | -126740 | 43 | 47 | 459119 | -1126740
10 | 4 | 8 | 3 | 46.4176 | 0 | 173.795 | 0 | 32.0189 | 0 | 6.332 | 19.0593 | 0 | 0 | 0 | 0 | 277.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41592.9 | 0 | 41592.9 | 483066 | -104404 | 44 | 48 | 483066 | -1104404
10 | 4 | 9 | 3 | 41.7052 | 0 | 172.186 | 0 | 36.1663 | 0 | 6.332 | 19.076 | 0 | 0 | 0 | 0 | 275.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64758.7 | 0 | 64758.7 | 490088 | -105564 | 44 | 48 | 490088 | -1105564
10 | 4 | 10 | 3 | 41.2167 | 0 | 163.102 | 0 | 31.3269 | 0 | 6.332 | 19.0547 | 0 | 0 | 0 | 0 | 261.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66206.5 | 0 | 66206.5 | 461682 | -88647.7 | 45 | 48 | 461682 | -1088647.7
10 | 4 | 11 | 3 | 40.7437 | 0 | 149.692 | 0 | 31.5412 | 0 | 6.332 | 19.0784 | 0 | 0 | 0 | 0 | 247.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66206.3 | 0 | 66206.3 | 477360 | -93762.9 | 44 | 49 | 477360 | -1093762.9
10 | 4 | 12 | 3 | 39.778 | 0 | 150.207 | 0 | 29.5193 | 0 | 6.332 | 19.1019 | 0 | 0 | 0 | 0 | 244.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66206.4 | 0 | 66206.4 | 459709 | -71371.1 | 45 | 51 | 459709 | -1071371.1
10 | 4 | 13 | 3 | 41.2764 | 0 | 165.698 | 0 | 31.0454 | 0 | 25.335 | 19.276 | 0 | 0 | 0 | 0 | 282.631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66206.4 | 0 | 66206.4 | 517682 | -62188.8 | 45 | 52 | 517682 | -1062188.8
10 | 4 | 14 | 3 | 40.9919 | 0 | 172.702 | 0 | 27.3821 | 0 | 25.335 | 19.2653 | 0 | 0 | 0 | 0 | 285.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64758.5 | 0 | 64758.5 | 509106 | -47639.7 | 46 | 52 | 509106 | -1047639.7
10 | 4 | 15 | 3 | 41.1681 | 0 | 173.986 | 0 | 25.2884 | 0 | 25.335 | 19.195 | 0 | 0 | 0 | 0 | 284.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58966.3 | 0 | 58966.3 | 477917 | -66437.3 | 44 | 46 | 477917 | -1066437.3
10 | 4 | 16 | 3 | 42.0043 | 0 | 169.782 | 0 | 26.7208 | 0 | 25.335 | 19.1573 | 0 | 0 | 0 | 1.2 | 284.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48830.5 | 0 | 48830.5 | 484422 | -71431 | 45 | 48 | 484422 | -1071431
10 | 4 | 17 | 3 | 41.9894 | 0 | 152.497 | 0 | 27.0498 | 0 | 6.332 | 19.044 | 0 | 0 | 0 | 4.8 | 251.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37247.2 | 0 | 37247.2 | 430236 | -85593.4 | 44 | 48 | 430236 | -1085593.4
10 | 4 | 18 | 3 | 33.595 | 0 | 93.4203 | 0 | 25.0854 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22768.8 | 0 | 22768.8 | 363107 | -149290 | 44 | 47 | 363107 | -1149290
10 | 4 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.3544 | 0 | 5.4931 | 8.818 | 0 | 0 | 0 | 7.2 | 117.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16254.4 | 0 | 16254.4 | 188944 | 0 | 44 | 45 | 188944 | -1000000
10 | 4 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.3265 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 7.2 | 103.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15532.3 | 0 | 15532.3 | 169009 | 0 | 42 | 45 | 169009 | -1000000
10 | 4 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 11.0468 | 0 | 5.9056 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9734.38 | 0 | 9734.38 | 155857 | -8713.43 | 42 | 44 | 155857 | -1008713.43
10 | 4 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2021 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9503.59 | 0 | 9503.59 | 144541 | 0 | 42 | 44 | 144541 | -1000000
10 | 4 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 10.906 | 0 | 5.9006 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.22 | 0 | 8288.22 | 139510 | -13520.3 | 40 | 43 | 139510 | -1013520.3
10 | 4 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8925 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8290.32 | 0 | 8290.32 | 137928 | 0 | 39 | 42 | 137928 | -1000000
10 | 5 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.2895 | 0 | 5.9016 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8292.15 | 0 | 8292.15 | 136935 | -16636 | 38 | 41 | 136935 | -1016636
10 | 5 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8037 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.3922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8294.06 | 0 | 8294.06 | 135995 | -4310.03 | 37 | 39 | 135995 | -1004310.03
10 | 5 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.9306 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8295.77 | 0 | 8295.77 | 137383 | -11661.4 | 36 | 37 | 137383 | -1011661.4
10 | 5 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 8.6603 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 4.8 | 88.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9195.27 | 0 | 9195.27 | 137628 | -9765.71 | 36 | 39 | 137628 | -1009765.71
10 | 5 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 11.183 | 0 | 5.9186 | 12.9754 | 0 | 0 | 0 | 4.8 | 129.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11195.1 | 0 | 11195.1 | 184084 | -7313.61 | 37 | 39 | 184084 | -1007313.61
10 | 5 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 21.9563 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30018.3 | 0 | 30018.3 | 329333 | -164791 | 38 | 40 | 329333 | -1164791
10 | 5 | 7 | 4 | 46.9501 | 0 | 168.222 | 0 | 27.1618 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0.8 | 287.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32911.4 | 0 | 32911.4 | 415132 | -243289 | 38 | 40 | 415132 | -1243289
10 | 5 | 8 | 4 | 40.3203 | 0 | 173.795 | 0 | 31.0411 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41600.1 | 0 | 41600.1 | 457684 | -193835 | 39 | 43 | 457684 | -1193835
10 | 5 | 9 | 4 | 40.8812 | 0 | 172.186 | 0 | 34.8413 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 292.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64765.1 | 0 | 64765.1 | 494219 | -179884 | 40 | 45 | 494219 | -1179884
10 | 5 | 10 | 4 | 41.2192 | 0 | 163.102 | 0 | 34.2421 | 0 | 6.332 | 19.0476 | 0 | 0 | 0 | 0 | 263.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66212.7 | 0 | 66212.7 | 466464 | -127564 | 42 | 48 | 466464 | -1127564
10 | 5 | 11 | 4 | 40.7697 | 0 | 149.692 | 0 | 33.5466 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66212 | 0 | 66212 | 450690 | -118711 | 42 | 49 | 450690 | -1118711
10 | 5 | 12 | 4 | 39.8828 | 0 | 150.207 | 0 | 30.6275 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66210.7 | 0 | 66210.7 | 421295 | -108219 | 42 | 49 | 421295 | -1108219
10 | 5 | 13 | 4 | 42.1307 | 0 | 165.698 | 0 | 34.5417 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 267.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66209.9 | 0 | 66209.9 | 479606 | -112065 | 41 | 50 | 479606 | -1112065
10 | 5 | 14 | 4 | 41.2008 | 0 | 172.702 | 0 | 33.5927 | 0 | 6.8244 | 19.0611 | 0 | 0 | 0 | 0 | 273.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64761.9 | 0 | 64761.9 | 492519 | -97730.1 | 41 | 50 | 492519 | -1097730.1
10 | 5 | 15 | 4 | 41.229 | 0 | 173.986 | 0 | 31.0564 | 0 | 25.335 | 19.078 | 0 | 0 | 0 | 0 | 290.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58969.7 | 0 | 58969.7 | 475976 | -95548.8 | 40 | 48 | 475976 | -1095548.8
10 | 5 | 16 | 4 | 42.442 | 0 | 169.782 | 0 | 30.9036 | 0 | 25.335 | 19.069 | 0 | 0 | 0 | 1.2 | 288.732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48833.9 | 0 | 48833.9 | 476608 | -100853 | 40 | 48 | 476608 | -1100853
10 | 5 | 17 | 4 | 37.2974 | 0 | 152.497 | 0 | 29.571 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 249.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37250.5 | 0 | 37250.5 | 431042 | -114482 | 40 | 48 | 431042 | -1114482
10 | 5 | 18 | 4 | 33.0996 | 0 | 93.4203 | 0 | 25.9447 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 7.2 | 204.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22771.9 | 0 | 22771.9 | 357518 | -185639 | 38 | 46 | 357518 | -1185639
10 | 5 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.7097 | 0 | 8.6394 | 8.818 | 0 | 0 | 0 | 7.2 | 121.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16257.3 | 0 | 16257.3 | 188114 | 0 | 37 | 44 | 188114 | -1000000
10 | 5 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 10.8586 | 0 | 5.9093 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15535.2 | 0 | 15535.2 | 168625 | -6537.21 | 36 | 42 | 168625 | -1006537.21
10 | 5 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.684 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9738.05 | 0 | 9738.05 | 155050 | 0 | 35 | 41 | 155050 | -1000000
10 | 5 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.7957 | 0 | 5.906 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.6077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9507.72 | 0 | 9507.72 | 143924 | -16124.8 | 34 | 39 | 143924 | -1016124.8
10 | 5 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.9415 | 0 | 5.8985 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8292.87 | 0 | 8292.87 | 138942 | -5105.6 | 33 | 35 | 138942 | -1005105.6
10 | 5 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 7.0048 | 0 | 5.8982 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8295.3 | 0 | 8295.3 | 140436 | -7963.39 | 34 | 37 | 140436 | -1007963.39
10 | 6 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8578 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8297.58 | 0 | 8297.58 | 137138 | -5314.28 | 37 | 41 | 137138 | -1005314.28
10 | 6 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.775 | 0 | 5.8996 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8299.41 | 0 | 8299.41 | 135353 | -6456.12 | 36 | 38 | 135353 | -1006456.12
10 | 6 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7347 | 0 | 5.8999 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.93 | 0 | 8300.93 | 134485 | -11347.9 | 36 | 37 | 134485 | -1011347.9
10 | 6 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.9569 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 4.8 | 89.2735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9200.01 | 0 | 9200.01 | 137006 | -12334.4 | 36 | 37 | 137006 | -1012334.4
10 | 6 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 12.1897 | 0 | 5.9288 | 12.9754 | 0 | 0 | 0 | 4.8 | 130.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11200 | 0 | 11200 | 186850 | -14238.5 | 36 | 37 | 186850 | -1014238.5
10 | 6 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 22.5788 | 0 | 6.3119 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30023.4 | 0 | 30023.4 | 328341 | -312135 | 36 | 37 | 328341 | -1312135
10 | 6 | 7 | 5 | 50.8701 | 0 | 168.222 | 0 | 24.9519 | 0 | 25.3177 | 19.0363 | 0 | 0 | 0 | 0.8 | 289.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32917.1 | 0 | 32917.1 | 390126 | -302985 | 36 | 37 | 390126 | -1302985
10 | 6 | 8 | 5 | 40.1005 | 0 | 173.795 | 0 | 26.2795 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 284.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41604.9 | 0 | 41604.9 | 411532 | -254281 | 36 | 37 | 411532 | -1254281
10 | 6 | 9 | 5 | 40.6828 | 0 | 172.186 | 0 | 27.8394 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 285.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64770 | 0 | 64770 | 426286 | -242346 | 36 | 38 | 426286 | -1242346
10 | 6 | 10 | 5 | 41.2201 | 0 | 163.102 | 0 | 29.0688 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 277.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66218 | 0 | 66218 | 438063 | -227377 | 37 | 40 | 438063 | -1227377
10 | 6 | 11 | 5 | 40.7493 | 0 | 149.692 | 0 | 30.4413 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 265.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66217.2 | 0 | 66217.2 | 444714 | -212615 | 36 | 42 | 444714 | -1212615
10 | 6 | 12 | 5 | 39.8724 | 0 | 150.207 | 0 | 28.2323 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 262.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66216.3 | 0 | 66216.3 | 412455 | -190402 | 37 | 44 | 412455 | -1190402
10 | 6 | 13 | 5 | 41.8479 | 0 | 165.698 | 0 | 32.8414 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 284.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66215.6 | 0 | 66215.6 | 468859 | -180697 | 37 | 45 | 468859 | -1180697
10 | 6 | 14 | 5 | 40.6597 | 0 | 172.702 | 0 | 35.4487 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 293.181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64766.5 | 0 | 64766.5 | 488538 | -136954 | 38 | 47 | 488538 | -1136954
10 | 6 | 15 | 5 | 40.5986 | 0 | 173.986 | 0 | 33.9407 | 0 | 6.399 | 19.0363 | 0 | 0 | 0 | 0 | 273.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58973.7 | 0 | 58973.7 | 471799 | -125115 | 37 | 45 | 471799 | -1125115
10 | 6 | 16 | 5 | 40.3574 | 0 | 169.782 | 0 | 34.0855 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 270.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48837.6 | 0 | 48837.6 | 474442 | -128771 | 37 | 45 | 474442 | -1128771
10 | 6 | 17 | 5 | 36.3691 | 0 | 152.497 | 0 | 30.0392 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 4.8 | 268.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37254.1 | 0 | 37254.1 | 434444 | -158259 | 37 | 44 | 434444 | -1158259
10 | 6 | 18 | 5 | 31.7183 | 0 | 93.4203 | 0 | 22.2942 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 7.2 | 199.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22775.6 | 0 | 22775.6 | 322049 | -211862 | 35 | 41 | 322049 | -1211862
10 | 6 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.2435 | 0 | 5.4913 | 8.818 | 0 | 0 | 0 | 7.2 | 117.772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16260.9 | 0 | 16260.9 | 187170 | 0 | 34 | 38 | 187170 | -1000000
10 | 6 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.2695 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 7.2 | 103.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15538.7 | 0 | 15538.7 | 167771 | 0 | 33 | 36 | 167771 | -1000000
10 | 6 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 10.3883 | 0 | 5.9021 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9742.37 | 0 | 9742.37 | 154156 | -10757.6 | 32 | 33 | 154156 | -1010757.6
10 | 6 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.1314 | 0 | 5.8976 | 12.9754 | 0 | 0 | 0 | 6.4 | 87.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9511.88 | 0 | 9511.88 | 142997 | -8753.53 | 33 | 34 | 142997 | -1008753.53
10 | 6 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 9.3941 | 0 | 5.897 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.7244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8296.88 | 0 | 8296.88 | 138081 | -13306.3 | 34 | 35 | 138081 | -1013306.3
10 | 6 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 9.2729 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8299.94 | 0 | 8299.94 | 136117 | -13641.5 | 33 | 36 | 136117 | -1013641.5
10 | 7 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.4893 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.51 | 0 | 8302.51 | 135726 | -14414.3 | 35 | 40 | 135726 | -1014414.3
10 | 7 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.2599 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.9123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8305.58 | 0 | 8305.58 | 134309 | -13797.7 | 36 | 41 | 134309 | -1013797.7
10 | 7 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.0959 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.08 | 0 | 8308.08 | 133508 | -13425.4 | 36 | 41 | 133508 | -1013425.4
10 | 7 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.0231 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8310.28 | 0 | 8310.28 | 132748 | -13370.7 | 37 | 42 | 132748 | -1013370.7
10 | 7 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.123 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.31 | 0 | 8312.31 | 132459 | -14171.3 | 37 | 42 | 132459 | -1014171.3
10 | 7 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 8.9016 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 2.4 | 79.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8314.29 | 0 | 8314.29 | 131276 | -13822.4 | 37 | 43 | 131276 | -1013822.4
10 | 7 | 7 | 6 | 6.2678 | 0 | 42.7453 | 22.8354 | 0 | 0 | 6.2968 | 18.8896 | 0 | 0 | 0 | 0.8 | 97.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316.2 | 0 | 8316.2 | 140882 | -406711 | 38 | 43 | 140882 | -1406711
10 | 7 | 8 | 6 | 6.0677 | 0 | 42.7453 | 22.0646 | 0 | 0 | 6.2904 | 18.8896 | 0 | 0 | 0 | 0 | 96.0576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.88 | 0 | 8317.88 | 195774 | -407702 | 39 | 45 | 195774 | -1407702
10 | 7 | 9 | 6 | 6.5522 | 0 | 42.7453 | 18.8751 | 0 | 0 | 6.1114 | 18.8896 | 0 | 0 | 0 | 0 | 93.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.93 | 0 | 8319.93 | 184342 | -331023 | 40 | 47 | 184342 | -1331023
10 | 7 | 10 | 6 | 6.0651 | 0 | 42.7453 | 16.5205 | 0 | 0 | 6.0042 | 18.8896 | 0 | 0 | 0 | 0 | 90.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.49 | 0 | 8318.49 | 187793 | -275785 | 43 | 51 | 187793 | -1275785
10 | 7 | 11 | 6 | 5.8743 | 0 | 42.7453 | 0 | 14.876 | 0 | 11.4845 | 18.8896 | 0 | 0 | 0 | 0 | 93.8697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.43 | 0 | 8319.43 | 187857 | -228610 | 45 | 54 | 187857 | -1228610
10 | 7 | 12 | 6 | 5.6794 | 0 | 42.7453 | 0 | 15.2709 | 0 | 11.7837 | 18.8896 | 0 | 0 | 0 | 0 | 94.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.62 | 0 | 8319.62 | 188620 | -190758 | 47 | 56 | 188620 | -1190758
10 | 7 | 13 | 6 | 5.8878 | 0 | 42.7453 | 0 | 14.9763 | 0 | 5.9624 | 18.8896 | 0 | 0 | 0 | 0 | 88.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.09 | 0 | 8320.09 | 183508 | -145173 | 50 | 60 | 183508 | -1145173
10 | 7 | 14 | 6 | 5.8548 | 0 | 42.7453 | 0 | 7.5991 | 0 | 6.7704 | 8.818 | 0 | 0 | 0 | 0 | 71.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.27 | 0 | 8320.27 | 128003 | 0 | 52 | 61 | 128003 | -1000000
10 | 7 | 15 | 6 | 6.1241 | 0 | 42.7453 | 0 | 7.2688 | 0 | 6.5844 | 8.818 | 0 | 0 | 0 | 0 | 71.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.5 | 0 | 8320.5 | 127482 | 0 | 51 | 61 | 127482 | -1000000
10 | 7 | 16 | 6 | 6.3967 | 0 | 42.7453 | 0 | 7.0559 | 0 | 6.5418 | 8.818 | 0 | 0 | 0 | 1.2 | 72.7576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.26 | 0 | 8320.26 | 127388 | 0 | 51 | 61 | 127388 | -1000000
10 | 7 | 17 | 6 | 7.0484 | 0 | 42.7453 | 0 | 6.6557 | 0 | 6.357 | 8.818 | 0 | 0 | 0 | 4.8 | 76.4243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.7 | 0 | 8319.7 | 127384 | 0 | 52 | 58 | 127384 | -1000000
10 | 7 | 18 | 6 | 8.5579 | 0 | 42.7453 | 0 | 6.3824 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 7.2 | 79.1885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.55 | 0 | 8319.55 | 126779 | 0 | 51 | 58 | 126779 | -1000000
10 | 7 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3733 | 0 | 5.4851 | 8.818 | 0 | 0 | 0 | 7.2 | 79.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.53 | 0 | 8319.53 | 126588 | 0 | 50 | 57 | 126588 | -1000000
10 | 7 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3666 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.89 | 0 | 8319.89 | 126443 | 0 | 50 | 57 | 126443 | -1000000
10 | 7 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4582 | 0 | 5.9023 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.9318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.39 | 0 | 8320.39 | 128482 | -5023.64 | 48 | 54 | 128482 | -1005023.64
10 | 7 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3351 | 0 | 5.4855 | 8.818 | 0 | 0 | 0 | 6.4 | 78.5813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.96 | 0 | 8320.96 | 125710 | 0 | 46 | 51 | 125710 | -1000000
10 | 7 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3178 | 0 | 5.9039 | 12.8287 | 0 | 0 | 0 | 5.6 | 82.1929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8321.58 | 0 | 8321.58 | 125371 | -1527.43 | 44 | 49 | 125371 | -1001527.43
10 | 7 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.3067 | 0 | 5.4859 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.16 | 0 | 3255.16 | 125130 | 0 | 44 | 48 | 125130 | -1000000
10 | 8 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.3574 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.7335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.09 | 0 | 3256.09 | 124933 | -12492 | 45 | 48 | 124933 | -1012492
10 | 8 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2796 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3257.47 | 0 | 3257.47 | 124533 | 0 | 45 | 48 | 124533 | -1000000
10 | 8 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.6354 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.0115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3258.72 | 0 | 3258.72 | 124298 | -14293 | 45 | 47 | 124298 | -1014293
10 | 8 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2475 | 0 | 5.9047 | 12.8287 | 0 | 0 | 0 | 4.8 | 77.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3260.11 | 0 | 3260.11 | 123830 | -4914.63 | 43 | 45 | 123830 | -1004914.63
10 | 8 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2717 | 0 | 5.9044 | 12.8287 | 0 | 0 | 0 | 4.8 | 77.6554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3261.31 | 0 | 3261.31 | 124377 | -10432.5 | 42 | 44 | 124377 | -1010432.5
10 | 8 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2265 | 0 | 5.9049 | 12.8287 | 0 | 0 | 0 | 2.4 | 75.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3262.71 | 0 | 3262.71 | 123361 | -9725.16 | 42 | 45 | 123361 | -1009725.16
10 | 8 | 7 | 7 | 4.9007 | 0 | 42.7453 | 0 | 8.1633 | 0 | 5.8985 | 12.8287 | 0 | 0 | 0 | 0.8 | 75.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3264.19 | 0 | 3264.19 | 123649 | -11504 | 40 | 44 | 123649 | -1011504
10 | 8 | 8 | 7 | 4.5484 | 0 | 42.7453 | 0 | 7.8333 | 0 | 5.8995 | 12.8287 | 0 | 0 | 0 | 0 | 73.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3265.8 | 0 | 3265.8 | 122817 | -10956.4 | 39 | 43 | 122817 | -1010956.4
10 | 8 | 9 | 7 | 4.868 | 0 | 42.7453 | 0 | 8.5884 | 0 | 5.8969 | 15.3158 | 0 | 0 | 0 | 0 | 77.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3267.34 | 0 | 3267.34 | 133337 | -19163.8 | 39 | 43 | 133337 | -1019163.8
10 | 8 | 10 | 7 | 4.7725 | 0 | 42.7453 | 0 | 7.887 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 0 | 74.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.79 | 0 | 3268.79 | 122407 | -11607.9 | 39 | 43 | 122407 | -1011607.9
10 | 8 | 11 | 7 | 4.6079 | 0 | 42.7453 | 0 | 8.44 | 0 | 5.897 | 15.3158 | 0 | 0 | 0 | 0 | 77.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3270.59 | 0 | 3270.59 | 133063 | -19581.4 | 39 | 43 | 133063 | -1019581.4
10 | 8 | 12 | 7 | 4.4814 | 0 | 42.7453 | 0 | 7.7397 | 0 | 5.8999 | 12.8287 | 0 | 0 | 0 | 0 | 73.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.04 | 0 | 3272.04 | 122008 | -11617.7 | 39 | 43 | 122008 | -1011617.7
10 | 8 | 13 | 7 | 4.5161 | 0 | 42.7453 | 0 | 8.304 | 0 | 5.8972 | 15.3158 | 0 | 0 | 0 | 0 | 76.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3273.36 | 0 | 3273.36 | 132863 | -19788.7 | 39 | 44 | 132863 | -1019788.7
10 | 8 | 14 | 7 | 4.4723 | 0 | 42.7453 | 0 | 10.3999 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 0 | 80.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3274.69 | 0 | 3274.69 | 153043 | -21400.1 | 38 | 41 | 153043 | -1021400.1
10 | 8 | 15 | 7 | 4.6636 | 0 | 42.7453 | 0 | 8.5181 | 0 | 5.897 | 15.3158 | 0 | 0 | 0 | 0 | 77.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3275.77 | 0 | 3275.77 | 132383 | -20746.8 | 37 | 41 | 132383 | -1020746.8
10 | 8 | 16 | 7 | 4.844 | 0 | 42.7453 | 0 | 10.1345 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3277.43 | 0 | 3277.43 | 150022 | -24014 | 37 | 41 | 150022 | -1024014
10 | 8 | 17 | 7 | 5.378 | 0 | 42.7453 | 0 | 8.9981 | 0 | 5.8967 | 15.3158 | 0 | 0 | 0 | 4.8 | 83.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3278.73 | 0 | 3278.73 | 130752 | -23515.8 | 37 | 41 | 130752 | -1023515.8
10 | 8 | 18 | 7 | 6.5392 | 0 | 42.7453 | 0 | 10.2921 | 0 | 5.8999 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3280.41 | 0 | 3280.41 | 147125 | -25903 | 37 | 41 | 147125 | -1025903
10 | 8 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3093 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3282.06 | 0 | 3282.06 | 144307 | -28099.1 | 36 | 40 | 144307 | -1028099.1
10 | 8 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4132 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3283.88 | 0 | 3283.88 | 142974 | -32964.1 | 35 | 39 | 142974 | -1032964.1
10 | 8 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6039 | 0 | 5.9 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3285.7 | 0 | 3285.7 | 141812 | -38326.8 | 34 | 39 | 141812 | -1038326.8
10 | 8 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.7964 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.8692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3287.55 | 0 | 3287.55 | 140827 | -47234.9 | 33 | 37 | 140827 | -1047234.9
10 | 8 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.7893 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3289.41 | 0 | 3289.41 | 139934 | -55271.7 | 33 | 36 | 139934 | -1055271.7
10 | 8 | 24 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0508 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3291.26 | 0 | 3291.26 | 139011 | -65490.4 | 32 | 35 | 139011 | -1065490.4
10 | 9 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.3301 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.2466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3293.06 | 0 | 3293.06 | 138306 | -74292.6 | 31 | 34 | 138306 | -1074292.6
10 | 9 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.3075 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3294.86 | 0 | 3294.86 | 137676 | -83405.3 | 31 | 33 | 137676 | -1083405.3
10 | 9 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.1944 | 0 | 5.9012 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3296.66 | 0 | 3296.66 | 136971 | -91297.7 | 29 | 32 | 136971 | -1091297.7
10 | 9 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.1064 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3298.47 | 0 | 3298.47 | 136372 | -99968.5 | 29 | 31 | 136372 | -1099968.5
10 | 9 | 5 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.0165 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3300.3 | 0 | 3300.3 | 135767 | -105049 | 29 | 31 | 135767 | -1105049
10 | 9 | 6 | 8 | 5.1054 | 0 | 42.7453 | 0 | 10.934 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 2.4 | 84.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3302.15 | 0 | 3302.15 | 135097 | -113871 | 27 | 30 | 135097 | -1113871
10 | 9 | 7 | 8 | 4.5866 | 0 | 42.7453 | 0 | 10.8915 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3303.98 | 0 | 3303.98 | 134833 | -107333 | 28 | 31 | 134833 | -1107333
10 | 9 | 8 | 8 | 3.8655 | 0 | 42.7453 | 0 | 11.0004 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 0 | 80.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3305.82 | 0 | 3305.82 | 136363 | -87640.4 | 29 | 33 | 136363 | -1087640.4
10 | 9 | 9 | 8 | 4.1852 | 0 | 42.7453 | 0 | 11.1469 | 0 | 5.9011 | 17.3638 | 0 | 0 | 0 | 0 | 81.3422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3307.6 | 0 | 3307.6 | 137530 | -66590.1 | 30 | 36 | 137530 | -1066590.1
10 | 9 | 10 | 8 | 4.1523 | 0 | 42.7453 | 0 | 11.3783 | 0 | 5.9025 | 17.3638 | 0 | 0 | 0 | 0 | 81.5422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3309.16 | 0 | 3309.16 | 139403 | -50480.9 | 32 | 39 | 139403 | -1050480.9
10 | 9 | 11 | 8 | 4.1473 | 0 | 42.7453 | 0 | 11.3252 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 0 | 81.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3309.8 | 0 | 3309.8 | 140631 | -43990.8 | 32 | 40 | 140631 | -1043990.8
10 | 9 | 12 | 8 | 4.1493 | 0 | 42.7453 | 0 | 10.7882 | 0 | 5.9005 | 17.3638 | 0 | 0 | 0 | 0 | 80.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.06 | 0 | 3310.06 | 141464 | -38436 | 34 | 42 | 141464 | -1038436
10 | 9 | 13 | 8 | 4.1514 | 0 | 42.7453 | 0 | 10.7468 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 0 | 80.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.16 | 0 | 3310.16 | 144076 | -35183 | 35 | 43 | 144076 | -1035183
10 | 9 | 14 | 8 | 4.1521 | 0 | 42.7453 | 0 | 10.2245 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 0 | 80.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.57 | 0 | 3310.57 | 142879 | -30396.7 | 35 | 43 | 142879 | -1030396.7
10 | 9 | 15 | 8 | 4.1532 | 0 | 42.7453 | 0 | 9.3327 | 0 | 5.8967 | 15.3158 | 0 | 0 | 0 | 0 | 77.4438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.87 | 0 | 3310.87 | 131130 | -27601.6 | 35 | 43 | 131130 | -1027601.6
10 | 9 | 16 | 8 | 4.1722 | 0 | 42.7453 | 0 | 9.2626 | 0 | 5.8967 | 15.3158 | 0 | 0 | 0 | 1.2 | 78.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3311.15 | 0 | 3311.15 | 130295 | -27506 | 35 | 43 | 130295 | -1027506
10 | 9 | 17 | 8 | 4.2414 | 0 | 42.7453 | 0 | 10.1563 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 85.2055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3311.58 | 0 | 3311.58 | 143096 | -28947.8 | 35 | 43 | 143096 | -1028947.8
10 | 9 | 18 | 8 | 6.4005 | 0 | 42.7453 | 0 | 10.2481 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3312.2 | 0 | 3312.2 | 140196 | -31401.5 | 33 | 40 | 140196 | -1031401.5
10 | 9 | 19 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.253 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.15 | 0 | 3313.15 | 137874 | -39067.3 | 32 | 38 | 137874 | -1039067.3
10 | 9 | 20 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.6088 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3314.37 | 0 | 3314.37 | 136110 | -49438.7 | 31 | 35 | 136110 | -1049438.7
10 | 9 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.7163 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.5878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3315.74 | 0 | 3315.74 | 134847 | -57277.6 | 31 | 37 | 134847 | -1057277.6
10 | 9 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.1287 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 6.4 | 90.2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3317.09 | 0 | 3317.09 | 134130 | -68496.7 | 29 | 33 | 134130 | -1068496.7
10 | 9 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.4475 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3318.56 | 0 | 3318.56 | 136662 | -74615.6 | 27 | 30 | 136662 | -1074615.6
10 | 9 | 24 | 8 | 10.424 | 0 | 42.3304 | 0 | 10.1429 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.9586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8387.3 | 0 | 8387.3 | 132588 | -71196.4 | 27 | 30 | 132588 | -1071196.4
10 | 10 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.4978 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.77 | 0 | 8388.77 | 133541 | -85295.4 | 26 | 28 | 133541 | -1085295.4
10 | 10 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.1114 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.93 | 0 | 8388.93 | 131851 | -90004.4 | 25 | 27 | 131851 | -1090004.4
10 | 10 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.2329 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8389.58 | 0 | 8389.58 | 132040 | -97693.1 | 25 | 26 | 132040 | -1097693.1
10 | 10 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 10.3432 | 0 | 5.8981 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.1962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9287.82 | 0 | 9287.82 | 134324 | -103371 | 24 | 25 | 134324 | -1103371
10 | 10 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 13.4577 | 0 | 5.9392 | 17.5105 | 0 | 0 | 0 | 4.8 | 135.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11286.4 | 0 | 11286.4 | 182046 | -90732.6 | 24 | 25 | 182046 | -1090732.6
10 | 10 | 6 | 2 | 49.0171 | 0 | 140.608 | 44.1604 | 0 | 0 | 6.217 | 19.06 | 0 | 0 | 0 | 2.4 | 261.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30108.5 | 0 | 30108.5 | 313011 | -809595 | 23 | 24 | 313011 | -1809595
10 | 10 | 7 | 2 | 48.31 | 0 | 168.222 | 40.8987 | 0 | 0 | 6.2313 | 19.0363 | 0 | 0 | 0 | 0.8 | 283.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33001.1 | 0 | 33001.1 | 375570 | -745773 | 23 | 25 | 375570 | -1745773
10 | 10 | 8 | 2 | 40.4234 | 0 | 173.795 | 27.9153 | 0 | 0 | 6.2451 | 19.0363 | 0 | 0 | 0 | 0 | 267.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41671.4 | 0 | 41671.4 | 394888 | -564784 | 26 | 28 | 394888 | -1564784
10 | 10 | 9 | 2 | 40.9278 | 0 | 172.186 | 0 | 25.0818 | 0 | 6.2781 | 19.0363 | 0 | 0 | 0 | 0 | 263.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64833.1 | 0 | 64833.1 | 393655 | -436329 | 30 | 34 | 393655 | -1436329
10 | 10 | 10 | 2 | 41.233 | 0 | 163.102 | 0 | 26.565 | 0 | 25.315 | 19.0363 | 0 | 0 | 0 | 0 | 275.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66278.4 | 0 | 66278.4 | 399084 | -361279 | 33 | 39 | 399084 | -1361279
10 | 10 | 11 | 2 | 40.7437 | 0 | 149.692 | 0 | 27.6153 | 0 | 25.3303 | 19.0363 | 0 | 0 | 0 | 0 | 262.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66275.8 | 0 | 66275.8 | 411273 | -311693 | 35 | 42 | 411273 | -1311693
10 | 10 | 12 | 2 | 39.8146 | 0 | 150.207 | 0 | 26.9745 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 242.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66272.8 | 0 | 66272.8 | 391264 | -253838 | 36 | 45 | 391264 | -1253838
10 | 10 | 13 | 2 | 41.314 | 0 | 165.698 | 0 | 32.433 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66269 | 0 | 66269 | 453982 | -218004 | 36 | 47 | 453982 | -1218004
10 | 10 | 14 | 2 | 40.7055 | 0 | 172.702 | 0 | 34.4329 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64816.8 | 0 | 64816.8 | 466868 | -170184 | 39 | 49 | 466868 | -1170184
10 | 10 | 15 | 2 | 40.6092 | 0 | 173.986 | 0 | 34.426 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59021.2 | 0 | 59021.2 | 465019 | -146927 | 40 | 49 | 465019 | -1146927
10 | 10 | 16 | 2 | 40.6113 | 0 | 169.782 | 0 | 32.7732 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 269.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48882.5 | 0 | 48882.5 | 447221 | -158651 | 40 | 48 | 447221 | -1158651
10 | 10 | 17 | 2 | 36.1883 | 0 | 152.497 | 0 | 29.3925 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 248.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37296.3 | 0 | 37296.3 | 416719 | -196033 | 38 | 47 | 416719 | -1196033
10 | 10 | 18 | 2 | 33.1982 | 0 | 93.4203 | 0 | 23.2977 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 182.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22815.2 | 0 | 22815.2 | 332552 | -280490 | 35 | 43 | 332552 | -1280490
10 | 10 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 8.911 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 7.2 | 117.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16298.4 | 0 | 16298.4 | 179588 | 0 | 32 | 37 | 179588 | -1000000
10 | 10 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 11.8555 | 0 | 5.9125 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15575.2 | 0 | 15575.2 | 160674 | -12070.1 | 32 | 37 | 160674 | -1012070.1
10 | 10 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.3379 | 0 | 5.897 | 12.9754 | 0 | 0 | 0 | 7.2 | 96.1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9784.4 | 0 | 9784.4 | 147483 | -8772.02 | 31 | 36 | 147483 | -1008772.02
10 | 10 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 9.752 | 0 | 5.8973 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9555.27 | 0 | 9555.27 | 136602 | -14561.6 | 32 | 36 | 136602 | -1014561.6
10 | 10 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 9.4266 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8341.71 | 0 | 8341.71 | 131928 | -14429.6 | 31 | 35 | 131928 | -1014429.6
10 | 10 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 10.4547 | 0 | 5.8991 | 15.3158 | 0 | 0 | 0 | 4.8 | 89.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8344.6 | 0 | 8344.6 | 139795 | -25727.6 | 30 | 34 | 139795 | -1025727.6
10 | 11 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.636 | 0 | 5.9082 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8347.18 | 0 | 8347.18 | 154091 | -30332.1 | 31 | 35 | 154091 | -1030332.1
10 | 11 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.9218 | 0 | 5.9091 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8349.75 | 0 | 8349.75 | 150944 | -34509 | 30 | 33 | 150944 | -1034509
10 | 11 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5481 | 0 | 5.9059 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8352.31 | 0 | 8352.31 | 148502 | -36455.1 | 30 | 34 | 148502 | -1036455.1
10 | 11 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 12.2802 | 0 | 5.9114 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9252.04 | 0 | 9252.04 | 150402 | -47907.4 | 30 | 34 | 150402 | -1047907.4
10 | 11 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.8169 | 0 | 5.9651 | 15.0234 | 0 | 0 | 0 | 4.8 | 134.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11252.1 | 0 | 11252.1 | 191004 | -28392.4 | 32 | 37 | 191004 | -1028392.4
10 | 11 | 6 | 3 | 49.0171 | 0 | 140.608 | 23.8058 | 0 | 0 | 6.2611 | 19.0363 | 0 | 0 | 0 | 2.4 | 241.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30075.4 | 0 | 30075.4 | 322797 | -493472 | 31 | 36 | 322797 | -1493472
10 | 11 | 7 | 3 | 49.5938 | 0 | 168.222 | 0 | 25.5008 | 0 | 6.274 | 19.0363 | 0 | 0 | 0 | 0.8 | 269.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32968.6 | 0 | 32968.6 | 385058 | -460064 | 32 | 37 | 385058 | -1460064
10 | 11 | 8 | 3 | 40.0633 | 0 | 173.795 | 0 | 26.7523 | 0 | 6.298 | 19.0363 | 0 | 0 | 0 | 0 | 265.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41647.6 | 0 | 41647.6 | 415206 | -356643 | 33 | 39 | 415206 | -1356643
10 | 11 | 9 | 3 | 40.6921 | 0 | 172.186 | 0 | 28.6449 | 0 | 25.326 | 19.0363 | 0 | 0 | 0 | 0 | 285.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64809.6 | 0 | 64809.6 | 432702 | -308174 | 35 | 41 | 432702 | -1308174
10 | 11 | 10 | 3 | 42.0691 | 0 | 163.102 | 0 | 29.1819 | 0 | 25.323 | 19.0363 | 0 | 0 | 0 | 0 | 278.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66254.7 | 0 | 66254.7 | 436638 | -319584 | 36 | 42 | 436638 | -1319584
10 | 11 | 11 | 3 | 41.3338 | 0 | 149.692 | 0 | 29.8336 | 0 | 25.3313 | 19.0363 | 0 | 0 | 0 | 0 | 265.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66252.5 | 0 | 66252.5 | 434099 | -290164 | 38 | 44 | 434099 | -1290164
10 | 11 | 12 | 3 | 39.9397 | 0 | 150.207 | 0 | 27.6302 | 0 | 25.3325 | 19.0363 | 0 | 0 | 0 | 0 | 262.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66250.3 | 0 | 66250.3 | 402977 | -258348 | 38 | 45 | 402977 | -1258348
10 | 11 | 13 | 3 | 42.1481 | 0 | 165.698 | 0 | 31.7707 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 283.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66247.8 | 0 | 66247.8 | 444853 | -206719 | 41 | 48 | 444853 | -1206719
10 | 11 | 14 | 3 | 41.2529 | 0 | 172.702 | 0 | 34.1851 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 292.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64797.3 | 0 | 64797.3 | 463875 | -172742 | 42 | 50 | 463875 | -1172742
10 | 11 | 15 | 3 | 41.2833 | 0 | 173.986 | 0 | 33.9069 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 293.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59002.5 | 0 | 59002.5 | 457588 | -154877 | 42 | 50 | 457588 | -1154877
10 | 11 | 16 | 3 | 46.4507 | 0 | 169.782 | 0 | 33.7453 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 1.2 | 295.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48864.7 | 0 | 48864.7 | 468229 | -203985 | 41 | 47 | 468229 | -1203985
10 | 11 | 17 | 3 | 45.2613 | 0 | 152.497 | 0 | 30.5285 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 4.8 | 277.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37279.5 | 0 | 37279.5 | 442950 | -242403 | 42 | 45 | 442950 | -1242403
10 | 11 | 18 | 3 | 33.8827 | 0 | 93.4203 | 0 | 25.1398 | 0 | 25.3185 | 19.0363 | 0 | 0 | 0 | 7.2 | 203.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22799.6 | 0 | 22799.6 | 356025 | -309646 | 43 | 44 | 356025 | -1309646
10 | 11 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.1549 | 0 | 5.49 | 8.818 | 0 | 0 | 0 | 7.2 | 117.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16283.8 | 0 | 16283.8 | 184620 | 0 | 43 | 43 | 184620 | -1000000
10 | 11 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 11.9084 | 0 | 5.9149 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15560.5 | 0 | 15560.5 | 165242 | -9548.45 | 43 | 43 | 165242 | -1009548.45
10 | 11 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.5374 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9768.09 | 0 | 9768.09 | 151846 | 0 | 43 | 43 | 151846 | -1000000
10 | 11 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.7348 | 0 | 5.9048 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9538.72 | 0 | 9538.72 | 140794 | -16838.7 | 43 | 43 | 140794 | -1016838.7
10 | 11 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8083 | 0 | 5.8994 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8324.58 | 0 | 8324.58 | 136032 | -5868.92 | 43 | 43 | 136032 | -1005868.92
10 | 11 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8309 | 0 | 5.8992 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8327.05 | 0 | 8327.05 | 136616 | -11564.8 | 43 | 43 | 136616 | -1011564.8
10 | 12 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.7025 | 0 | 5.9001 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8329.21 | 0 | 8329.21 | 133748 | -9567.11 | 44 | 44 | 133748 | -1009567.11
10 | 12 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.6803 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.2662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8331.07 | 0 | 8331.07 | 133285 | -10909.7 | 44 | 44 | 133285 | -1010909.7
10 | 12 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.466 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8332.73 | 0 | 8332.73 | 132098 | -10759 | 43 | 43 | 132098 | -1010759
10 | 12 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 9.109 | 0 | 5.8968 | 12.9754 | 0 | 0 | 0 | 4.8 | 89.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9231.84 | 0 | 9231.84 | 138466 | -11680.2 | 43 | 43 | 138466 | -1011680.2
10 | 12 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 11.3012 | 0 | 5.9181 | 12.9754 | 0 | 0 | 0 | 4.8 | 129.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11231.2 | 0 | 11231.2 | 181477 | -8573.74 | 43 | 43 | 181477 | -1008573.74
10 | 12 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 23.2274 | 0 | 6.3115 | 19.0363 | 0 | 0 | 0 | 2.4 | 240.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30054 | 0 | 30054 | 327069 | -298026 | 44 | 44 | 327069 | -1298026
10 | 12 | 7 | 4 | 51.7669 | 0 | 168.222 | 0 | 31.4087 | 0 | 25.3161 | 19.0363 | 0 | 0 | 0 | 0.8 | 296.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32946.8 | 0 | 32946.8 | 462405 | -331042 | 44 | 44 | 462405 | -1331042
10 | 12 | 8 | 4 | 40.6612 | 0 | 173.795 | 0 | 32.6207 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 291.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41628.3 | 0 | 41628.3 | 471113 | -247687 | 44 | 45 | 471113 | -1247687
10 | 12 | 9 | 4 | 41.0273 | 0 | 172.186 | 0 | 33.7521 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64791.3 | 0 | 64791.3 | 463916 | -181691 | 45 | 49 | 463916 | -1181691
10 | 12 | 10 | 4 | 41.2963 | 0 | 163.102 | 0 | 33.5556 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66237.1 | 0 | 66237.1 | 439306 | -124108 | 48 | 53 | 439306 | -1124108
10 | 12 | 11 | 4 | 40.7523 | 0 | 149.692 | 0 | 33.1177 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66234.3 | 0 | 66234.3 | 441981 | -87309.2 | 48 | 56 | 441981 | -1087309.2
10 | 12 | 12 | 4 | 39.82 | 0 | 150.207 | 0 | 30.372 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66231.1 | 0 | 66231.1 | 460902 | -62382.8 | 49 | 58 | 460902 | -1062382.8
10 | 12 | 13 | 4 | 41.2808 | 0 | 165.698 | 0 | 30.0185 | 0 | 6.332 | 19.0429 | 0 | 0 | 0 | 0 | 262.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66228.9 | 0 | 66228.9 | 479757 | -39820.8 | 50 | 58 | 479757 | -1039820.8
10 | 12 | 14 | 4 | 40.6844 | 0 | 172.702 | 0 | 30.7364 | 0 | 6.332 | 19.0924 | 0 | 0 | 0 | 0 | 269.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64779.6 | 0 | 64779.6 | 513519 | -40797.3 | 51 | 56 | 513519 | -1040797.3
10 | 12 | 15 | 4 | 40.604 | 0 | 173.986 | 0 | 27.8172 | 0 | 25.335 | 19.1718 | 0 | 0 | 0 | 0 | 286.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58986.4 | 0 | 58986.4 | 507561 | -30976.6 | 51 | 56 | 507561 | -1030976.6
10 | 12 | 16 | 4 | 40.3845 | 0 | 169.782 | 0 | 27.3562 | 0 | 6.332 | 19.074 | 0 | 0 | 0 | 1.2 | 264.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48849.6 | 0 | 48849.6 | 468124 | -45949.8 | 49 | 53 | 468124 | -1045949.8
10 | 12 | 17 | 4 | 36.8279 | 0 | 152.497 | 0 | 25.6498 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 245.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37265.4 | 0 | 37265.4 | 420079 | -68257.2 | 49 | 52 | 420079 | -1068257.2
10 | 12 | 18 | 4 | 33.3158 | 0 | 93.4203 | 0 | 23.1797 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 182.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22786.1 | 0 | 22786.1 | 342208 | -167161 | 46 | 48 | 342208 | -1167161
10 | 12 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.266 | 0 | 5.4917 | 8.818 | 0 | 0 | 0 | 7.2 | 117.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16270.9 | 0 | 16270.9 | 187330 | 0 | 45 | 46 | 187330 | -1000000
10 | 12 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.2718 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 7.2 | 103.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15548.2 | 0 | 15548.2 | 167820 | 0 | 44 | 44 | 167820 | -1000000
10 | 12 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 10.3352 | 0 | 5.9019 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9752.88 | 0 | 9752.88 | 154268 | -6855.13 | 43 | 43 | 154268 | -1006855.13
10 | 12 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.1344 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9522.63 | 0 | 9522.63 | 143060 | 0 | 42 | 42 | 143060 | -1000000
10 | 12 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0777 | 0 | 5.8978 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.71 | 0 | 8307.71 | 141990 | -2225.99 | 40 | 40 | 141990 | -1002225.99
10 | 12 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.8339 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8309.57 | 0 | 8309.57 | 136581 | 0 | 40 | 40 | 136581 | -1000000
10 | 13 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9691 | 0 | 5.8983 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8311.13 | 0 | 8311.13 | 139682 | -3425.66 | 38 | 38 | 139682 | -1003425.66
10 | 13 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8401 | 0 | 5.8991 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.6 | 0 | 8312.6 | 136759 | -3909.64 | 38 | 38 | 136759 | -1003909.64
10 | 13 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8768 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8313.79 | 0 | 8313.79 | 137625 | -4892.44 | 38 | 38 | 137625 | -1004892.44
10 | 13 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 8.6723 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 4.8 | 88.9889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9212.75 | 0 | 9212.75 | 136490 | -8642.77 | 39 | 39 | 136490 | -1008642.77
10 | 13 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 8.9 | 0 | 5.9048 | 12.9754 | 0 | 0 | 0 | 4.8 | 126.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11212.7 | 0 | 11212.7 | 182667 | -6445.88 | 39 | 39 | 182667 | -1006445.88
10 | 13 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 23.0219 | 0 | 6.3184 | 19.0363 | 0 | 0 | 0 | 2.4 | 240.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30035.7 | 0 | 30035.7 | 328100 | -288244 | 40 | 40 | 328100 | -1288244
10 | 13 | 7 | 5 | 52.1429 | 0 | 168.222 | 0 | 27.1161 | 0 | 25.3167 | 19.0363 | 0 | 0 | 0 | 0.8 | 292.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32928.5 | 0 | 32928.5 | 414355 | -302156 | 40 | 40 | 414355 | -1302156
10 | 13 | 8 | 5 | 49.4902 | 0 | 173.795 | 0 | 28.7751 | 0 | 25.3346 | 19.0363 | 0 | 0 | 0 | 0 | 296.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41613.5 | 0 | 41613.5 | 435916 | -252156 | 40 | 40 | 435916 | -1252156
10 | 13 | 9 | 5 | 42.3834 | 0 | 172.186 | 0 | 30.3903 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 289.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64778 | 0 | 64778 | 450831 | -264082 | 41 | 41 | 450831 | -1264082
10 | 13 | 10 | 5 | 42.3674 | 0 | 163.102 | 0 | 31.0778 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 280.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66224.7 | 0 | 66224.7 | 458913 | -266490 | 42 | 42 | 458913 | -1266490
10 | 13 | 11 | 5 | 41.2254 | 0 | 149.692 | 0 | 31.933 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 267.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66223.8 | 0 | 66223.8 | 459842 | -230908 | 44 | 44 | 459842 | -1230908
10 | 13 | 12 | 5 | 39.8151 | 0 | 150.207 | 0 | 29.5446 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 263.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66223.2 | 0 | 66223.2 | 416543 | -172402 | 46 | 47 | 416543 | -1172402
10 | 13 | 13 | 5 | 41.3088 | 0 | 165.698 | 0 | 34.0961 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66222.4 | 0 | 66222.4 | 456055 | -116575 | 49 | 51 | 456055 | -1116575
10 | 13 | 14 | 5 | 40.6994 | 0 | 172.702 | 0 | 42.3951 | 0 | 6.332 | 19.0615 | 0 | 0 | 0 | 0 | 281.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64773.1 | 0 | 64773.1 | 557328 | -57907.3 | 54 | 57 | 557328 | -1057907.3
10 | 13 | 15 | 5 | 40.6031 | 0 | 173.986 | 0 | 32.3255 | 0 | 25.335 | 19.604 | 0 | 0 | 0 | 0 | 291.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58979.9 | 0 | 58979.9 | 620188 | -21796.4 | 56 | 61 | 620188 | -1021796.4
10 | 13 | 16 | 5 | 40.4667 | 0 | 169.782 | 0 | 33.305 | 0 | 25.335 | 19.7165 | 0 | 0 | 0 | 1.2 | 289.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48843.2 | 0 | 48843.2 | 639441 | -16531.2 | 56 | 63 | 639441 | -1016531.2
10 | 13 | 17 | 5 | 36.495 | 0 | 152.497 | 0 | 21.5921 | 0 | 6.332 | 19.4227 | 0 | 0 | 0 | 4.8 | 241.139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37259 | 0 | 37259 | 472691 | -13113.9 | 54 | 59 | 472691 | -1013113.9
10 | 13 | 18 | 5 | 33.5323 | 0 | 93.4203 | 0 | 20.0354 | 0 | 6.3317 | 19.0363 | 0 | 0 | 0 | 7.2 | 179.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22779.7 | 0 | 22779.7 | 331328 | -24628 | 51 | 54 | 331328 | -1024628
10 | 13 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.2942 | 0 | 5.4921 | 8.818 | 0 | 0 | 0 | 7.2 | 117.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16264.4 | 0 | 16264.4 | 188142 | 0 | 50 | 52 | 188142 | -1000000
10 | 13 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.2986 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 7.2 | 103.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15541.8 | 0 | 15541.8 | 168401 | 0 | 48 | 49 | 168401 | -1000000
10 | 13 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.6788 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9744.83 | 0 | 9744.83 | 154939 | 0 | 46 | 47 | 154939 | -1000000
10 | 13 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.1714 | 0 | 5.4793 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9513.61 | 0 | 9513.61 | 143874 | 0 | 45 | 46 | 143874 | -1000000
10 | 13 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 9.5038 | 0 | 5.8972 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.8342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8298.34 | 0 | 8298.34 | 139081 | -7412.34 | 45 | 46 | 139081 | -1007412.34
10 | 13 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.8591 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 75.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.26 | 0 | 8300.26 | 137191 | 0 | 45 | 46 | 137191 | -1000000
10 | 14 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.2165 | 0 | 5.898 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.06 | 0 | 8302.06 | 136220 | -12070.7 | 45 | 45 | 136220 | -1012070.7
10 | 14 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7651 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304.46 | 0 | 8304.46 | 135148 | 0 | 44 | 44 | 135148 | -1000000
10 | 14 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.4609 | 0 | 5.8983 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8306.25 | 0 | 8306.25 | 134130 | -14522.5 | 41 | 41 | 134130 | -1014522.5
10 | 14 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.685 | 0 | 5.9003 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.16 | 0 | 8308.16 | 133400 | -4215.31 | 40 | 40 | 133400 | -1004215.31
10 | 14 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 8.6564 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8309.8 | 0 | 8309.8 | 134666 | -10985 | 39 | 39 | 134666 | -1010985
10 | 14 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 8.2361 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 2.4 | 78.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8311.7 | 0 | 8311.7 | 131889 | -9275.94 | 39 | 39 | 131889 | -1009275.94
10 | 14 | 7 | 6 | 6.192 | 0 | 42.7453 | 21.1576 | 0 | 0 | 6.219 | 18.8896 | 0 | 0 | 0 | 0.8 | 96.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8313.59 | 0 | 8313.59 | 139312 | -371596 | 41 | 41 | 139312 | -1371596
10 | 14 | 8 | 6 | 6.1934 | 0 | 42.7453 | 21.363 | 0 | 0 | 6.2636 | 18.8896 | 0 | 0 | 0 | 0 | 95.4548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8315.36 | 0 | 8315.36 | 205695 | -401272 | 42 | 42 | 205695 | -1401272
10 | 14 | 9 | 6 | 5.4771 | 0 | 42.7453 | 16.9642 | 0 | 0 | 6.0338 | 18.8896 | 0 | 0 | 0 | 0 | 90.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.54 | 0 | 8317.54 | 188659 | -301705 | 45 | 45 | 188659 | -1301705
10 | 14 | 10 | 6 | 5.4895 | 0 | 42.7453 | 0 | 14.6947 | 0 | 11.5547 | 18.8896 | 0 | 0 | 0 | 0 | 93.3738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316.79 | 0 | 8316.79 | 193478 | -233064 | 48 | 50 | 193478 | -1233064
10 | 14 | 11 | 6 | 5.4752 | 0 | 42.7453 | 0 | 15.7129 | 0 | 5.9804 | 18.8896 | 0 | 0 | 0 | 0 | 88.8034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.89 | 0 | 8317.89 | 189969 | -155870 | 52 | 58 | 189969 | -1155870
10 | 14 | 12 | 6 | 5.4768 | 0 | 42.7453 | 0 | 20.4993 | 0 | 6.2076 | 18.8896 | 0 | 0 | 0 | 0 | 93.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.28 | 0 | 8318.28 | 221987 | -110182 | 56 | 64 | 221987 | -1110182
10 | 14 | 13 | 6 | 5.4791 | 0 | 42.7453 | 0 | 21.5383 | 0 | 6.332 | 18.8896 | 0 | 0 | 0 | 0 | 94.9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.13 | 0 | 8318.13 | 280282 | -93071 | 57 | 68 | 280282 | -1093071
10 | 14 | 14 | 6 | 5.48 | 0 | 42.7453 | 0 | 9.1573 | 0 | 8.3072 | 12.8287 | 0 | 0 | 0 | 0 | 78.5184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.79 | 0 | 8317.79 | 162771 | 0 | 58 | 68 | 162771 | -1000000
10 | 14 | 15 | 6 | 5.4879 | 0 | 42.7453 | 0 | 9.7307 | 0 | 8.9799 | 12.8287 | 0 | 0 | 0 | 0 | 79.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.41 | 0 | 8317.41 | 161881 | 0 | 58 | 70 | 161881 | -1000000
10 | 14 | 16 | 6 | 5.5432 | 0 | 42.7453 | 0 | 8.906 | 0 | 8.3369 | 12.8287 | 0 | 0 | 0 | 1.2 | 79.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316.17 | 0 | 8316.17 | 163470 | 0 | 58 | 70 | 163470 | -1000000
10 | 14 | 17 | 6 | 5.6434 | 0 | 42.7453 | 0 | 5.9098 | 0 | 5.4879 | 8.818 | 0 | 0 | 0 | 4.8 | 73.4044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8314.11 | 0 | 8314.11 | 127836 | 0 | 57 | 67 | 127836 | -1000000
10 | 14 | 18 | 6 | 8.6385 | 0 | 42.7453 | 0 | 5.184 | 0 | 5.5033 | 8.818 | 0 | 0 | 0 | 7.2 | 78.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.95 | 0 | 8312.95 | 127430 | 0 | 54 | 62 | 127430 | -1000000
10 | 14 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 5.8947 | 0 | 5.4914 | 8.818 | 0 | 0 | 0 | 7.2 | 78.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312 | 0 | 8312 | 127344 | 0 | 53 | 59 | 127344 | -1000000
10 | 14 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3975 | 0 | 5.4848 | 8.818 | 0 | 0 | 0 | 7.2 | 79.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8311.68 | 0 | 8311.68 | 127117 | 0 | 52 | 56 | 127117 | -1000000
10 | 14 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3828 | 0 | 5.485 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8311.81 | 0 | 8311.81 | 126793 | 0 | 51 | 54 | 126793 | -1000000
10 | 14 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.368 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 6.4 | 78.6137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.24 | 0 | 8312.24 | 126469 | 0 | 50 | 53 | 126469 | -1000000
10 | 14 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3582 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 5.6 | 77.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.83 | 0 | 8312.83 | 126257 | 0 | 50 | 53 | 126257 | -1000000
10 | 14 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.343 | 0 | 5.4854 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.3 | 0 | 3246.3 | 125922 | 0 | 50 | 52 | 125922 | -1000000
10 | 15 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.3229 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.08 | 0 | 3247.08 | 125493 | -7359.2 | 49 | 51 | 125493 | -1007359.2
10 | 15 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.3081 | 0 | 5.4858 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3248.05 | 0 | 3248.05 | 125158 | 0 | 48 | 50 | 125158 | -1000000
10 | 15 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.6595 | 0 | 5.8974 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.03 | 0 | 3249.03 | 124962 | -9317.62 | 48 | 49 | 124962 | -1009317.62
10 | 15 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2787 | 0 | 5.4862 | 8.818 | 0 | 0 | 0 | 4.8 | 73.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.15 | 0 | 3250.15 | 124513 | 0 | 47 | 49 | 124513 | -1000000
10 | 15 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.0404 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.4168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.17 | 0 | 3251.17 | 124400 | -11348.2 | 47 | 48 | 124400 | -1011348.2
10 | 15 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 6.2506 | 0 | 5.4865 | 8.818 | 0 | 0 | 0 | 2.4 | 70.8058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3252.35 | 0 | 3252.35 | 123898 | 0 | 45 | 47 | 123898 | -1000000
10 | 15 | 7 | 7 | 4.7989 | 0 | 42.7453 | 0 | 9.3859 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0.8 | 76.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.45 | 0 | 3253.45 | 123911 | -13290.8 | 46 | 48 | 123911 | -1013290.8
10 | 15 | 8 | 7 | 3.8753 | 0 | 42.7453 | 0 | 6.2444 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 0 | 67.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3254.7 | 0 | 3254.7 | 123767 | 0 | 48 | 51 | 123767 | -1000000
10 | 15 | 9 | 7 | 4.186 | 0 | 42.7453 | 0 | 9.1273 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 0 | 74.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.89 | 0 | 3255.89 | 123637 | -12163.1 | 50 | 55 | 123637 | -1012163.1
10 | 15 | 10 | 7 | 4.1512 | 0 | 42.7453 | 0 | 6.2401 | 0 | 5.4866 | 8.818 | 0 | 0 | 0 | 0 | 67.4412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.85 | 0 | 3256.85 | 123676 | 0 | 53 | 60 | 123676 | -1000000
10 | 15 | 11 | 7 | 4.1484 | 0 | 42.7453 | 0 | 8.0405 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 0 | 73.6618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.39 | 0 | 3256.39 | 130428 | -1779.75 | 55 | 65 | 130428 | -1001779.75
10 | 15 | 12 | 7 | 4.1496 | 0 | 42.7453 | 0 | 8.9844 | 0 | 5.9127 | 12.8287 | 0 | 0 | 0 | 0 | 74.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.39 | 0 | 3255.39 | 152088 | -1148.15 | 57 | 69 | 152088 | -1001148.15
10 | 15 | 13 | 7 | 4.1511 | 0 | 42.7453 | 0 | 9.6481 | 0 | 5.9308 | 12.8287 | 0 | 0 | 0 | 0 | 75.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.81 | 0 | 3253.81 | 167900 | -741.86 | 57 | 72 | 167900 | -1000741.86
10 | 15 | 14 | 7 | 4.1518 | 0 | 42.7453 | 0 | 8.9305 | 0 | 5.4962 | 12.8287 | 0 | 0 | 0 | 0 | 74.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3252.45 | 0 | 3252.45 | 169829 | 0 | 58 | 72 | 169829 | -1000000
10 | 15 | 15 | 7 | 4.1531 | 0 | 42.7453 | 0 | 8.8375 | 0 | 5.4945 | 12.8287 | 0 | 0 | 0 | 0 | 74.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.79 | 0 | 3250.79 | 167862 | 0 | 59 | 72 | 167862 | -1000000
10 | 15 | 16 | 7 | 4.1678 | 0 | 42.7453 | 0 | 8.4301 | 0 | 5.4873 | 12.8287 | 0 | 0 | 0 | 1.2 | 74.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.03 | 0 | 3249.03 | 166178 | 0 | 59 | 71 | 166178 | -1000000
10 | 15 | 17 | 7 | 4.3643 | 0 | 42.7453 | 0 | 6.0502 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 4.8 | 72.2631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.41 | 0 | 3247.41 | 123604 | 0 | 57 | 69 | 123604 | -1000000
10 | 15 | 18 | 7 | 6.5746 | 0 | 42.7453 | 0 | 5.356 | 0 | 5.498 | 8.818 | 0 | 0 | 0 | 7.2 | 76.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.09 | 0 | 3246.09 | 123660 | 0 | 55 | 65 | 123660 | -1000000
10 | 15 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 4.9574 | 0 | 5.5097 | 8.818 | 0 | 0 | 0 | 7.2 | 75.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.24 | 0 | 3245.24 | 123676 | 0 | 53 | 59 | 123676 | -1000000
10 | 15 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2379 | 0 | 5.4867 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.85 | 0 | 3244.85 | 123627 | 0 | 53 | 58 | 123627 | -1000000
10 | 15 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2348 | 0 | 5.4867 | 8.818 | 0 | 0 | 0 | 7.2 | 77.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.82 | 0 | 3244.82 | 123560 | 0 | 53 | 58 | 123560 | -1000000
10 | 15 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2274 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 6.4 | 76.3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.92 | 0 | 3244.92 | 123396 | 0 | 52 | 57 | 123396 | -1000000
10 | 15 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 6.2269 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 5.6 | 75.5403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.97 | 0 | 3244.97 | 123386 | 0 | 52 | 56 | 123386 | -1000000
10 | 15 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 6.2276 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.68 | 0 | 8312.68 | 123403 | 0 | 50 | 53 | 123403 | -1000000
10 | 16 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2237 | 0 | 5.4868 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8313.1 | 0 | 8313.1 | 123314 | 0 | 49 | 52 | 123314 | -1000000
10 | 16 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.2208 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 4.8 | 78.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.82 | 0 | 8312.82 | 123252 | 0 | 49 | 52 | 123252 | -1000000
10 | 16 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 6.219 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.73 | 0 | 8312.73 | 123213 | 0 | 50 | 53 | 123213 | -1000000
10 | 16 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 8.3007 | 0 | 5.8975 | 12.9754 | 0 | 0 | 0 | 4.8 | 88.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9210.38 | 0 | 9210.38 | 129857 | -7907.07 | 50 | 53 | 129857 | -1007907.07
10 | 16 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 9.6101 | 0 | 5.9157 | 12.9754 | 0 | 0 | 0 | 4.8 | 127.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22096.5 | 0 | 22096.5 | 198589 | -3563.52 | 49 | 52 | 198589 | -1003563.52
10 | 16 | 6 | 1 | 49.0171 | 0 | 140.608 | 0 | 23.5463 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 240.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65113.4 | 0 | 65113.4 | 319726 | -69931 | 49 | 52 | 319726 | -1069931
10 | 16 | 7 | 1 | 49.8598 | 0 | 168.222 | 0 | 29.6747 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 273.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79039.5 | 0 | 79039.5 | 432467 | -100825 | 49 | 52 | 432467 | -1100825
10 | 16 | 8 | 1 | 40.8743 | 0 | 173.795 | 0 | 31.7591 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109345 | 0 | 109345 | 473657 | -66638.1 | 50 | 55 | 473657 | -1066638.1
10 | 16 | 9 | 1 | 41.0299 | 0 | 172.186 | 0 | 34.491 | 0 | 6.332 | 19.4308 | 0 | 0 | 0 | 0 | 273.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128631 | 0 | 128631 | 533328 | -24456.6 | 52 | 61 | 533328 | -1024456.6
10 | 16 | 10 | 1 | 41.2858 | 0 | 163.102 | 0 | 44.8291 | 0 | 6.332 | 19.6258 | 0 | 0 | 0 | 0 | 275.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131381 | 0 | 131381 | 667179 | -41503.6 | 54 | 63 | 667179 | -1041503.6
10 | 16 | 11 | 1 | 40.7638 | 0 | 149.692 | 0 | 48.6162 | 0 | 6.332 | 19.7791 | 0 | 0 | 0 | 0 | 265.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131380 | 0 | 131380 | 718781 | -42053 | 55 | 68 | 718781 | -1042053
10 | 16 | 12 | 1 | 39.8257 | 0 | 150.207 | 0 | 60.3863 | 0 | 6.332 | 19.6555 | 0 | 0 | 0 | 0 | 276.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131380 | 0 | 131380 | 873428 | -58718.7 | 58 | 73 | 873428 | -1058718.7
10 | 16 | 13 | 1 | 41.3205 | 0 | 165.698 | 0 | 64.2116 | 0 | 6.332 | 20.2686 | 0 | 0 | 0 | 0 | 297.831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131380 | 0 | 131380 | 980033 | -44503.2 | 59 | 75 | 980033 | -1044503.2
10 | 16 | 14 | 1 | 40.711 | 0 | 172.702 | 0 | 66.508 | 0 | 6.332 | 20.6264 | 0 | 0 | 0 | 0 | 306.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129686 | 0 | 129686 | 1048960 | -36428.2 | 60 | 76 | 1048960 | -1036428.2
10 | 16 | 15 | 1 | 40.6151 | 0 | 173.986 | 0 | 72.2461 | 0 | 6.332 | 20.5763 | 0 | 0 | 0 | 0 | 313.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117912 | 0 | 117912 | 1131370 | -41673.6 | 61 | 76 | 1131370 | -1041673.6
10 | 16 | 16 | 1 | 40.7602 | 0 | 169.782 | 0 | 59.6954 | 0 | 6.332 | 21.3137 | 0 | 0 | 0 | 1.2 | 299.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96277.8 | 0 | 96277.8 | 1022240 | -19934.2 | 60 | 75 | 1022240 | -1019934.2
10 | 16 | 17 | 1 | 36.7882 | 0 | 152.497 | 0 | 47.4575 | 0 | 6.332 | 21.0643 | 0 | 0 | 0 | 4.8 | 268.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72240.2 | 0 | 72240.2 | 874512 | -9966.45 | 60 | 73 | 874512 | -1009966.45
10 | 16 | 18 | 1 | 33.6794 | 0 | 93.4203 | 0 | 24.0659 | 0 | 6.332 | 19.6177 | 0 | 0 | 0 | 7.2 | 184.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44786.3 | 0 | 44786.3 | 502170 | -7831.19 | 57 | 69 | 502170 | -1007831.19
10 | 16 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 9.1527 | 0 | 5.4958 | 8.818 | 0 | 0 | 0 | 7.2 | 117.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32087.1 | 0 | 32087.1 | 185862 | 0 | 56 | 67 | 185862 | -1000000
10 | 16 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.2052 | 0 | 5.4824 | 8.818 | 0 | 0 | 0 | 7.2 | 103.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28496.7 | 0 | 28496.7 | 166210 | 0 | 56 | 66 | 166210 | -1000000
10 | 16 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.5244 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17542.2 | 0 | 17542.2 | 152783 | 0 | 54 | 65 | 152783 | -1000000
10 | 16 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.987 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9505.7 | 0 | 9505.7 | 142210 | 0 | 54 | 64 | 142210 | -1000000
10 | 16 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.7263 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 5.6 | 79.4832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.52 | 0 | 8288.52 | 137513 | 0 | 54 | 63 | 137513 | -1000000
10 | 16 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.331 | 0 | 5.4852 | 8.818 | 0 | 0 | 0 | 4.8 | 78.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.74 | 0 | 8288.74 | 136141 | 0 | 54 | 61 | 136141 | -1000000
10 | 17 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5127 | 0 | 5.4837 | 8.818 | 0 | 0 | 0 | 4.8 | 78.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.93 | 0 | 8288.93 | 135241 | 0 | 53 | 59 | 135241 | -1000000
10 | 17 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7361 | 0 | 5.4817 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8289.09 | 0 | 8289.09 | 134518 | 0 | 52 | 57 | 134518 | -1000000
10 | 17 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.7154 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8289.28 | 0 | 8289.28 | 134071 | 0 | 53 | 57 | 134071 | -1000000
10 | 17 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.8482 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 82.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9187.21 | 0 | 9187.21 | 137034 | 0 | 52 | 54 | 137034 | -1000000
10 | 17 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 8.9307 | 0 | 5.487 | 8.818 | 0 | 0 | 0 | 4.8 | 122.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22073.2 | 0 | 22073.2 | 183341 | 0 | 49 | 51 | 183341 | -1000000
10 | 17 | 6 | 2 | 49.0171 | 0 | 140.608 | 0 | 28.3543 | 0 | 6.332 | 19.5441 | 0 | 0 | 0 | 2.4 | 246.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65090.2 | 0 | 65090.2 | 361706 | -30703.8 | 50 | 52 | 361706 | -1030703.8
10 | 17 | 7 | 2 | 51.3096 | 0 | 168.222 | 0 | 20.6974 | 0 | 6.332 | 19.171 | 0 | 0 | 0 | 0.8 | 266.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79016.3 | 0 | 79016.3 | 440651 | -25875.2 | 49 | 50 | 440651 | -1025875.2
10 | 17 | 8 | 2 | 40.4732 | 0 | 173.795 | 0 | 27.0542 | 0 | 6.332 | 19.3824 | 0 | 0 | 0 | 0 | 267.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109331 | 0 | 109331 | 578108 | -25445.7 | 53 | 56 | 578108 | -1025445.7
10 | 17 | 9 | 2 | 40.9237 | 0 | 172.186 | 0 | 28.1213 | 0 | 6.332 | 20.0225 | 0 | 0 | 0 | 0 | 267.586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128618 | 0 | 128618 | 598967 | -14270.4 | 53 | 57 | 598967 | -1014270.4
10 | 17 | 10 | 2 | 41.2231 | 0 | 163.102 | 0 | 37.5457 | 0 | 6.332 | 20.6032 | 0 | 0 | 0 | 0 | 268.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131370 | 0 | 131370 | 680457 | -18381 | 54 | 61 | 680457 | -1018381
10 | 17 | 11 | 2 | 40.7533 | 0 | 149.692 | 0 | 43.191 | 0 | 9.0721 | 20.4682 | 0 | 0 | 0 | 0 | 263.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131369 | 0 | 131369 | 749474 | -27988.3 | 56 | 65 | 749474 | -1027988.3
10 | 17 | 12 | 2 | 39.8141 | 0 | 150.207 | 0 | 49.5266 | 0 | 25.335 | 20.1147 | 0 | 0 | 0 | 0 | 284.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131369 | 0 | 131369 | 822592 | -44988.4 | 56 | 68 | 822592 | -1044988.4
10 | 17 | 13 | 2 | 41.3167 | 0 | 165.698 | 0 | 42.1537 | 0 | 25.335 | 21.2682 | 0 | 0 | 0 | 0 | 295.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131370 | 0 | 131370 | 762226 | -8289.67 | 56 | 67 | 762226 | -1008289.67
10 | 17 | 14 | 2 | 41.2499 | 0 | 172.702 | 0 | 40.9464 | 0 | 25.335 | 21.1481 | 0 | 0 | 0 | 0 | 301.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129676 | 0 | 129676 | 744658 | -8251.21 | 55 | 66 | 744658 | -1008251.21
10 | 17 | 15 | 2 | 41.7418 | 0 | 173.986 | 0 | 39.6156 | 0 | 25.335 | 21.2028 | 0 | 0 | 0 | 0 | 301.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117902 | 0 | 117902 | 730560 | -8054.94 | 54 | 65 | 730560 | -1008054.94
10 | 17 | 16 | 2 | 42.7732 | 0 | 169.782 | 0 | 36.4536 | 0 | 25.335 | 20.8015 | 0 | 0 | 0 | 1.2 | 296.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96266.9 | 0 | 96266.9 | 705052 | -8003.47 | 54 | 63 | 705052 | -1008003.47
10 | 17 | 17 | 2 | 45.7809 | 0 | 152.497 | 0 | 28.7648 | 0 | 25.335 | 20.5104 | 0 | 0 | 0 | 4.8 | 277.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72229 | 0 | 72229 | 581629 | -7668.14 | 53 | 60 | 581629 | -1007668.14
10 | 17 | 18 | 2 | 33.9776 | 0 | 93.4203 | 0 | 18.6202 | 0 | 6.332 | 19.1911 | 0 | 0 | 0 | 7.2 | 178.741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44776.1 | 0 | 44776.1 | 365287 | -8036.47 | 52 | 57 | 365287 | -1008036.47
10 | 17 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.3823 | 0 | 5.4935 | 8.818 | 0 | 0 | 0 | 7.2 | 117.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32078.7 | 0 | 32078.7 | 189527 | 0 | 51 | 55 | 189527 | -1000000
10 | 17 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.3578 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 7.2 | 103.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28489.6 | 0 | 28489.6 | 169697 | 0 | 50 | 54 | 169697 | -1000000
10 | 17 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.7454 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17534.8 | 0 | 17534.8 | 156400 | 0 | 50 | 53 | 156400 | -1000000
10 | 17 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.226 | 0 | 5.4791 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9499.17 | 0 | 9499.17 | 145064 | 0 | 48 | 50 | 145064 | -1000000
10 | 17 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.997 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 5.6 | 79.753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8282.64 | 0 | 8282.64 | 140158 | 0 | 47 | 48 | 140158 | -1000000
10 | 17 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.9196 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8283.67 | 0 | 8283.67 | 138520 | 0 | 46 | 47 | 138520 | -1000000
10 | 18 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8693 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8284.4 | 0 | 8284.4 | 137428 | 0 | 44 | 45 | 137428 | -1000000
10 | 18 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.8287 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.14 | 0 | 8285.14 | 136543 | 0 | 43 | 44 | 136543 | -1000000
10 | 18 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7927 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.79 | 0 | 8285.79 | 135757 | 0 | 43 | 45 | 135757 | -1000000
10 | 18 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.9149 | 0 | 5.8987 | 12.9754 | 0 | 0 | 0 | 4.8 | 87.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9184.15 | 0 | 9184.15 | 138489 | -1672.71 | 42 | 44 | 138489 | -1001672.71
10 | 18 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.9853 | 0 | 5.4877 | 8.818 | 0 | 0 | 0 | 4.8 | 122.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22070.5 | 0 | 22070.5 | 184531 | 0 | 40 | 42 | 184531 | -1000000
10 | 18 | 6 | 3 | 49.0171 | 0 | 140.608 | 0 | 22.0547 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65088.6 | 0 | 65088.6 | 329766 | -62994.4 | 39 | 41 | 329766 | -1062994.4
10 | 18 | 7 | 3 | 50.2195 | 0 | 168.222 | 0 | 28.1074 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79015.5 | 0 | 79015.5 | 424304 | -142645 | 38 | 39 | 424304 | -1142645
10 | 18 | 8 | 3 | 41.099 | 0 | 173.795 | 0 | 35.3083 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109329 | 0 | 109329 | 496815 | -131175 | 42 | 45 | 496815 | -1131175
10 | 18 | 9 | 3 | 41.2852 | 0 | 172.186 | 0 | 31.7459 | 0 | 6.332 | 19.2737 | 0 | 0 | 0 | 0 | 270.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128618 | 0 | 128618 | 516537 | -92973.5 | 42 | 48 | 516537 | -1092973.5
10 | 18 | 10 | 3 | 41.3641 | 0 | 163.102 | 0 | 31.0157 | 0 | 17.4009 | 19.4793 | 0 | 0 | 0 | 0 | 272.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131369 | 0 | 131369 | 509759 | -63946.5 | 42 | 50 | 509759 | -1063946.5
10 | 18 | 11 | 3 | 40.7736 | 0 | 149.692 | 0 | 34.0167 | 0 | 6.332 | 19.5907 | 0 | 0 | 0 | 0 | 250.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 531138 | -51540.1 | 43 | 53 | 531138 | -1051540.1
10 | 18 | 12 | 3 | 39.8177 | 0 | 150.207 | 0 | 36.7614 | 0 | 6.332 | 19.8263 | 0 | 0 | 0 | 0 | 252.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 568621 | -46109.1 | 44 | 56 | 568621 | -1046109.1
10 | 18 | 13 | 3 | 41.2952 | 0 | 165.698 | 0 | 34.0082 | 0 | 6.332 | 20.9309 | 0 | 0 | 0 | 0 | 268.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131369 | 0 | 131369 | 573142 | -14928.7 | 44 | 57 | 573142 | -1014928.7
10 | 18 | 14 | 3 | 40.6876 | 0 | 172.702 | 0 | 31.7767 | 0 | 25.335 | 20.8126 | 0 | 0 | 0 | 0 | 291.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129674 | 0 | 129674 | 592743 | -12642.7 | 43 | 56 | 592743 | -1012642.7
10 | 18 | 15 | 3 | 40.5937 | 0 | 173.986 | 0 | 28.93 | 0 | 25.335 | 20.7875 | 0 | 0 | 0 | 0 | 289.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117901 | 0 | 117901 | 544292 | -14161.4 | 42 | 53 | 544292 | -1014161.4
10 | 18 | 16 | 3 | 40.4718 | 0 | 169.782 | 0 | 26.9514 | 0 | 25.335 | 20.2817 | 0 | 0 | 0 | 1.2 | 284.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96266 | 0 | 96266 | 523255 | -16640 | 42 | 53 | 523255 | -1016640
10 | 18 | 17 | 3 | 38.948 | 0 | 152.497 | 0 | 23.559 | 0 | 25.335 | 19.4031 | 0 | 0 | 0 | 4.8 | 264.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72228.2 | 0 | 72228.2 | 429991 | -30922.8 | 41 | 51 | 429991 | -1030922.8
10 | 18 | 18 | 3 | 33.9636 | 0 | 93.4203 | 0 | 21.7166 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 181.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44775.3 | 0 | 44775.3 | 343675 | -78685.5 | 40 | 49 | 343675 | -1078685.5
10 | 18 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.3446 | 0 | 5.4929 | 8.818 | 0 | 0 | 0 | 7.2 | 117.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32078.1 | 0 | 32078.1 | 189054 | 0 | 38 | 47 | 189054 | -1000000
10 | 18 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.3466 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 7.2 | 103.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28489.3 | 0 | 28489.3 | 169455 | 0 | 36 | 44 | 169455 | -1000000
10 | 18 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 9.9348 | 0 | 5.9009 | 12.9754 | 0 | 0 | 0 | 7.2 | 98.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17536.1 | 0 | 17536.1 | 155935 | -5089.2 | 36 | 42 | 155935 | -1005089.2
10 | 18 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2062 | 0 | 5.4792 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9501.3 | 0 | 9501.3 | 144631 | 0 | 36 | 42 | 144631 | -1000000
10 | 18 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 10.6077 | 0 | 5.8996 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.76 | 0 | 8285.76 | 139727 | -12262.5 | 35 | 41 | 139727 | -1012262.5
10 | 18 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.8964 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8287.88 | 0 | 8287.88 | 138011 | 0 | 35 | 41 | 138011 | -1000000
10 | 19 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.2617 | 0 | 5.9015 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.8523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8289.66 | 0 | 8289.66 | 137019 | -16508.8 | 34 | 39 | 137019 | -1016508.8
10 | 19 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8048 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.3933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.59 | 0 | 8291.59 | 136018 | -3993.89 | 33 | 38 | 136018 | -1003993.89
10 | 19 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 8.6189 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.2048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8293.34 | 0 | 8293.34 | 137256 | -10621 | 33 | 38 | 137256 | -1010621
10 | 19 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 8.5389 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 4.8 | 88.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9192.86 | 0 | 9192.86 | 137763 | -8897.75 | 34 | 39 | 137763 | -1008897.75
10 | 19 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 11.4746 | 0 | 5.9243 | 12.9754 | 0 | 0 | 0 | 4.8 | 129.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22080.2 | 0 | 22080.2 | 189763 | -11584.3 | 34 | 39 | 189763 | -1011584.3
10 | 19 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 21.8326 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65098.6 | 0 | 65098.6 | 328919 | -237538 | 33 | 38 | 328919 | -1237538
10 | 19 | 7 | 4 | 52.8024 | 0 | 168.222 | 0 | 25.6297 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79025.9 | 0 | 79025.9 | 399211 | -237962 | 33 | 38 | 399211 | -1237962
10 | 19 | 8 | 4 | 44.6444 | 0 | 173.795 | 0 | 27.1793 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109335 | 0 | 109335 | 420614 | -214555 | 33 | 38 | 420614 | -1214555
10 | 19 | 9 | 4 | 40.7177 | 0 | 172.186 | 0 | 29.8505 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 268.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128622 | 0 | 128622 | 446952 | -208908 | 34 | 40 | 446952 | -1208908
10 | 19 | 10 | 4 | 41.306 | 0 | 163.102 | 0 | 31.8965 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131374 | 0 | 131374 | 464330 | -194165 | 36 | 43 | 464330 | -1194165
10 | 19 | 11 | 4 | 40.7555 | 0 | 149.692 | 0 | 34.3811 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 250.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131374 | 0 | 131374 | 481746 | -171260 | 37 | 45 | 481746 | -1171260
10 | 19 | 12 | 4 | 39.8618 | 0 | 150.207 | 0 | 27.9387 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131374 | 0 | 131374 | 403170 | -149148 | 36 | 44 | 403170 | -1149148
10 | 19 | 13 | 4 | 42.0519 | 0 | 165.698 | 0 | 32.2259 | 0 | 7.262 | 19.0363 | 0 | 0 | 0 | 0 | 266.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131373 | 0 | 131373 | 463956 | -163303 | 35 | 43 | 463956 | -1163303
10 | 19 | 14 | 4 | 40.6827 | 0 | 172.702 | 0 | 35.5342 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129678 | 0 | 129678 | 499862 | -151929 | 36 | 44 | 499862 | -1151929
10 | 19 | 15 | 4 | 41.1292 | 0 | 173.986 | 0 | 33.6775 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117904 | 0 | 117904 | 477590 | -144499 | 35 | 43 | 477590 | -1144499
10 | 19 | 16 | 4 | 40.5945 | 0 | 169.782 | 0 | 33.2168 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 270.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96269.8 | 0 | 96269.8 | 476885 | -165497 | 35 | 42 | 476885 | -1165497
10 | 19 | 17 | 4 | 42.6529 | 0 | 152.497 | 0 | 27.2681 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 252.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72233.1 | 0 | 72233.1 | 411423 | -190350 | 33 | 40 | 411423 | -1190350
10 | 19 | 18 | 4 | 34.0591 | 0 | 93.4203 | 0 | 21.8492 | 0 | 10.2897 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44780.8 | 0 | 44780.8 | 322896 | -242281 | 34 | 39 | 322896 | -1242281
10 | 19 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.2524 | 0 | 5.4915 | 8.818 | 0 | 0 | 0 | 7.2 | 117.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32083.8 | 0 | 32083.8 | 187353 | 0 | 34 | 39 | 187353 | -1000000
10 | 19 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 12.9324 | 0 | 5.9254 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28494.7 | 0 | 28494.7 | 167993 | -11776 | 33 | 39 | 167993 | -1011776
10 | 19 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.6535 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17543.8 | 0 | 17543.8 | 154383 | 0 | 32 | 39 | 154383 | -1000000
10 | 19 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.9662 | 0 | 5.9069 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9510.06 | 0 | 9510.06 | 143194 | -19788 | 31 | 37 | 143194 | -1019788
10 | 19 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 6.9148 | 0 | 5.8987 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8295.35 | 0 | 8295.35 | 138361 | -7000.83 | 31 | 37 | 138361 | -1007000.83
10 | 19 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 9.8356 | 0 | 5.8977 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.5414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8297.84 | 0 | 8297.84 | 139403 | -14621.4 | 31 | 37 | 139403 | -1014621.4
10 | 20 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.1928 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.33 | 0 | 8300.33 | 135663 | -12405.6 | 30 | 36 | 135663 | -1012405.6
10 | 20 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.2921 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.61 | 0 | 8302.61 | 134794 | -14424.1 | 30 | 35 | 134794 | -1014424.1
10 | 20 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.3941 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304.77 | 0 | 8304.77 | 133891 | -15202.4 | 30 | 35 | 133891 | -1015202.4
10 | 20 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 10.5826 | 0 | 5.9011 | 15.4625 | 0 | 0 | 0 | 4.8 | 93.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9204.47 | 0 | 9204.47 | 147981 | -25619.9 | 29 | 34 | 147981 | -1025619.9
10 | 20 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.4132 | 0 | 5.9722 | 15.0234 | 0 | 0 | 0 | 4.8 | 134.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22092.2 | 0 | 22092.2 | 206367 | -20186 | 30 | 34 | 206367 | -1020186
10 | 20 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 22.3779 | 0 | 6.2898 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65111.2 | 0 | 65111.2 | 327634 | -389702 | 29 | 34 | 327634 | -1389702
10 | 20 | 7 | 5 | 52.6005 | 0 | 168.222 | 0 | 25.1166 | 0 | 6.2979 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79039.1 | 0 | 79039.1 | 389571 | -370927 | 30 | 34 | 389571 | -1370927
10 | 20 | 8 | 5 | 45.5648 | 0 | 173.795 | 0 | 25.9186 | 0 | 6.3108 | 19.0363 | 0 | 0 | 0 | 0 | 270.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109346 | 0 | 109346 | 407851 | -305348 | 30 | 35 | 407851 | -1305348
10 | 20 | 9 | 5 | 41.8757 | 0 | 172.186 | 0 | 26.1257 | 0 | 25.3203 | 19.0363 | 0 | 0 | 0 | 0 | 284.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128633 | 0 | 128633 | 409007 | -291055 | 30 | 36 | 409007 | -1291055
10 | 20 | 10 | 5 | 42.1499 | 0 | 163.102 | 0 | 28.4829 | 0 | 25.3335 | 19.0363 | 0 | 0 | 0 | 0 | 278.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131384 | 0 | 131384 | 431736 | -279654 | 33 | 40 | 431736 | -1279654
10 | 20 | 11 | 5 | 41.4162 | 0 | 149.692 | 0 | 30.0171 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 265.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131384 | 0 | 131384 | 438483 | -241731 | 36 | 43 | 438483 | -1241731
10 | 20 | 12 | 5 | 39.9029 | 0 | 150.207 | 0 | 28.2762 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 262.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131383 | 0 | 131383 | 409924 | -199414 | 37 | 45 | 409924 | -1199414
10 | 20 | 13 | 5 | 41.3064 | 0 | 165.698 | 0 | 32.9089 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131381 | 0 | 131381 | 451937 | -136803 | 38 | 49 | 451937 | -1136803
10 | 20 | 14 | 5 | 40.685 | 0 | 172.702 | 0 | 36.5224 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129685 | 0 | 129685 | 478047 | -93021.5 | 40 | 52 | 478047 | -1093021.5
10 | 20 | 15 | 5 | 40.6075 | 0 | 173.986 | 0 | 33.6773 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117910 | 0 | 117910 | 479153 | -63021.5 | 42 | 53 | 479153 | -1063021.5
10 | 20 | 16 | 5 | 40.3886 | 0 | 169.782 | 0 | 30.1157 | 0 | 6.332 | 19.0438 | 0 | 0 | 0 | 1.2 | 266.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96274.9 | 0 | 96274.9 | 478189 | -53093.5 | 43 | 54 | 478189 | -1053093.5
10 | 20 | 17 | 5 | 46.3118 | 0 | 152.497 | 0 | 26.6912 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 255.669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72237.2 | 0 | 72237.2 | 434025 | -62318.5 | 43 | 54 | 434025 | -1062318.5
10 | 20 | 18 | 5 | 34.11 | 0 | 93.4203 | 0 | 22.8602 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 182.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44783.8 | 0 | 44783.8 | 343065 | -102223 | 43 | 53 | 343065 | -1102223
10 | 20 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.3011 | 0 | 5.4922 | 8.818 | 0 | 0 | 0 | 7.2 | 117.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32086.2 | 0 | 32086.2 | 188096 | 0 | 43 | 52 | 188096 | -1000000
10 | 20 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.2991 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 7.2 | 103.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28496.9 | 0 | 28496.9 | 168415 | 0 | 43 | 52 | 168415 | -1000000
10 | 20 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.6841 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17545.6 | 0 | 17545.6 | 155057 | 0 | 43 | 52 | 155057 | -1000000
10 | 20 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 9.3865 | 0 | 5.8975 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9510.92 | 0 | 9510.92 | 143983 | -6383.37 | 43 | 51 | 143983 | -1006383.37
10 | 20 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 6.9437 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8295.42 | 0 | 8295.42 | 138991 | 0 | 42 | 49 | 138991 | -1000000
10 | 20 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.8587 | 0 | 5.899 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8297.09 | 0 | 8297.09 | 137184 | -1598.12 | 41 | 46 | 137184 | -1001598.12
10 | 21 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.8079 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8298.7 | 0 | 8298.7 | 136083 | 0 | 40 | 45 | 136083 | -1000000
10 | 21 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.2532 | 0 | 5.898 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.9069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.75 | 0 | 8300.75 | 135525 | -12529.3 | 43 | 48 | 135525 | -1012529.3
10 | 21 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7336 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.64 | 0 | 8302.64 | 134458 | 0 | 43 | 50 | 134458 | -1000000
10 | 21 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6986 | 0 | 5.9002 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304.31 | 0 | 8304.31 | 133698 | -2931.04 | 41 | 47 | 133698 | -1002931.04
10 | 21 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6632 | 0 | 5.4823 | 8.818 | 0 | 0 | 0 | 4.8 | 74.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8305.55 | 0 | 8305.55 | 132923 | 0 | 40 | 47 | 132923 | -1000000
10 | 21 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.3131 | 0 | 5.8978 | 12.8287 | 0 | 0 | 0 | 2.4 | 80.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.04 | 0 | 8307.04 | 132182 | -15002.6 | 39 | 46 | 132182 | -1015002.6
10 | 21 | 7 | 6 | 6.1593 | 0 | 42.7453 | 13.351 | 0 | 0 | 5.9147 | 18.8896 | 0 | 0 | 0 | 0.8 | 87.8599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.59 | 0 | 8308.59 | 144543 | -294709 | 37 | 44 | 144543 | -1294709
10 | 21 | 8 | 6 | 5.1479 | 0 | 42.7453 | 17.4182 | 0 | 0 | 6.0538 | 18.8896 | 0 | 0 | 0 | 0 | 90.2547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8310.01 | 0 | 8310.01 | 207685 | -327676 | 37 | 44 | 207685 | -1327676
10 | 21 | 9 | 6 | 5.4819 | 0 | 42.7453 | 15.8244 | 0 | 0 | 5.9976 | 18.8896 | 0 | 0 | 0 | 0 | 88.9388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.52 | 0 | 8312.52 | 196013 | -285070 | 38 | 45 | 196013 | -1285070
10 | 21 | 10 | 6 | 6.8582 | 0 | 42.7453 | 16.3552 | 0 | 0 | 6.0142 | 18.8896 | 0 | 0 | 0 | 0 | 90.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.53 | 0 | 8312.53 | 201938 | -294062 | 39 | 46 | 201938 | -1294062
10 | 21 | 11 | 6 | 6.0301 | 0 | 42.7453 | 15.6185 | 0 | 0 | 5.9869 | 18.8896 | 0 | 0 | 0 | 0 | 89.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8313.62 | 0 | 8313.62 | 198216 | -277696 | 39 | 46 | 198216 | -1277696
10 | 21 | 12 | 6 | 5.8804 | 0 | 42.7453 | 14.7037 | 0 | 0 | 5.9644 | 18.8896 | 0 | 0 | 0 | 0 | 88.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8314.37 | 0 | 8314.37 | 199002 | -265218 | 40 | 47 | 199002 | -1265218
10 | 21 | 13 | 6 | 6.0361 | 0 | 42.7453 | 14.7961 | 0 | 0 | 5.9643 | 18.8896 | 0 | 0 | 0 | 0 | 88.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8315.21 | 0 | 8315.21 | 198151 | -259256 | 40 | 48 | 198151 | -1259256
10 | 21 | 14 | 6 | 6.1119 | 0 | 42.7453 | 0 | 7.2765 | 0 | 6.5745 | 8.818 | 0 | 0 | 0 | 0 | 71.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8315.89 | 0 | 8315.89 | 127635 | 0 | 40 | 48 | 127635 | -1000000
10 | 21 | 15 | 6 | 6.4138 | 0 | 42.7453 | 0 | 8.9742 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 0 | 76.8588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316.72 | 0 | 8316.72 | 127273 | -8274.22 | 40 | 47 | 127273 | -1008274.22
10 | 21 | 16 | 6 | 6.9334 | 0 | 42.7453 | 0 | 6.9197 | 0 | 6.4782 | 8.818 | 0 | 0 | 0 | 1.2 | 73.0946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8317.05 | 0 | 8317.05 | 126891 | 0 | 39 | 46 | 126891 | -1000000
10 | 21 | 17 | 6 | 8.1286 | 0 | 42.7453 | 0 | 10.019 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.4185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.04 | 0 | 8318.04 | 126573 | -13928 | 39 | 46 | 126573 | -1013928
10 | 21 | 18 | 6 | 8.7888 | 0 | 42.7453 | 0 | 6.3559 | 0 | 5.4853 | 8.818 | 0 | 0 | 0 | 7.2 | 79.3933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8319.1 | 0 | 8319.1 | 126203 | 0 | 39 | 45 | 126203 | -1000000
10 | 21 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.4066 | 0 | 5.8974 | 12.8287 | 0 | 0 | 0 | 7.2 | 87.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8320.35 | 0 | 8320.35 | 125844 | -16516.3 | 39 | 45 | 125844 | -1016516.3
10 | 21 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3241 | 0 | 5.9038 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8321.8 | 0 | 8321.8 | 125508 | -5564.43 | 38 | 45 | 125508 | -1005564.43
10 | 21 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4224 | 0 | 5.9027 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8323.18 | 0 | 8323.18 | 127702 | -11015.8 | 38 | 44 | 127702 | -1011015.8
10 | 21 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.2941 | 0 | 5.9041 | 12.8287 | 0 | 0 | 0 | 6.4 | 82.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8324.71 | 0 | 8324.71 | 124810 | -9520.17 | 36 | 40 | 124810 | -1009520.17
10 | 21 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 8.1976 | 0 | 5.8983 | 12.8287 | 0 | 0 | 0 | 5.6 | 84.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8326.22 | 0 | 8326.22 | 124385 | -11801.7 | 35 | 38 | 124385 | -1011801.7
10 | 21 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 9.3226 | 0 | 5.8967 | 15.3158 | 0 | 0 | 0 | 4.8 | 83.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3260.52 | 0 | 3260.52 | 133982 | -22515.2 | 33 | 35 | 133982 | -1022515.2
10 | 22 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.5684 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3262.29 | 0 | 3262.29 | 128520 | -16325.9 | 33 | 35 | 128520 | -1016325.9
10 | 22 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1811 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3264.77 | 0 | 3264.77 | 149685 | -26472.3 | 31 | 33 | 149685 | -1026472.3
10 | 22 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.4982 | 0 | 5.9052 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.4178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3267.02 | 0 | 3267.02 | 147157 | -41100.5 | 31 | 32 | 147157 | -1041100.5
10 | 22 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.3602 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.2785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.86 | 0 | 3268.86 | 145132 | -48350.5 | 30 | 30 | 145132 | -1048350.5
10 | 22 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.7492 | 0 | 5.9056 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.6693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3271.7 | 0 | 3271.7 | 143608 | -58136.7 | 30 | 31 | 143608 | -1058136.7
10 | 22 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.6282 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.1473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3274.1 | 0 | 3274.1 | 142646 | -68950.5 | 30 | 31 | 142646 | -1068950.5
10 | 22 | 7 | 7 | 5.0074 | 0 | 42.7453 | 0 | 11.5658 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 0.8 | 83.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3276.62 | 0 | 3276.62 | 141749 | -72081.3 | 29 | 30 | 141749 | -1072081.3
10 | 22 | 8 | 7 | 4.6787 | 0 | 42.7453 | 0 | 12.1512 | 0 | 5.9094 | 17.3638 | 0 | 0 | 0 | 0 | 82.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3279.02 | 0 | 3279.02 | 147284 | -64820.2 | 32 | 33 | 147284 | -1064820.2
10 | 22 | 9 | 7 | 5.2597 | 0 | 42.7453 | 0 | 10.438 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 0 | 81.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3281.24 | 0 | 3281.24 | 141423 | -48834.2 | 34 | 36 | 141423 | -1048834.2
10 | 22 | 10 | 7 | 4.844 | 0 | 42.7453 | 0 | 10.1742 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 81.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3283.26 | 0 | 3283.26 | 141416 | -42796.7 | 35 | 38 | 141416 | -1042796.7
10 | 22 | 11 | 7 | 4.7378 | 0 | 42.7453 | 0 | 10.8686 | 0 | 5.9011 | 17.3638 | 0 | 0 | 0 | 0 | 81.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3284.56 | 0 | 3284.56 | 142621 | -41379.5 | 37 | 40 | 142621 | -1041379.5
10 | 22 | 12 | 7 | 4.5951 | 0 | 42.7453 | 0 | 9.545 | 0 | 5.8967 | 15.3158 | 0 | 0 | 0 | 0 | 78.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3285.95 | 0 | 3285.95 | 128166 | -29966.4 | 38 | 42 | 128166 | -1029966.4
10 | 22 | 13 | 7 | 4.6266 | 0 | 42.7453 | 0 | 10.2892 | 0 | 5.8992 | 17.3638 | 0 | 0 | 0 | 0 | 80.9241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3287.47 | 0 | 3287.47 | 143192 | -30134.3 | 38 | 44 | 143192 | -1030134.3
10 | 22 | 14 | 7 | 4.6353 | 0 | 42.7453 | 0 | 9.3739 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 0 | 77.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3288.8 | 0 | 3288.8 | 134202 | -17535.3 | 38 | 44 | 134202 | -1017535.3
10 | 22 | 15 | 7 | 4.6883 | 0 | 42.7453 | 0 | 8.836 | 0 | 5.897 | 15.3158 | 0 | 0 | 0 | 0 | 77.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3290.02 | 0 | 3290.02 | 127757 | -24735.4 | 37 | 43 | 127757 | -1024735.4
10 | 22 | 16 | 7 | 5.1695 | 0 | 42.7453 | 0 | 9.9902 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 1.2 | 82.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3290.9 | 0 | 3290.9 | 144913 | -27038.9 | 37 | 44 | 144913 | -1027038.9
10 | 22 | 17 | 7 | 6.103 | 0 | 42.7453 | 0 | 8.0166 | 0 | 5.8994 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.3929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3291.98 | 0 | 3291.98 | 120207 | -13061 | 37 | 44 | 120207 | -1013061
10 | 22 | 18 | 7 | 6.6582 | 0 | 42.7453 | 0 | 10.0898 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3293.24 | 0 | 3293.24 | 140996 | -35199.2 | 37 | 42 | 140996 | -1035199.2
10 | 22 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.8777 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.7478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3294.21 | 0 | 3294.21 | 139313 | -40507.3 | 36 | 41 | 139313 | -1040507.3
10 | 22 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2053 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3295.8 | 0 | 3295.8 | 138767 | -45990.6 | 36 | 41 | 138767 | -1045990.6
10 | 22 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4495 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3297.35 | 0 | 3297.35 | 139856 | -48655.7 | 36 | 41 | 139856 | -1048655.7
10 | 22 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.2258 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3298.88 | 0 | 3298.88 | 137560 | -44111.3 | 36 | 40 | 137560 | -1044111.3
10 | 22 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.9272 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3300.32 | 0 | 3300.32 | 142753 | -57417.9 | 35 | 39 | 142753 | -1057417.9
10 | 22 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 9.1562 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.3962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8368.69 | 0 | 8368.69 | 137020 | -46894.2 | 36 | 40 | 137020 | -1046894.2
10 | 23 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.9229 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.13 | 0 | 8370.13 | 139231 | -62383.7 | 36 | 39 | 139231 | -1062383.7
10 | 23 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1513 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8370.29 | 0 | 8370.29 | 136635 | -60213.9 | 36 | 39 | 136635 | -1060213.9
10 | 23 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 11.2374 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8371.45 | 0 | 8371.45 | 141243 | -73251.5 | 32 | 36 | 141243 | -1073251.5
10 | 23 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 9.6928 | 0 | 5.8974 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9270.09 | 0 | 9270.09 | 139099 | -69861.3 | 32 | 34 | 139099 | -1069861.3
10 | 23 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 16.3643 | 0 | 6.005 | 17.5105 | 0 | 0 | 0 | 4.8 | 138.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22156.8 | 0 | 22156.8 | 204086 | -70081.9 | 30 | 32 | 204086 | -1070081.9
10 | 23 | 6 | 1 | 49.0171 | 0 | 140.608 | 32.7613 | 0 | 0 | 6.2353 | 19.0363 | 0 | 0 | 0 | 2.4 | 250.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65174.1 | 0 | 65174.1 | 314893 | -633360 | 29 | 30 | 314893 | -1633360
10 | 23 | 7 | 1 | 51.3494 | 0 | 168.222 | 31.7599 | 0 | 0 | 6.2493 | 19.0363 | 0 | 0 | 0 | 0.8 | 277.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79101.3 | 0 | 79101.3 | 377441 | -603431 | 29 | 30 | 377441 | -1603431
10 | 23 | 8 | 1 | 41.2656 | 0 | 173.795 | 0 | 25.1679 | 0 | 6.2788 | 19.0363 | 0 | 0 | 0 | 0 | 265.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109394 | 0 | 109394 | 396671 | -417203 | 32 | 34 | 396671 | -1417203
10 | 23 | 9 | 1 | 41.2302 | 0 | 172.186 | 0 | 28.0144 | 0 | 25.3194 | 19.0363 | 0 | 0 | 0 | 0 | 285.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128678 | 0 | 128678 | 424443 | -331230 | 35 | 39 | 424443 | -1331230
10 | 23 | 10 | 1 | 41.2373 | 0 | 163.102 | 0 | 30.6915 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 279.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131427 | 0 | 131427 | 448068 | -300186 | 37 | 43 | 448068 | -1300186
10 | 23 | 11 | 1 | 40.7699 | 0 | 149.692 | 0 | 30.4126 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131424 | 0 | 131424 | 437689 | -275278 | 37 | 44 | 437689 | -1275278
10 | 23 | 12 | 1 | 39.8314 | 0 | 150.207 | 0 | 28.1266 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131420 | 0 | 131420 | 393938 | -204102 | 39 | 48 | 393938 | -1204102
10 | 23 | 13 | 1 | 41.3108 | 0 | 165.698 | 0 | 32.8861 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131417 | 0 | 131417 | 462354 | -208250 | 37 | 46 | 462354 | -1208250
10 | 23 | 14 | 1 | 40.7062 | 0 | 172.702 | 0 | 35.2015 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129720 | 0 | 129720 | 479222 | -167733 | 39 | 48 | 479222 | -1167733
10 | 23 | 15 | 1 | 40.6745 | 0 | 173.986 | 0 | 34.2205 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117943 | 0 | 117943 | 464590 | -142469 | 39 | 48 | 464590 | -1142469
10 | 23 | 16 | 1 | 41.0091 | 0 | 169.782 | 0 | 33.6584 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 1.2 | 271.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96306.2 | 0 | 96306.2 | 450348 | -129024 | 41 | 50 | 450348 | -1129024
10 | 23 | 17 | 1 | 38.2259 | 0 | 152.497 | 0 | 29.5642 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 4.8 | 250.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72266.8 | 0 | 72266.8 | 416838 | -179978 | 40 | 47 | 416838 | -1179978
10 | 23 | 18 | 1 | 34.067 | 0 | 93.4203 | 0 | 24.259 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44811.4 | 0 | 44811.4 | 342023 | -266147 | 38 | 44 | 342023 | -1266147
10 | 23 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 8.9653 | 0 | 5.4874 | 8.818 | 0 | 0 | 0 | 7.2 | 117.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32112.5 | 0 | 32112.5 | 180637 | 0 | 36 | 41 | 180637 | -1000000
10 | 23 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 11.3945 | 0 | 5.9097 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28522.7 | 0 | 28522.7 | 161562 | -8841 | 36 | 39 | 161562 | -1008841
10 | 23 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.3779 | 0 | 5.4787 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17576.2 | 0 | 17576.2 | 148357 | 0 | 36 | 39 | 148357 | -1000000
10 | 23 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.5096 | 0 | 5.9028 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.3183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9543.19 | 0 | 9543.19 | 137448 | -19638 | 36 | 39 | 137448 | -1019638
10 | 23 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.6593 | 0 | 5.9005 | 12.9754 | 0 | 0 | 0 | 5.6 | 83.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8329.37 | 0 | 8329.37 | 132772 | -9407.45 | 35 | 38 | 132772 | -1009407.45
10 | 23 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 9.7325 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8332.06 | 0 | 8332.06 | 132842 | -15728.6 | 35 | 37 | 132842 | -1015728.6
10 | 24 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.187 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8334.59 | 0 | 8334.59 | 130488 | -14551 | 34 | 37 | 130488 | -1014551
10 | 24 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.3447 | 0 | 5.8986 | 15.3158 | 0 | 0 | 0 | 4.8 | 89.1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8336.76 | 0 | 8336.76 | 138658 | -26374.1 | 34 | 37 | 138658 | -1026374.1
10 | 24 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.7903 | 0 | 5.9014 | 14.8767 | 0 | 0 | 0 | 4.8 | 89.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8338.86 | 0 | 8338.86 | 145658 | -20879.1 | 34 | 37 | 145658 | -1020879.1
10 | 24 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.6661 | 0 | 5.9083 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.5294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9238.81 | 0 | 9238.81 | 153693 | -34012.1 | 33 | 36 | 153693 | -1034012.1
10 | 24 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.3114 | 0 | 5.9593 | 15.0234 | 0 | 0 | 0 | 4.8 | 134.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22126.4 | 0 | 22126.4 | 193415 | -24185.8 | 33 | 35 | 193415 | -1024185.8
10 | 24 | 6 | 2 | 49.0171 | 0 | 140.608 | 0 | 22.6464 | 0 | 6.2737 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65145 | 0 | 65145 | 323504 | -453881 | 33 | 36 | 323504 | -1453881
10 | 24 | 7 | 2 | 51.6931 | 0 | 168.222 | 0 | 25.3696 | 0 | 6.283 | 19.0363 | 0 | 0 | 0 | 0.8 | 271.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79072.4 | 0 | 79072.4 | 385829 | -427998 | 34 | 37 | 385829 | -1427998
10 | 24 | 8 | 2 | 41.2079 | 0 | 173.795 | 0 | 26.7261 | 0 | 25.3151 | 19.0363 | 0 | 0 | 0 | 0 | 286.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109373 | 0 | 109373 | 414964 | -319873 | 35 | 39 | 414964 | -1319873
10 | 24 | 9 | 2 | 41.26 | 0 | 172.186 | 0 | 31.3817 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 289.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128658 | 0 | 128658 | 459762 | -262732 | 38 | 44 | 459762 | -1262732
10 | 24 | 10 | 2 | 41.3741 | 0 | 163.102 | 0 | 31.5737 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131408 | 0 | 131408 | 440955 | -203011 | 41 | 48 | 440955 | -1203011
10 | 24 | 11 | 2 | 40.7861 | 0 | 149.692 | 0 | 32.9799 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131405 | 0 | 131405 | 426244 | -134958 | 44 | 54 | 426244 | -1134958
10 | 24 | 12 | 2 | 39.8383 | 0 | 150.207 | 0 | 33.8611 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131403 | 0 | 131403 | 428235 | -82632.3 | 46 | 58 | 428235 | -1082632.3
10 | 24 | 13 | 2 | 41.3272 | 0 | 165.698 | 0 | 33.8223 | 0 | 6.332 | 19.3521 | 0 | 0 | 0 | 0 | 266.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131399 | 0 | 131399 | 507089 | -40026.3 | 49 | 61 | 507089 | -1040026.3
10 | 24 | 14 | 2 | 40.7179 | 0 | 172.702 | 0 | 41.1844 | 0 | 6.332 | 19.6067 | 0 | 0 | 0 | 0 | 280.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129702 | 0 | 129702 | 605332 | -23814 | 51 | 65 | 605332 | -1023814
10 | 24 | 15 | 2 | 40.7263 | 0 | 173.986 | 0 | 41.0734 | 0 | 6.332 | 19.742 | 0 | 0 | 0 | 0 | 281.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117926 | 0 | 117926 | 665416 | -21462.5 | 53 | 66 | 665416 | -1021462.5
10 | 24 | 16 | 2 | 41.0016 | 0 | 169.782 | 0 | 38.1059 | 0 | 6.332 | 19.9209 | 0 | 0 | 0 | 1.2 | 276.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96290 | 0 | 96290 | 651226 | -15976.5 | 54 | 67 | 651226 | -1015976.5
10 | 24 | 17 | 2 | 38.7543 | 0 | 152.497 | 0 | 26.1323 | 0 | 6.332 | 19.5346 | 0 | 0 | 0 | 4.8 | 248.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72251.6 | 0 | 72251.6 | 501694 | -11831.5 | 52 | 63 | 501694 | -1011831.5
10 | 24 | 18 | 2 | 34.081 | 0 | 93.4203 | 0 | 18.3776 | 0 | 6.2272 | 19.0363 | 0 | 0 | 0 | 7.2 | 178.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44797.3 | 0 | 44797.3 | 325320 | -18690.2 | 50 | 58 | 325320 | -1018690.2
10 | 24 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.2386 | 0 | 5.4913 | 8.818 | 0 | 0 | 0 | 7.2 | 117.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32098.8 | 0 | 32098.8 | 187005 | 0 | 50 | 57 | 187005 | -1000000
10 | 24 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.2443 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 7.2 | 103.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28508.9 | 0 | 28508.9 | 167212 | 0 | 49 | 55 | 167212 | -1000000
10 | 24 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.6304 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17558.5 | 0 | 17558.5 | 153883 | 0 | 49 | 56 | 153883 | -1000000
10 | 24 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.1306 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9523.7 | 0 | 9523.7 | 142983 | 0 | 49 | 55 | 142983 | -1000000
10 | 24 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9007 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.11 | 0 | 8308.11 | 138050 | 0 | 48 | 53 | 138050 | -1000000
10 | 24 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 6.8319 | 0 | 5.4811 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8309.48 | 0 | 8309.48 | 136603 | 0 | 49 | 55 | 136603 | -1000000
10 | 25 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7977 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8310.62 | 0 | 8310.62 | 135866 | 0 | 50 | 55 | 135866 | -1000000
10 | 25 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7507 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8311.42 | 0 | 8311.42 | 134832 | 0 | 49 | 55 | 134832 | -1000000
10 | 25 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 8.6159 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8312.32 | 0 | 8312.32 | 134536 | -5713.98 | 50 | 59 | 134536 | -1005713.98
10 | 25 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 6.8686 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 82.6119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9210.62 | 0 | 9210.62 | 137480 | 0 | 50 | 60 | 137480 | -1000000
10 | 25 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.9882 | 0 | 5.4877 | 8.818 | 0 | 0 | 0 | 4.8 | 122.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22096.8 | 0 | 22096.8 | 184615 | 0 | 51 | 60 | 184615 | -1000000
10 | 25 | 6 | 3 | 49.0171 | 0 | 140.608 | 0 | 28.362 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 245.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65113.9 | 0 | 65113.9 | 354339 | -49910.1 | 49 | 59 | 354339 | -1049910.1
10 | 25 | 7 | 3 | 51.7649 | 0 | 168.222 | 0 | 21.223 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 267.379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79039.7 | 0 | 79039.7 | 452295 | -31644.3 | 50 | 60 | 452295 | -1031644.3
10 | 25 | 8 | 3 | 41.3033 | 0 | 173.795 | 0 | 31.887 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109345 | 0 | 109345 | 498722 | -21132.8 | 50 | 61 | 498722 | -1021132.8
10 | 25 | 9 | 3 | 41.4191 | 0 | 172.186 | 0 | 33.0022 | 0 | 6.332 | 19.3304 | 0 | 0 | 0 | 0 | 272.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128632 | 0 | 128632 | 545854 | -15827.3 | 51 | 62 | 545854 | -1015827.3
10 | 25 | 10 | 3 | 41.3964 | 0 | 163.102 | 0 | 36.6056 | 0 | 6.332 | 19.7679 | 0 | 0 | 0 | 0 | 267.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131382 | 0 | 131382 | 619927 | -29666.4 | 52 | 63 | 619927 | -1029666.4
10 | 25 | 11 | 3 | 40.79 | 0 | 149.692 | 0 | 38.9455 | 0 | 7.5898 | 19.8881 | 0 | 0 | 0 | 0 | 256.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131381 | 0 | 131381 | 669549 | -31532.5 | 54 | 66 | 669549 | -1031532.5
10 | 25 | 12 | 3 | 39.84 | 0 | 150.207 | 0 | 49.2992 | 0 | 25.335 | 19.6425 | 0 | 0 | 0 | 0 | 284.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131380 | 0 | 131380 | 792335 | -51329.9 | 56 | 70 | 792335 | -1051329.9
10 | 25 | 13 | 3 | 41.3292 | 0 | 165.698 | 0 | 53.238 | 0 | 25.335 | 20.3681 | 0 | 0 | 0 | 0 | 305.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131380 | 0 | 131380 | 882070 | -34502.4 | 56 | 73 | 882070 | -1034502.4
10 | 25 | 14 | 3 | 40.7205 | 0 | 172.702 | 0 | 52.8687 | 0 | 25.335 | 20.7637 | 0 | 0 | 0 | 0 | 312.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129686 | 0 | 129686 | 913177 | -25706.1 | 56 | 73 | 913177 | -1025706.1
10 | 25 | 15 | 3 | 40.7513 | 0 | 173.986 | 0 | 53.7249 | 0 | 25.335 | 20.6733 | 0 | 0 | 0 | 0 | 314.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117913 | 0 | 117913 | 938899 | -30127.6 | 56 | 72 | 938899 | -1030127.6
10 | 25 | 16 | 3 | 41.0568 | 0 | 169.782 | 0 | 47.0484 | 0 | 25.335 | 21.2418 | 0 | 0 | 0 | 1.2 | 305.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96278.2 | 0 | 96278.2 | 861736 | -12746.6 | 56 | 71 | 861736 | -1012746.6
10 | 25 | 17 | 3 | 39.1001 | 0 | 152.497 | 0 | 35.0674 | 0 | 25.335 | 20.8934 | 0 | 0 | 0 | 4.8 | 277.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72240.5 | 0 | 72240.5 | 684098 | -6048.21 | 55 | 68 | 684098 | -1006048.21
10 | 25 | 18 | 3 | 34.0955 | 0 | 93.4203 | 0 | 20.4661 | 0 | 6.332 | 19.2794 | 0 | 0 | 0 | 7.2 | 180.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44786.5 | 0 | 44786.5 | 434966 | -5798.87 | 54 | 65 | 434966 | -1005798.87
10 | 25 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 8.8045 | 0 | 5.4867 | 8.818 | 0 | 0 | 0 | 7.2 | 117.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32087.1 | 0 | 32087.1 | 190545 | 0 | 53 | 62 | 190545 | -1000000
10 | 25 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 7.8743 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 7.2 | 102.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28497.5 | 0 | 28497.5 | 170335 | 0 | 51 | 59 | 170335 | -1000000
10 | 25 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.7776 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 91.9946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17543.5 | 0 | 17543.5 | 157105 | 0 | 51 | 58 | 157105 | -1000000
10 | 25 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 7.2689 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9507.62 | 0 | 9507.62 | 146006 | 0 | 52 | 60 | 146006 | -1000000
10 | 25 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 7.0309 | 0 | 5.4799 | 8.818 | 0 | 0 | 0 | 5.6 | 79.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.04 | 0 | 8291.04 | 140897 | 0 | 51 | 60 | 140897 | -1000000
10 | 25 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 6.964 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.9 | 0 | 8291.9 | 139494 | 0 | 51 | 59 | 139494 | -1000000
10 | 26 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.9131 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 4.8 | 79.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8292.51 | 0 | 8292.51 | 138385 | 0 | 50 | 58 | 138385 | -1000000
10 | 26 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8805 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8293.01 | 0 | 8293.01 | 137679 | 0 | 50 | 56 | 137679 | -1000000
10 | 26 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 6.8338 | 0 | 5.481 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8293.44 | 0 | 8293.44 | 136652 | 0 | 49 | 55 | 136652 | -1000000
10 | 26 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 6.9672 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 82.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9191.55 | 0 | 9191.55 | 139638 | 0 | 48 | 53 | 139638 | -1000000
10 | 26 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 9.0561 | 0 | 5.4886 | 8.818 | 0 | 0 | 0 | 4.8 | 122.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22077.7 | 0 | 22077.7 | 186088 | 0 | 47 | 51 | 186088 | -1000000
10 | 26 | 6 | 4 | 49.0171 | 0 | 140.608 | 0 | 24.6835 | 0 | 6.332 | 19.1077 | 0 | 0 | 0 | 2.4 | 242.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65094.9 | 0 | 65094.9 | 336951 | -41553.1 | 45 | 48 | 336951 | -1041553.1
10 | 26 | 7 | 4 | 52.1582 | 0 | 168.222 | 0 | 26.2246 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79021.2 | 0 | 79021.2 | 437985 | -71525 | 45 | 48 | 437985 | -1071525
10 | 26 | 8 | 4 | 44.1001 | 0 | 173.795 | 0 | 33.044 | 0 | 6.332 | 19.0518 | 0 | 0 | 0 | 0 | 276.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109333 | 0 | 109333 | 487202 | -86852.9 | 46 | 50 | 487202 | -1086852.9
10 | 26 | 9 | 4 | 40.7926 | 0 | 172.186 | 0 | 32.8097 | 0 | 6.332 | 19.0647 | 0 | 0 | 0 | 0 | 271.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128621 | 0 | 128621 | 502086 | -63381.5 | 48 | 53 | 502086 | -1063381.5
10 | 26 | 10 | 4 | 41.2365 | 0 | 163.102 | 0 | 31.0294 | 0 | 6.332 | 19.6883 | 0 | 0 | 0 | 0 | 261.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131372 | 0 | 131372 | 518849 | -33510.7 | 50 | 56 | 518849 | -1033510.7
10 | 26 | 11 | 4 | 40.7821 | 0 | 149.692 | 0 | 33.2387 | 0 | 18.2031 | 20.1152 | 0 | 0 | 0 | 0 | 262.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131372 | 0 | 131372 | 588991 | -23585.9 | 53 | 61 | 588991 | -1023585.9
10 | 26 | 12 | 4 | 39.8156 | 0 | 150.207 | 0 | 40.9428 | 0 | 25.335 | 20.0475 | 0 | 0 | 0 | 0 | 276.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131372 | 0 | 131372 | 692153 | -34252.1 | 55 | 66 | 692153 | -1034252.1
10 | 26 | 13 | 4 | 41.2967 | 0 | 165.698 | 0 | 41.0482 | 0 | 25.335 | 21.1742 | 0 | 0 | 0 | 0 | 294.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131372 | 0 | 131372 | 726298 | -8756.02 | 55 | 68 | 726298 | -1008756.02
10 | 26 | 14 | 4 | 40.7039 | 0 | 172.702 | 0 | 47.2828 | 0 | 25.335 | 21.4048 | 0 | 0 | 0 | 0 | 307.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129677 | 0 | 129677 | 846703 | -8493.74 | 57 | 68 | 846703 | -1008493.74
10 | 26 | 15 | 4 | 40.6102 | 0 | 173.986 | 0 | 52.9595 | 0 | 25.335 | 21.2421 | 0 | 0 | 0 | 0 | 314.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117904 | 0 | 117904 | 931433 | -9030.03 | 58 | 70 | 931433 | -1009030.03
10 | 26 | 16 | 4 | 41.6397 | 0 | 169.782 | 0 | 41.1307 | 0 | 25.335 | 21.2865 | 0 | 0 | 0 | 1.2 | 300.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96269.6 | 0 | 96269.6 | 774557 | -7459.06 | 56 | 68 | 774557 | -1007459.06
10 | 26 | 17 | 4 | 43.3342 | 0 | 152.497 | 0 | 32.0389 | 0 | 25.335 | 20.8019 | 0 | 0 | 0 | 4.8 | 278.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72232.4 | 0 | 72232.4 | 635085 | -6503.86 | 54 | 65 | 635085 | -1006503.86
10 | 26 | 18 | 4 | 34.11 | 0 | 93.4203 | 0 | 18.8007 | 0 | 6.332 | 19.2886 | 0 | 0 | 0 | 7.2 | 179.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44777.9 | 0 | 44777.9 | 407062 | -6297.94 | 53 | 62 | 407062 | -1006297.94
10 | 26 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 8.9626 | 0 | 5.4874 | 8.818 | 0 | 0 | 0 | 7.2 | 117.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32080.3 | 0 | 32080.3 | 190895 | 0 | 51 | 58 | 190895 | -1000000
10 | 26 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.4244 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 7.2 | 103.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28491 | 0 | 28491 | 171156 | 0 | 51 | 56 | 171156 | -1000000
10 | 26 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 7.7893 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17536.2 | 0 | 17536.2 | 157353 | 0 | 49 | 54 | 157353 | -1000000
10 | 26 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.285 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 6.4 | 83.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9500.18 | 0 | 9500.18 | 146360 | 0 | 49 | 54 | 146360 | -1000000
10 | 26 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 7.0572 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8283.28 | 0 | 8283.28 | 141477 | 0 | 49 | 53 | 141477 | -1000000
10 | 26 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 6.9768 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8284.44 | 0 | 8284.44 | 139769 | 0 | 49 | 53 | 139769 | -1000000
10 | 27 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.9317 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 4.8 | 79.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.33 | 0 | 8285.33 | 138794 | 0 | 49 | 52 | 138794 | -1000000
10 | 27 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8887 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8286.24 | 0 | 8286.24 | 137854 | 0 | 49 | 51 | 137854 | -1000000
10 | 27 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8481 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 4.8 | 79.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8287.05 | 0 | 8287.05 | 136968 | 0 | 49 | 51 | 136968 | -1000000
10 | 27 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 6.9764 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 82.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9185.5 | 0 | 9185.5 | 139838 | 0 | 49 | 52 | 139838 | -1000000
10 | 27 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 12.1097 | 0 | 5.9326 | 12.9754 | 0 | 0 | 0 | 4.8 | 130.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22071.9 | 0 | 22071.9 | 193513 | -5238.51 | 49 | 52 | 193513 | -1005238.51
10 | 27 | 6 | 5 | 49.0171 | 0 | 140.608 | 0 | 21.8569 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 239.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65089.3 | 0 | 65089.3 | 353295 | -27652.1 | 48 | 52 | 353295 | -1027652.1
10 | 27 | 7 | 5 | 52.5931 | 0 | 168.222 | 0 | 31.4019 | 0 | 6.332 | 19.0586 | 0 | 0 | 0 | 0.8 | 278.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79015.7 | 0 | 79015.7 | 468244 | -79226.5 | 48 | 51 | 468244 | -1079226.5
10 | 27 | 8 | 5 | 48.5773 | 0 | 173.795 | 0 | 28.4398 | 0 | 6.332 | 19.0852 | 0 | 0 | 0 | 0 | 276.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109329 | 0 | 109329 | 499156 | -69356.1 | 48 | 52 | 499156 | -1069356.1
10 | 27 | 9 | 5 | 42.9266 | 0 | 172.186 | 0 | 31.1534 | 0 | 6.332 | 19.1054 | 0 | 0 | 0 | 0 | 271.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128617 | 0 | 128617 | 512887 | -52858.8 | 50 | 54 | 512887 | -1052858.8
10 | 27 | 10 | 5 | 43.2797 | 0 | 163.102 | 0 | 28.9796 | 0 | 6.332 | 19.2213 | 0 | 0 | 0 | 0 | 260.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 507989 | -30346.5 | 52 | 56 | 507989 | -1030346.5
10 | 27 | 11 | 5 | 41.6423 | 0 | 149.692 | 0 | 26.2971 | 0 | 25.335 | 19.129 | 0 | 0 | 0 | 0 | 262.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 482656 | -26863.6 | 52 | 57 | 482656 | -1026863.6
10 | 27 | 12 | 5 | 39.8109 | 0 | 150.207 | 0 | 28.4237 | 0 | 25.335 | 19.6689 | 0 | 0 | 0 | 0 | 263.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 525226 | -12289.3 | 54 | 61 | 525226 | -1012289.3
10 | 27 | 13 | 5 | 41.2973 | 0 | 165.698 | 0 | 37.5114 | 0 | 25.335 | 20.939 | 0 | 0 | 0 | 0 | 290.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131368 | 0 | 131368 | 690528 | -10029.9 | 56 | 62 | 690528 | -1010029.9
10 | 27 | 14 | 5 | 40.7045 | 0 | 172.702 | 0 | 40.937 | 0 | 25.335 | 20.5418 | 0 | 0 | 0 | 0 | 300.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129674 | 0 | 129674 | 736051 | -9373.63 | 57 | 64 | 736051 | -1009373.63
10 | 27 | 15 | 5 | 40.5938 | 0 | 173.986 | 0 | 42.7013 | 0 | 25.335 | 21.0668 | 0 | 0 | 0 | 0 | 303.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117900 | 0 | 117900 | 774837 | -11015.5 | 56 | 65 | 774837 | -1011015.5
10 | 27 | 16 | 5 | 40.5888 | 0 | 169.782 | 0 | 39.1991 | 0 | 25.335 | 20.6606 | 0 | 0 | 0 | 1.2 | 296.765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96265.2 | 0 | 96265.2 | 748158 | -10966.2 | 56 | 64 | 748158 | -1010966.2
10 | 27 | 17 | 5 | 40.6215 | 0 | 152.497 | 0 | 31.7914 | 0 | 25.335 | 20.1795 | 0 | 0 | 0 | 4.8 | 275.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72228 | 0 | 72228 | 626917 | -10291.1 | 55 | 62 | 626917 | -1010291.1
10 | 27 | 18 | 5 | 34.11 | 0 | 93.4203 | 0 | 17.5113 | 0 | 6.332 | 19.1616 | 0 | 0 | 0 | 7.2 | 177.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44774.9 | 0 | 44774.9 | 372521 | -11401.7 | 53 | 59 | 372521 | -1011401.7
10 | 27 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.4528 | 0 | 5.4947 | 8.818 | 0 | 0 | 0 | 7.2 | 117.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32077.6 | 0 | 32077.6 | 190974 | 0 | 53 | 58 | 190974 | -1000000
10 | 27 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.4172 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 7.2 | 103.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28488.6 | 0 | 28488.6 | 170994 | 0 | 52 | 56 | 170994 | -1000000
10 | 27 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.8004 | 0 | 5.4788 | 8.818 | 0 | 0 | 0 | 7.2 | 92.0175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17533.7 | 0 | 17533.7 | 157602 | 0 | 52 | 55 | 157602 | -1000000
10 | 27 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 7.2825 | 0 | 5.479 | 8.818 | 0 | 0 | 0 | 6.4 | 83.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9498.17 | 0 | 9498.17 | 146302 | 0 | 51 | 54 | 146302 | -1000000
10 | 27 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 7.0548 | 0 | 5.4798 | 8.818 | 0 | 0 | 0 | 5.6 | 79.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8281.66 | 0 | 8281.66 | 141425 | 0 | 51 | 54 | 141425 | -1000000
10 | 27 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 6.9635 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8282.79 | 0 | 8282.79 | 139475 | 0 | 50 | 52 | 139475 | -1000000
10 | 28 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.9123 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 4.8 | 75.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8283.82 | 0 | 8283.82 | 138368 | 0 | 49 | 51 | 138368 | -1000000
10 | 28 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.871 | 0 | 5.4808 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8285.45 | 0 | 8285.45 | 137467 | 0 | 48 | 49 | 137467 | -1000000
10 | 28 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.077 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.7294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8286.74 | 0 | 8286.74 | 136461 | -6573.09 | 46 | 47 | 136461 | -1006573.09
10 | 28 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7776 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 4.8 | 75.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.12 | 0 | 8288.12 | 135422 | 0 | 43 | 43 | 135422 | -1000000
10 | 28 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.7568 | 0 | 5.4816 | 8.818 | 0 | 0 | 0 | 4.8 | 74.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8289.55 | 0 | 8289.55 | 134976 | 0 | 45 | 45 | 134976 | -1000000
10 | 28 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.7604 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 2.4 | 80.0131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.07 | 0 | 8291.07 | 133908 | -11452.9 | 43 | 44 | 133908 | -1011452.9
10 | 28 | 7 | 6 | 6.3158 | 0 | 42.7453 | 0 | 13.3109 | 0 | 5.9409 | 18.8896 | 0 | 0 | 0 | 0.8 | 88.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8292.29 | 0 | 8292.29 | 187050 | -148438 | 40 | 42 | 187050 | -1148438
10 | 28 | 8 | 6 | 5.4167 | 0 | 42.7453 | 0 | 15.3625 | 0 | 5.9944 | 18.8896 | 0 | 0 | 0 | 0 | 88.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8293.9 | 0 | 8293.9 | 213140 | -247916 | 40 | 45 | 213140 | -1247916
10 | 28 | 9 | 6 | 5.507 | 0 | 42.7453 | 0 | 15.2895 | 0 | 12.5334 | 18.8896 | 0 | 0 | 0 | 0 | 94.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8298.7 | 0 | 8298.7 | 208398 | -219336 | 40 | 46 | 208398 | -1219336
10 | 28 | 10 | 6 | 5.477 | 0 | 42.7453 | 0 | 15.4827 | 0 | 12.6258 | 18.8896 | 0 | 0 | 0 | 0 | 95.2204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8299.92 | 0 | 8299.92 | 207321 | -193864 | 42 | 48 | 207321 | -1193864
10 | 28 | 11 | 6 | 5.476 | 0 | 42.7453 | 0 | 16.5081 | 0 | 13.6402 | 18.8896 | 0 | 0 | 0 | 0 | 97.2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8301.56 | 0 | 8301.56 | 212792 | -160361 | 43 | 51 | 212792 | -1160361
10 | 28 | 12 | 6 | 5.4764 | 0 | 42.7453 | 0 | 17.0587 | 0 | 6.0317 | 18.8896 | 0 | 0 | 0 | 0 | 90.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.51 | 0 | 8302.51 | 214031 | -131783 | 43 | 53 | 214031 | -1131783
10 | 28 | 13 | 6 | 5.4761 | 0 | 42.7453 | 0 | 16.5563 | 0 | 6.0242 | 18.8896 | 0 | 0 | 0 | 0 | 89.6915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8303.51 | 0 | 8303.51 | 217329 | -122590 | 43 | 53 | 217329 | -1122590
10 | 28 | 14 | 6 | 6.2916 | 0 | 42.7453 | 0 | 7.4384 | 0 | 6.6357 | 8.818 | 0 | 0 | 0 | 0 | 71.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8303.98 | 0 | 8303.98 | 129176 | 0 | 44 | 53 | 129176 | -1000000
10 | 28 | 15 | 6 | 6.3777 | 0 | 42.7453 | 0 | 7.3014 | 0 | 6.5767 | 8.818 | 0 | 0 | 0 | 0 | 71.8189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304.59 | 0 | 8304.59 | 128637 | 0 | 42 | 52 | 128637 | -1000000
10 | 28 | 16 | 6 | 7.3006 | 0 | 42.7453 | 0 | 7.0503 | 0 | 6.5259 | 8.818 | 0 | 0 | 0 | 1.2 | 73.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.88 | 0 | 8302.88 | 128446 | 0 | 42 | 51 | 128446 | -1000000
10 | 28 | 17 | 6 | 8.1608 | 0 | 42.7453 | 0 | 8.7181 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.1499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8302.92 | 0 | 8302.92 | 128052 | -6852.73 | 41 | 50 | 128052 | -1006852.73
10 | 28 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.4232 | 0 | 5.4846 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8303.29 | 0 | 8303.29 | 127676 | 0 | 40 | 48 | 127676 | -1000000
10 | 28 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.402 | 0 | 5.9029 | 12.8287 | 0 | 0 | 0 | 7.2 | 83.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304.14 | 0 | 8304.14 | 127212 | -1599.32 | 37 | 45 | 127212 | -1001599.32
10 | 28 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3955 | 0 | 5.4849 | 8.818 | 0 | 0 | 0 | 7.2 | 79.4409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8305.26 | 0 | 8305.26 | 127074 | 0 | 38 | 41 | 127074 | -1000000
10 | 28 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3431 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 7.2 | 87.8116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8306.49 | 0 | 8306.49 | 126498 | -16154.4 | 38 | 39 | 126498 | -1016154.4
10 | 28 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 6.3419 | 0 | 5.9036 | 12.8287 | 0 | 0 | 0 | 6.4 | 83.0167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.06 | 0 | 8308.06 | 125893 | -5889.34 | 36 | 37 | 125893 | -1005889.34
10 | 28 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.1228 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 5.6 | 84.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8309.76 | 0 | 8309.76 | 127877 | -13295 | 36 | 37 | 127877 | -1013295
10 | 28 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 6.3057 | 0 | 5.904 | 12.8287 | 0 | 0 | 0 | 4.8 | 77.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.5 | 0 | 3244.5 | 125064 | -11451.4 | 36 | 37 | 125064 | -1011451.4
10 | 29 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.9888 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3246.53 | 0 | 3246.53 | 125301 | -15221.9 | 36 | 37 | 125301 | -1015221.9
10 | 29 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 8.8002 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3248.77 | 0 | 3248.77 | 124215 | -15023.6 | 35 | 36 | 124215 | -1015023.6
10 | 29 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.8109 | 0 | 5.8972 | 15.3158 | 0 | 0 | 0 | 4.8 | 83.6746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.94 | 0 | 3250.94 | 134993 | -24060.4 | 35 | 36 | 134993 | -1024060.4
10 | 29 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 9.2524 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 80.6286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3253.09 | 0 | 3253.09 | 123469 | -18585.9 | 34 | 35 | 123469 | -1018585.9
10 | 29 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.5091 | 0 | 5.907 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3255.62 | 0 | 3255.62 | 153051 | -31495.4 | 32 | 33 | 153051 | -1031495.4
10 | 29 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.5993 | 0 | 5.9066 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3258.03 | 0 | 3258.03 | 149832 | -38704.8 | 30 | 31 | 149832 | -1038704.8
10 | 29 | 7 | 7 | 5.0604 | 0 | 42.7453 | 0 | 11.6513 | 0 | 5.9065 | 17.3638 | 0 | 0 | 0 | 0.8 | 83.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3260.43 | 0 | 3260.43 | 148308 | -43339.4 | 31 | 32 | 148308 | -1043339.4
10 | 29 | 8 | 7 | 4.1895 | 0 | 42.7453 | 0 | 12.1465 | 0 | 5.9098 | 17.3638 | 0 | 0 | 0 | 0 | 82.3549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3263.23 | 0 | 3263.23 | 148555 | -45662 | 31 | 32 | 148555 | -1045662
10 | 29 | 9 | 7 | 4.192 | 0 | 42.7453 | 0 | 11.7829 | 0 | 5.9073 | 17.3638 | 0 | 0 | 0 | 0 | 81.9912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3265.72 | 0 | 3265.72 | 148579 | -39246.8 | 33 | 35 | 148579 | -1039246.8
10 | 29 | 10 | 7 | 4.1651 | 0 | 42.7453 | 0 | 10.7203 | 0 | 5.8992 | 15.3158 | 0 | 0 | 0 | 0 | 78.8457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3268.25 | 0 | 3268.25 | 135072 | -33834.9 | 34 | 36 | 135072 | -1033834.9
10 | 29 | 11 | 7 | 4.1509 | 0 | 42.7453 | 0 | 11.2236 | 0 | 5.9053 | 17.3638 | 0 | 0 | 0 | 0 | 81.3889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3269.99 | 0 | 3269.99 | 152734 | -30524.8 | 37 | 41 | 152734 | -1030524.8
10 | 29 | 12 | 7 | 4.1502 | 0 | 42.7453 | 0 | 9.2135 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 74.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3271.08 | 0 | 3271.08 | 126039 | -16984.9 | 39 | 44 | 126039 | -1016984.9
10 | 29 | 13 | 7 | 4.1512 | 0 | 42.7453 | 0 | 6.1391 | 0 | 5.906 | 12.8287 | 0 | 0 | 0 | 0 | 71.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.15 | 0 | 3272.15 | 121389 | -11420.6 | 39 | 46 | 121389 | -1011420.6
10 | 29 | 14 | 7 | 4.153 | 0 | 42.7453 | 0 | 6.1972 | 0 | 5.9053 | 12.8287 | 0 | 0 | 0 | 0 | 71.8294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.4 | 0 | 3272.4 | 122761 | -11136.1 | 39 | 46 | 122761 | -1011136.1
10 | 29 | 15 | 7 | 4.1636 | 0 | 42.7453 | 0 | 7.7617 | 0 | 5.9 | 12.8287 | 0 | 0 | 0 | 0 | 73.3992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.08 | 0 | 3272.08 | 121453 | -9398.23 | 42 | 48 | 121453 | -1009398.23
10 | 29 | 16 | 7 | 4.2184 | 0 | 42.7453 | 0 | 7.8681 | 0 | 5.8993 | 12.8287 | 0 | 0 | 0 | 1.2 | 74.7597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3271.95 | 0 | 3271.95 | 123597 | -9130.77 | 41 | 49 | 123597 | -1009130.77
10 | 29 | 17 | 7 | 5.5163 | 0 | 42.7453 | 0 | 7.7448 | 0 | 5.9001 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.08 | 0 | 3272.08 | 121077 | -7734.29 | 38 | 46 | 121077 | -1007734.29
10 | 29 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 8.461 | 0 | 5.8969 | 15.3158 | 0 | 0 | 0 | 7.2 | 86.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3272.42 | 0 | 3272.42 | 134798 | -17402.1 | 37 | 43 | 134798 | -1017402.1
10 | 29 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 8.3273 | 0 | 5.8971 | 15.3158 | 0 | 0 | 0 | 7.2 | 86.1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3273.03 | 0 | 3273.03 | 133343 | -20046.9 | 36 | 40 | 133343 | -1020046.9
10 | 29 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.245 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3274.63 | 0 | 3274.63 | 150977 | -25351.3 | 35 | 39 | 150977 | -1025351.3
10 | 29 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2807 | 0 | 5.9 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3276.85 | 0 | 3276.85 | 147420 | -31109.2 | 34 | 37 | 147420 | -1031109.2
10 | 29 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 11.0411 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 6.4 | 90.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3278.72 | 0 | 3278.72 | 151159 | -34755.5 | 33 | 36 | 151159 | -1034755.5
10 | 29 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.685 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3280.75 | 0 | 3280.75 | 144255 | -32094.7 | 35 | 37 | 144255 | -1032094.7
10 | 29 | 24 | 7 | 10.8489 | 0 | 42.3304 | 0 | 11.0977 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8349.86 | 0 | 8349.86 | 145061 | -40296.6 | 36 | 38 | 145061 | -1040296.6
10 | 30 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.5659 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8351.25 | 0 | 8351.25 | 142919 | -40949.9 | 36 | 37 | 142919 | -1040949.9
10 | 30 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.9276 | 0 | 5.9012 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8352.41 | 0 | 8352.41 | 142039 | -44235.3 | 36 | 37 | 142039 | -1044235.3
10 | 30 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.8344 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8353.77 | 0 | 8353.77 | 141280 | -44525.1 | 35 | 37 | 141280 | -1044525.1
10 | 30 | 4 | 1 | 11.8202 | 0 | 44.8242 | 0 | 11.7525 | 0 | 5.9073 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.6148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9252.82 | 0 | 9252.82 | 149257 | -47355.8 | 36 | 37 | 149257 | -1047355.8
10 | 30 | 5 | 1 | 24.3093 | 0 | 69.9783 | 0 | 12.9524 | 0 | 5.9409 | 17.5105 | 0 | 0 | 0 | 4.8 | 135.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22139.8 | 0 | 22139.8 | 192535 | -37538.1 | 35 | 37 | 192535 | -1037538.1
10 | 30 | 6 | 1 | 49.0171 | 0 | 140.608 | 25.2067 | 0 | 0 | 6.2655 | 19.0363 | 0 | 0 | 0 | 2.4 | 242.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65157.8 | 0 | 65157.8 | 316034 | -479331 | 35 | 37 | 316034 | -1479331
10 | 30 | 7 | 1 | 52.7953 | 0 | 168.222 | 0 | 25.6138 | 0 | 6.2832 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79084.7 | 0 | 79084.7 | 382465 | -431788 | 35 | 38 | 382465 | -1431788
10 | 30 | 8 | 1 | 41.6017 | 0 | 173.795 | 0 | 26.8845 | 0 | 6.3103 | 19.0363 | 0 | 0 | 0 | 0 | 267.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109380 | 0 | 109380 | 413973 | -328536 | 37 | 40 | 413973 | -1328536
10 | 30 | 9 | 1 | 41.0949 | 0 | 172.186 | 0 | 30.7874 | 0 | 7.3533 | 19.0363 | 0 | 0 | 0 | 0 | 270.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128665 | 0 | 128665 | 451454 | -276195 | 39 | 44 | 451454 | -1276195
10 | 30 | 10 | 1 | 41.2311 | 0 | 163.102 | 0 | 30.4733 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 260.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131415 | 0 | 131415 | 435923 | -237206 | 40 | 46 | 435923 | -1237206
10 | 30 | 11 | 1 | 40.7807 | 0 | 149.692 | 0 | 32.1071 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131412 | 0 | 131412 | 424730 | -162885 | 43 | 52 | 424730 | -1162885
10 | 30 | 12 | 1 | 39.8323 | 0 | 150.207 | 0 | 31.2986 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131410 | 0 | 131410 | 401155 | -113754 | 45 | 55 | 401155 | -1113754
10 | 30 | 13 | 1 | 41.3232 | 0 | 165.698 | 0 | 32.8605 | 0 | 6.332 | 19.0565 | 0 | 0 | 0 | 0 | 265.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131406 | 0 | 131406 | 467682 | -70308.4 | 47 | 58 | 467682 | -1070308.4
10 | 30 | 14 | 1 | 40.704 | 0 | 172.702 | 0 | 31.5588 | 0 | 6.332 | 19.2304 | 0 | 0 | 0 | 0 | 270.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129709 | 0 | 129709 | 497026 | -30429.6 | 49 | 60 | 497026 | -1030429.6
10 | 30 | 15 | 1 | 40.6055 | 0 | 173.986 | 0 | 33.8967 | 0 | 6.332 | 19.3692 | 0 | 0 | 0 | 0 | 274.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117932 | 0 | 117932 | 530440 | -21197.7 | 49 | 61 | 530440 | -1021197.7
10 | 30 | 16 | 1 | 49.9955 | 0 | 169.782 | 0 | 28.2989 | 0 | 6.332 | 19.2799 | 0 | 0 | 0 | 1.2 | 274.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96294.5 | 0 | 96294.5 | 469511 | -17878 | 48 | 59 | 469511 | -1017878
10 | 30 | 17 | 1 | 41.944 | 0 | 152.497 | 0 | 26.8901 | 0 | 6.332 | 19.1367 | 0 | 0 | 0 | 4.8 | 251.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72255.8 | 0 | 72255.8 | 426319 | -19244.6 | 48 | 59 | 426319 | -1019244.6
10 | 30 | 18 | 1 | 34.11 | 0 | 93.4203 | 0 | 20.0353 | 0 | 6.2961 | 19.0363 | 0 | 0 | 0 | 7.2 | 180.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44801.4 | 0 | 44801.4 | 317122 | -101201 | 46 | 53 | 317122 | -1101201
10 | 30 | 19 | 1 | 24.2281 | 0 | 62.7906 | 0 | 9.0386 | 0 | 5.4884 | 8.818 | 0 | 0 | 0 | 7.2 | 117.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32102.8 | 0 | 32102.8 | 182692 | 0 | 47 | 56 | 182692 | -1000000
10 | 30 | 20 | 1 | 18.7229 | 0 | 54.6418 | 0 | 8.0619 | 0 | 5.4797 | 8.818 | 0 | 0 | 0 | 7.2 | 102.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28512.7 | 0 | 28512.7 | 163226 | 0 | 46 | 55 | 163226 | -1000000
10 | 30 | 21 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.4523 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17563.8 | 0 | 17563.8 | 149984 | 0 | 44 | 52 | 149984 | -1000000
10 | 30 | 22 | 1 | 11.1963 | 0 | 44.3342 | 0 | 6.964 | 0 | 5.4802 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9529.29 | 0 | 9529.29 | 139341 | 0 | 45 | 53 | 139341 | -1000000
10 | 30 | 23 | 1 | 10.3176 | 0 | 42.5403 | 0 | 8.8558 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8313.9 | 0 | 8313.9 | 134526 | -6242.16 | 44 | 53 | 134526 | -1006242.16
10 | 30 | 24 | 1 | 10.424 | 0 | 42.3304 | 0 | 6.6777 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 78.5323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8315.49 | 0 | 8315.49 | 133231 | 0 | 43 | 51 | 133231 | -1000000
10 | 31 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6575 | 0 | 5.9005 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8316.85 | 0 | 8316.85 | 132803 | -1313.44 | 45 | 50 | 132803 | -1001313.44
10 | 31 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.6123 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.04 | 0 | 8318.04 | 131805 | 0 | 45 | 51 | 131805 | -1000000
10 | 31 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 6.5862 | 0 | 5.9011 | 12.8287 | 0 | 0 | 0 | 4.8 | 82.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8318.98 | 0 | 8318.98 | 131241 | -2009.85 | 44 | 50 | 131241 | -1002009.85
10 | 31 | 4 | 2 | 11.8202 | 0 | 44.8242 | 0 | 6.7164 | 0 | 5.4819 | 8.818 | 0 | 0 | 0 | 4.8 | 82.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9217.68 | 0 | 9217.68 | 134147 | 0 | 42 | 49 | 134147 | -1000000
10 | 31 | 5 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.64 | 0 | 5.9294 | 12.9754 | 0 | 0 | 0 | 4.8 | 130.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22104.1 | 0 | 22104.1 | 180914 | -11693.9 | 41 | 48 | 180914 | -1011693.9
10 | 31 | 6 | 2 | 49.0171 | 0 | 140.608 | 0 | 23.0234 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 240.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65121.7 | 0 | 65121.7 | 326289 | -172596 | 40 | 48 | 326289 | -1172596
10 | 31 | 7 | 2 | 52.8339 | 0 | 168.222 | 0 | 31.317 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 278.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79048.2 | 0 | 79048.2 | 440786 | -186615 | 40 | 48 | 440786 | -1186615
10 | 31 | 8 | 2 | 49.0338 | 0 | 173.795 | 0 | 33.4705 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 281.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109353 | 0 | 109353 | 456330 | -136548 | 42 | 50 | 456330 | -1136548
10 | 31 | 9 | 2 | 42.5579 | 0 | 172.186 | 0 | 34.82 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128638 | 0 | 128638 | 464951 | -132053 | 42 | 51 | 464951 | -1132053
10 | 31 | 10 | 2 | 42.6152 | 0 | 163.102 | 0 | 32.4458 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131388 | 0 | 131388 | 443140 | -102460 | 43 | 53 | 443140 | -1102460
10 | 31 | 11 | 2 | 42.0076 | 0 | 149.692 | 0 | 30.957 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131387 | 0 | 131387 | 437146 | -86230 | 44 | 55 | 437146 | -1086230
10 | 31 | 12 | 2 | 39.8417 | 0 | 150.207 | 0 | 29.3698 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131385 | 0 | 131385 | 431999 | -46235.1 | 46 | 59 | 431999 | -1046235.1
10 | 31 | 13 | 2 | 42.4404 | 0 | 165.698 | 0 | 30.3169 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131385 | 0 | 131385 | 484485 | -30954.7 | 46 | 60 | 484485 | -1030954.7
10 | 31 | 14 | 2 | 41.4587 | 0 | 172.702 | 0 | 30.4464 | 0 | 6.332 | 19.1274 | 0 | 0 | 0 | 0 | 270.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129690 | 0 | 129690 | 514324 | -16030.2 | 48 | 61 | 514324 | -1016030.2
10 | 31 | 15 | 2 | 41.5236 | 0 | 173.986 | 0 | 27.787 | 0 | 25.335 | 19.3149 | 0 | 0 | 0 | 0 | 287.946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117916 | 0 | 117916 | 529797 | -13694 | 47 | 61 | 529797 | -1013694
10 | 31 | 16 | 2 | 45.6007 | 0 | 169.782 | 0 | 28.2047 | 0 | 9.3789 | 19.4617 | 0 | 0 | 0 | 1.2 | 273.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96280.3 | 0 | 96280.3 | 528998 | -11792.5 | 47 | 61 | 528998 | -1011792.5
10 | 31 | 17 | 2 | 47.6076 | 0 | 152.497 | 0 | 25.3293 | 0 | 6.332 | 19.3943 | 0 | 0 | 0 | 4.8 | 255.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72242.4 | 0 | 72242.4 | 458741 | -10712.4 | 46 | 60 | 458741 | -1010712.4
10 | 31 | 18 | 2 | 34.11 | 0 | 93.4203 | 0 | 21.046 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 181.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44788.9 | 0 | 44788.9 | 337259 | -13595.7 | 46 | 59 | 337259 | -1013595.7
10 | 31 | 19 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.2896 | 0 | 5.4921 | 8.818 | 0 | 0 | 0 | 7.2 | 117.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32090.9 | 0 | 32090.9 | 187939 | 0 | 45 | 57 | 187939 | -1000000
10 | 31 | 20 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.2888 | 0 | 5.4809 | 8.818 | 0 | 0 | 0 | 7.2 | 103.152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28501.3 | 0 | 28501.3 | 168188 | 0 | 44 | 55 | 168188 | -1000000
10 | 31 | 21 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.6691 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17549.8 | 0 | 17549.8 | 154727 | 0 | 42 | 52 | 154727 | -1000000
10 | 31 | 22 | 2 | 11.1963 | 0 | 44.3342 | 0 | 7.1566 | 0 | 5.4794 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9514.71 | 0 | 9514.71 | 143548 | 0 | 41 | 50 | 143548 | -1000000
10 | 31 | 23 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.9291 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 5.6 | 79.6854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8298.99 | 0 | 8298.99 | 138673 | 0 | 40 | 48 | 138673 | -1000000
10 | 31 | 24 | 2 | 10.8489 | 0 | 42.3304 | 0 | 9.2324 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.9372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.53 | 0 | 8300.53 | 137114 | -6972.88 | 38 | 46 | 137114 | -1006972.88
11 | 1 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7916 | 0 | 5.4813 | 8.818 | 0 | 0 | 0 | 4.8 | 79.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8998.43 | 0 | 8998.43 | 135722 | 0 | 36 | 42 | 135722 | -1000000
11 | 1 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.2431 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8999.98 | 0 | 8999.98 | 134814 | -12879.4 | 34 | 40 | 134814 | -1012879.4
11 | 1 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.7082 | 0 | 5.482 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9001.68 | 0 | 9001.68 | 133906 | 0 | 33 | 38 | 133906 | -1000000
11 | 1 | 4 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.4952 | 0 | 5.9024 | 12.9754 | 0 | 0 | 0 | 4.8 | 91.8175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9987.36 | 0 | 9987.36 | 136459 | -19451.7 | 31 | 36 | 136459 | -1019451.7
11 | 1 | 5 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.886 | 0 | 5.9046 | 12.9754 | 0 | 0 | 0 | 4.8 | 126.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24114.5 | 0 | 24114.5 | 182355 | -8852.15 | 29 | 33 | 182355 | -1008852.15
11 | 1 | 6 | 3 | 49.0171 | 0 | 140.608 | 0 | 21.8531 | 0 | 6.2994 | 19.0363 | 0 | 0 | 0 | 3.2 | 240.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71271.5 | 0 | 71271.5 | 327149 | -292366 | 27 | 30 | 327149 | -1292366
11 | 1 | 7 | 3 | 53.0484 | 0 | 168.222 | 0 | 25.0578 | 0 | 25.2891 | 19.0363 | 0 | 0 | 0 | 0.8 | 291.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86539.4 | 0 | 86539.4 | 389095 | -401107 | 26 | 29 | 389095 | -1401107
11 | 1 | 8 | 3 | 47.6655 | 0 | 173.795 | 0 | 25.8653 | 0 | 25.2946 | 19.0363 | 0 | 0 | 0 | 0 | 291.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119762 | 0 | 119762 | 407477 | -368824 | 26 | 29 | 407477 | -1368824
11 | 1 | 9 | 3 | 42.3428 | 0 | 172.186 | 0 | 25.7472 | 0 | 25.2979 | 19.0363 | 0 | 0 | 0 | 0 | 284.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140907 | 0 | 140907 | 405263 | -371844 | 27 | 30 | 405263 | -1371844
11 | 1 | 10 | 3 | 42.3957 | 0 | 163.102 | 0 | 25.5786 | 0 | 25.2982 | 19.0363 | 0 | 0 | 0 | 0 | 275.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143924 | 0 | 143924 | 402672 | -387372 | 27 | 31 | 402672 | -1387372
11 | 1 | 11 | 3 | 41.4004 | 0 | 149.692 | 0 | 24.6923 | 0 | 25.3074 | 19.0363 | 0 | 0 | 0 | 0 | 260.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143924 | 0 | 143924 | 387931 | -342018 | 28 | 32 | 387931 | -1342018
11 | 1 | 12 | 3 | 39.9358 | 0 | 150.207 | 0 | 23.0525 | 0 | 25.3012 | 19.0363 | 0 | 0 | 0 | 0 | 257.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143924 | 0 | 143924 | 361359 | -332109 | 28 | 33 | 361359 | -1332109
11 | 1 | 13 | 3 | 42.177 | 0 | 165.698 | 0 | 24.9739 | 0 | 25.3171 | 19.0363 | 0 | 0 | 0 | 0 | 277.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143923 | 0 | 143923 | 392877 | -295160 | 28 | 33 | 392877 | -1295160
11 | 1 | 14 | 3 | 40.7107 | 0 | 172.702 | 0 | 26.1236 | 0 | 25.333 | 19.0363 | 0 | 0 | 0 | 0 | 283.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142064 | 0 | 142064 | 410949 | -281891 | 27 | 32 | 410949 | -1281891
11 | 1 | 15 | 3 | 40.6102 | 0 | 173.986 | 0 | 26.2892 | 0 | 25.3303 | 19.0363 | 0 | 0 | 0 | 0 | 285.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129157 | 0 | 129157 | 413440 | -295560 | 26 | 32 | 413440 | -1295560
11 | 1 | 16 | 3 | 40.7878 | 0 | 169.782 | 0 | 26.0099 | 0 | 25.3179 | 19.0363 | 0 | 0 | 0 | 2.4 | 283.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105442 | 0 | 105442 | 409170 | -336746 | 25 | 30 | 409170 | -1336746
11 | 1 | 17 | 3 | 42.8683 | 0 | 152.497 | 0 | 25.3016 | 0 | 25.2877 | 19.0363 | 0 | 0 | 0 | 6.4 | 271.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79092.5 | 0 | 79092.5 | 398494 | -441815 | 24 | 27 | 398494 | -1441815
11 | 1 | 18 | 3 | 34.11 | 0 | 93.4203 | 28.7466 | 0 | 0 | 6.2839 | 19.0363 | 0 | 0 | 0 | 7.2 | 188.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48998.9 | 0 | 48998.9 | 319360 | -501928 | 22 | 25 | 319360 | -1501928
11 | 1 | 19 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.8946 | 0 | 5.9635 | 12.9754 | 0 | 0 | 0 | 7.2 | 128.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35079.9 | 0 | 35079.9 | 184610 | -13692.7 | 21 | 24 | 184610 | -1013692.7
11 | 1 | 20 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.0332 | 0 | 5.9251 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31145 | 0 | 31145 | 165452 | -19887.9 | 20 | 23 | 165452 | -1019887.9
11 | 1 | 21 | 3 | 13.825 | 0 | 48.8953 | 0 | 13.0369 | 0 | 5.9238 | 15.4625 | 0 | 0 | 0 | 7.2 | 104.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19143.2 | 0 | 19143.2 | 163327 | -33411.9 | 19 | 22 | 163327 | -1033411.9
11 | 1 | 22 | 3 | 11.1963 | 0 | 44.3342 | 0 | 13.4426 | 0 | 5.9317 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.8154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10338.8 | 0 | 10338.8 | 169813 | -42973.2 | 19 | 21 | 169813 | -1042973.2
11 | 1 | 23 | 3 | 10.3176 | 0 | 42.5403 | 0 | 12.7158 | 0 | 5.9192 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9009.06 | 0 | 9009.06 | 160170 | -53194.4 | 18 | 21 | 160170 | -1053194.4
11 | 1 | 24 | 3 | 10.73 | 0 | 42.3304 | 0 | 12.3717 | 0 | 5.9147 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9013.66 | 0 | 9013.66 | 156722 | -72881.2 | 18 | 20 | 156722 | -1072881.2
11 | 2 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.1417 | 0 | 5.912 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.2779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9017.47 | 0 | 9017.47 | 154478 | -90496.6 | 18 | 20 | 154478 | -1090496.6
11 | 2 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.9386 | 0 | 5.9098 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9021.06 | 0 | 9021.06 | 152658 | -102153 | 18 | 20 | 152658 | -1102153
11 | 2 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.7634 | 0 | 5.908 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9024.23 | 0 | 9024.23 | 151030 | -113898 | 18 | 20 | 151030 | -1113898
11 | 2 | 4 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.84 | 0 | 5.9091 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10011.2 | 0 | 10011.2 | 152635 | -128628 | 18 | 19 | 152635 | -1128628
11 | 2 | 5 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.0047 | 0 | 5.9756 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24139.3 | 0 | 24139.3 | 199709 | -113479 | 18 | 19 | 199709 | -1113479
11 | 2 | 6 | 4 | 49.0171 | 0 | 140.608 | 42.7148 | 0 | 0 | 6.2166 | 19.0363 | 0 | 0 | 0 | 3.2 | 260.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71297.2 | 0 | 71297.2 | 324794 | -807372 | 17 | 18 | 324794 | -1807372
11 | 2 | 7 | 4 | 53.0759 | 0 | 168.222 | 41.2022 | 0 | 0 | 6.2279 | 19.0363 | 0 | 0 | 0 | 0.8 | 288.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86566.1 | 0 | 86566.1 | 385727 | -767493 | 18 | 19 | 385727 | -1767493
11 | 2 | 8 | 4 | 42.0737 | 0 | 173.795 | 31.713 | 0 | 0 | 6.2384 | 19.0363 | 0 | 0 | 0 | 0 | 272.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119782 | 0 | 119782 | 404753 | -636044 | 19 | 21 | 404753 | -1636044
11 | 2 | 9 | 4 | 41.0182 | 0 | 172.186 | 29.2132 | 0 | 0 | 6.2551 | 19.0363 | 0 | 0 | 0 | 0 | 267.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140926 | 0 | 140926 | 402398 | -569411 | 19 | 22 | 402398 | -1569411
11 | 2 | 10 | 4 | 41.2327 | 0 | 163.102 | 28.972 | 0 | 0 | 6.274 | 19.0363 | 0 | 0 | 0 | 0 | 258.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143942 | 0 | 143942 | 392222 | -528200 | 22 | 25 | 392222 | -1528200
11 | 2 | 11 | 4 | 40.7809 | 0 | 149.692 | 0 | 25.9556 | 0 | 25.2973 | 19.0363 | 0 | 0 | 0 | 0 | 260.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143942 | 0 | 143942 | 381617 | -433928 | 24 | 28 | 381617 | -1433928
11 | 2 | 12 | 4 | 39.83 | 0 | 150.207 | 0 | 23.6479 | 0 | 25.3032 | 19.0363 | 0 | 0 | 0 | 0 | 258.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143942 | 0 | 143942 | 357437 | -379836 | 25 | 31 | 357437 | -1379836
11 | 2 | 13 | 4 | 41.3019 | 0 | 165.698 | 0 | 24.8257 | 0 | 25.3153 | 19.0363 | 0 | 0 | 0 | 0 | 276.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143940 | 0 | 143940 | 390780 | -329272 | 26 | 32 | 390780 | -1329272
11 | 2 | 14 | 4 | 40.6929 | 0 | 172.702 | 0 | 25.9967 | 0 | 25.3293 | 19.0363 | 0 | 0 | 0 | 0 | 283.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142081 | 0 | 142081 | 409045 | -298104 | 26 | 33 | 409045 | -1298104
11 | 2 | 15 | 4 | 40.6094 | 0 | 173.986 | 0 | 26.171 | 0 | 25.3301 | 19.0363 | 0 | 0 | 0 | 0 | 285.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129174 | 0 | 129174 | 411593 | -301283 | 26 | 34 | 411593 | -1301283
11 | 2 | 16 | 4 | 40.9078 | 0 | 169.782 | 0 | 25.8669 | 0 | 25.3111 | 19.0363 | 0 | 0 | 0 | 2.4 | 283.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105457 | 0 | 105457 | 407074 | -363081 | 25 | 31 | 407074 | -1363081
11 | 2 | 17 | 4 | 43.4685 | 0 | 152.497 | 0 | 25.6342 | 0 | 25.2873 | 19.0363 | 0 | 0 | 0 | 6.4 | 272.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79107 | 0 | 79107 | 397063 | -467236 | 23 | 28 | 397063 | -1467236
11 | 2 | 18 | 4 | 34.11 | 0 | 93.4203 | 31.6177 | 0 | 0 | 6.2796 | 19.0363 | 0 | 0 | 0 | 7.2 | 191.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49012.9 | 0 | 49012.9 | 317809 | -543087 | 21 | 25 | 317809 | -1543087
11 | 2 | 19 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.8057 | 0 | 5.9611 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35093.3 | 0 | 35093.3 | 183254 | -15208.8 | 20 | 24 | 183254 | -1015208.8
11 | 2 | 20 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.1213 | 0 | 5.9253 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31158 | 0 | 31158 | 164188 | -22940.6 | 20 | 23 | 164188 | -1022940.6
11 | 2 | 21 | 4 | 13.825 | 0 | 48.8953 | 0 | 14.0254 | 0 | 5.9446 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19157 | 0 | 19157 | 178839 | -40643.8 | 19 | 22 | 178839 | -1040643.8
11 | 2 | 22 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.8294 | 0 | 5.9216 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10352.9 | 0 | 10352.9 | 162636 | -57531.2 | 19 | 21 | 162636 | -1057531.2
11 | 2 | 23 | 4 | 10.3176 | 0 | 42.5403 | 0 | 12.2327 | 0 | 5.9131 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9023.09 | 0 | 9023.09 | 155459 | -78561.5 | 18 | 20 | 155459 | -1078561.5
11 | 2 | 24 | 4 | 10.8489 | 0 | 42.3304 | 0 | 11.9135 | 0 | 5.9095 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9027.58 | 0 | 9027.58 | 152301 | -99896.6 | 17 | 19 | 152301 | -1099896.6
11 | 3 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.6988 | 0 | 5.9074 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.15 | 0 | 9031.15 | 150396 | -114882 | 17 | 19 | 150396 | -1114882
11 | 3 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.525 | 0 | 5.9058 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9034.49 | 0 | 9034.49 | 148613 | -127267 | 17 | 18 | 148613 | -1127267
11 | 3 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3741 | 0 | 5.9045 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9037.47 | 0 | 9037.47 | 147071 | -140575 | 16 | 18 | 147071 | -1140575
11 | 3 | 4 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.4668 | 0 | 5.9055 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10024.3 | 0 | 10024.3 | 148834 | -150800 | 16 | 18 | 148834 | -1150800
11 | 3 | 5 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.6412 | 0 | 5.9663 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24152.1 | 0 | 24152.1 | 195865 | -133527 | 16 | 18 | 195865 | -1133527
11 | 3 | 6 | 5 | 49.0171 | 0 | 140.608 | 46.4413 | 0 | 0 | 6.2115 | 19.0669 | 0 | 0 | 0 | 3.2 | 264.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71309.8 | 0 | 71309.8 | 323574 | -863543 | 16 | 18 | 323574 | -1863543
11 | 3 | 7 | 5 | 52.9913 | 0 | 168.222 | 42.7012 | 0 | 0 | 6.2257 | 19.0363 | 0 | 0 | 0 | 0.8 | 289.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86578.4 | 0 | 86578.4 | 385019 | -789775 | 18 | 20 | 385019 | -1789775
11 | 3 | 8 | 5 | 42.2348 | 0 | 173.795 | 33.0626 | 0 | 0 | 6.2348 | 19.0363 | 0 | 0 | 0 | 0 | 274.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119791 | 0 | 119791 | 403934 | -660618 | 19 | 21 | 403934 | -1660618
11 | 3 | 9 | 5 | 40.9627 | 0 | 172.186 | 31.0727 | 0 | 0 | 6.2509 | 19.0363 | 0 | 0 | 0 | 0 | 269.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140933 | 0 | 140933 | 401638 | -602957 | 20 | 23 | 401638 | -1602957
11 | 3 | 10 | 5 | 41.2632 | 0 | 163.102 | 33.1843 | 0 | 0 | 6.2648 | 19.0363 | 0 | 0 | 0 | 0 | 262.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143949 | 0 | 143949 | 394945 | -600926 | 22 | 25 | 394945 | -1600926
11 | 3 | 11 | 5 | 40.7787 | 0 | 149.692 | 27.2439 | 0 | 0 | 6.2718 | 19.0363 | 0 | 0 | 0 | 0 | 243.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143949 | 0 | 143949 | 375554 | -505804 | 23 | 27 | 375554 | -1505804
11 | 3 | 12 | 5 | 39.8019 | 0 | 150.207 | 24.5872 | 0 | 0 | 6.2722 | 19.0363 | 0 | 0 | 0 | 0 | 239.905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143948 | 0 | 143948 | 356517 | -474136 | 24 | 29 | 356517 | -1474136
11 | 3 | 13 | 5 | 41.2992 | 0 | 165.698 | 0 | 24.7458 | 0 | 25.2888 | 19.0363 | 0 | 0 | 0 | 0 | 276.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143947 | 0 | 143947 | 390003 | -398953 | 25 | 30 | 390003 | -1398953
11 | 3 | 14 | 5 | 40.6927 | 0 | 172.702 | 0 | 25.9121 | 0 | 25.2992 | 19.0363 | 0 | 0 | 0 | 0 | 283.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142088 | 0 | 142088 | 408305 | -379483 | 25 | 31 | 408305 | -1379483
11 | 3 | 15 | 5 | 40.9102 | 0 | 173.986 | 0 | 26.0899 | 0 | 25.2985 | 19.0363 | 0 | 0 | 0 | 0 | 285.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129180 | 0 | 129180 | 410953 | -387531 | 25 | 32 | 410953 | -1387531
11 | 3 | 16 | 5 | 40.8474 | 0 | 169.782 | 0 | 25.6961 | 0 | 25.2998 | 19.0363 | 0 | 0 | 0 | 2.4 | 283.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105464 | 0 | 105464 | 404560 | -396759 | 25 | 31 | 404560 | -1396759
11 | 3 | 17 | 5 | 43.1817 | 0 | 152.497 | 0 | 25.6854 | 0 | 25.2797 | 19.0363 | 0 | 0 | 0 | 6.4 | 272.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79114 | 0 | 79114 | 394596 | -481967 | 23 | 29 | 394596 | -1481967
11 | 3 | 18 | 5 | 34.11 | 0 | 93.4203 | 29.9697 | 0 | 0 | 6.2828 | 19.0363 | 0 | 0 | 0 | 7.2 | 190.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49019.4 | 0 | 49019.4 | 310019 | -527483 | 22 | 28 | 310019 | -1527483
11 | 3 | 19 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.7615 | 0 | 5.9599 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35099.5 | 0 | 35099.5 | 182777 | -15407.2 | 22 | 27 | 182777 | -1015407.2
11 | 3 | 20 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.1182 | 0 | 5.925 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31163.9 | 0 | 31163.9 | 163656 | -22376.9 | 21 | 26 | 163656 | -1022376.9
11 | 3 | 21 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.7269 | 0 | 5.9191 | 15.4625 | 0 | 0 | 0 | 7.2 | 104.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19163.4 | 0 | 19163.4 | 159694 | -35582.7 | 21 | 25 | 159694 | -1035582.7
11 | 3 | 22 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.9576 | 0 | 5.9229 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10359.2 | 0 | 10359.2 | 163060 | -50018.6 | 22 | 26 | 163060 | -1050018.6
11 | 3 | 23 | 5 | 10.3176 | 0 | 42.5403 | 0 | 12.3652 | 0 | 5.9139 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.2475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.21 | 0 | 9029.21 | 154837 | -59813.6 | 23 | 27 | 154837 | -1059813.6
11 | 3 | 24 | 5 | 6.3817 | 0 | 42.7453 | 0 | 12.0932 | 0 | 5.9105 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9033.38 | 0 | 9033.38 | 151470 | -74742.6 | 23 | 28 | 151470 | -1074742.6
11 | 4 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.9496 | 0 | 5.9088 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.1492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9036.55 | 0 | 9036.55 | 149727 | -88301 | 23 | 27 | 149727 | -1088301
11 | 4 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7862 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9040.1 | 0 | 9040.1 | 147780 | -96269.5 | 23 | 27 | 147780 | -1096269.5
11 | 4 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7062 | 0 | 5.9063 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9042.87 | 0 | 9042.87 | 146891 | -108622 | 22 | 26 | 146891 | -1108622
11 | 4 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.5597 | 0 | 5.905 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9045.48 | 0 | 9045.48 | 145030 | -113580 | 22 | 26 | 145030 | -1113580
11 | 4 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.5331 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.92 | 0 | 9047.92 | 144736 | -121557 | 22 | 25 | 144736 | -1121557
11 | 4 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4631 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9050.24 | 0 | 9050.24 | 142753 | -123271 | 21 | 25 | 142753 | -1123271
11 | 4 | 7 | 6 | 6.3704 | 0 | 42.7453 | 50.3948 | 0 | 0 | 6.2359 | 19.1931 | 0 | 0 | 0 | 0.8 | 125.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.5 | 0 | 9052.5 | 126812 | -846834 | 24 | 27 | 126812 | -1846834
11 | 4 | 8 | 6 | 6.092 | 0 | 42.7453 | 42.9608 | 0 | 0 | 6.239 | 18.9464 | 0 | 0 | 0 | 0 | 116.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9054.37 | 0 | 9054.37 | 133405 | -720641 | 26 | 30 | 133405 | -1720641
11 | 4 | 9 | 6 | 5.5721 | 0 | 42.7453 | 31.876 | 0 | 0 | 6.2482 | 18.8896 | 0 | 0 | 0 | 0 | 105.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9046.21 | 0 | 9046.21 | 141553 | -566464 | 28 | 32 | 141553 | -1566464
11 | 4 | 10 | 6 | 5.4776 | 0 | 42.7453 | 27.4957 | 0 | 0 | 6.2492 | 18.8896 | 0 | 0 | 0 | 0 | 100.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9042.54 | 0 | 9042.54 | 144183 | -497655 | 30 | 34 | 144183 | -1497655
11 | 4 | 11 | 6 | 5.4768 | 0 | 42.7453 | 25.2868 | 0 | 0 | 6.2478 | 18.8896 | 0 | 0 | 0 | 0 | 98.6463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9041.23 | 0 | 9041.23 | 148736 | -467370 | 31 | 36 | 148736 | -1467370
11 | 4 | 12 | 6 | 6.0867 | 0 | 42.7453 | 25.2441 | 0 | 0 | 6.2448 | 18.8896 | 0 | 0 | 0 | 0 | 99.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9040.38 | 0 | 9040.38 | 162996 | -473783 | 32 | 38 | 162996 | -1473783
11 | 4 | 13 | 6 | 5.9315 | 0 | 42.7453 | 24.7843 | 0 | 0 | 6.2422 | 18.8896 | 0 | 0 | 0 | 0 | 98.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9040.01 | 0 | 9040.01 | 162559 | -469782 | 33 | 38 | 162559 | -1469782
11 | 4 | 14 | 6 | 6.4411 | 0 | 42.7453 | 0 | 9.4809 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 77.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9039.89 | 0 | 9039.89 | 124469 | -10498.9 | 33 | 39 | 124469 | -1010498.9
11 | 4 | 15 | 6 | 6.4638 | 0 | 42.7453 | 0 | 9.0021 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 0 | 76.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9040.04 | 0 | 9040.04 | 123252 | -13624.4 | 33 | 39 | 123252 | -1013624.4
11 | 4 | 16 | 6 | 6.3116 | 0 | 42.7453 | 0 | 9.6398 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 2.4 | 79.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9042.51 | 0 | 9042.51 | 123332 | -17699.9 | 32 | 37 | 123332 | -1017699.9
11 | 4 | 17 | 6 | 7.7893 | 0 | 42.7453 | 0 | 10.2514 | 0 | 5.8976 | 15.3158 | 0 | 0 | 0 | 6.4 | 88.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9045.45 | 0 | 9045.45 | 131567 | -26805.8 | 31 | 35 | 131567 | -1026805.8
11 | 4 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.676 | 0 | 5.9054 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.6878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.34 | 0 | 9047.34 | 144532 | -32743.3 | 29 | 33 | 144532 | -1032743.3
11 | 4 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.7225 | 0 | 5.9052 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9049.92 | 0 | 9049.92 | 142647 | -43516.6 | 29 | 32 | 142647 | -1043516.6
11 | 4 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3911 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.3964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.38 | 0 | 9052.38 | 139291 | -49063.7 | 28 | 30 | 139291 | -1049063.7
11 | 4 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3904 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.3991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9054.7 | 0 | 9054.7 | 137975 | -72738.1 | 27 | 29 | 137975 | -1072738.1
11 | 4 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.224 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9056.45 | 0 | 9056.45 | 137041 | -81378.3 | 27 | 29 | 137041 | -1081378.3
11 | 4 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.13 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.5372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9058.56 | 0 | 9058.56 | 136708 | -93278.8 | 28 | 30 | 136708 | -1093278.8
11 | 4 | 24 | 6 | 5.1054 | 0 | 42.7453 | 0 | 10.9906 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3505.85 | 0 | 3505.85 | 135259 | -100298 | 28 | 30 | 135259 | -1100298
11 | 5 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9184 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3507.89 | 0 | 3507.89 | 134826 | -109009 | 29 | 31 | 134826 | -1109009
11 | 5 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8662 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3509.99 | 0 | 3509.99 | 134013 | -111464 | 29 | 32 | 134013 | -1111464
11 | 5 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8412 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511.94 | 0 | 3511.94 | 133606 | -113480 | 30 | 33 | 133606 | -1113480
11 | 5 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8199 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3513.83 | 0 | 3513.83 | 133137 | -114677 | 30 | 33 | 133137 | -1114677
11 | 5 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7851 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515.62 | 0 | 3515.62 | 132531 | -119093 | 30 | 32 | 132531 | -1119093
11 | 5 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7604 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3517.36 | 0 | 3517.36 | 132166 | -122087 | 29 | 32 | 132166 | -1122087
11 | 5 | 7 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.7662 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 3.2 | 85.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3519.02 | 0 | 3519.02 | 132064 | -123156 | 30 | 33 | 132064 | -1123156
11 | 5 | 8 | 7 | 4.65 | 0 | 42.7453 | 0 | 10.7354 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520.64 | 0 | 3520.64 | 131526 | -114608 | 31 | 34 | 131526 | -1114608
11 | 5 | 9 | 7 | 4.6762 | 0 | 42.7453 | 0 | 10.79 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 0 | 81.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522.2 | 0 | 3522.2 | 132097 | -111049 | 31 | 35 | 132097 | -1111049
11 | 5 | 10 | 7 | 4.9581 | 0 | 42.7453 | 0 | 10.7591 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 81.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3523.69 | 0 | 3523.69 | 131265 | -99709.1 | 32 | 35 | 131265 | -1099709.1
11 | 5 | 11 | 7 | 4.6076 | 0 | 42.7453 | 0 | 10.7566 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 81.3718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525.07 | 0 | 3525.07 | 131191 | -86519.3 | 32 | 36 | 131191 | -1086519.3
11 | 5 | 12 | 7 | 4.6593 | 0 | 42.7453 | 0 | 10.8124 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 0 | 81.4796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526.44 | 0 | 3526.44 | 131826 | -82910 | 32 | 36 | 131826 | -1082910
11 | 5 | 13 | 7 | 4.1511 | 0 | 42.7453 | 0 | 10.7852 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 0 | 80.9442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3527.7 | 0 | 3527.7 | 131246 | -62221.4 | 33 | 37 | 131246 | -1062221.4
11 | 5 | 14 | 7 | 4.1518 | 0 | 42.7453 | 0 | 10.995 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 0 | 81.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3528.89 | 0 | 3528.89 | 133664 | -54991.1 | 33 | 37 | 133664 | -1054991.1
11 | 5 | 15 | 7 | 4.1653 | 0 | 42.7453 | 0 | 10.9549 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 0 | 81.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530.08 | 0 | 3530.08 | 133129 | -48901.4 | 32 | 38 | 133129 | -1048901.4
11 | 5 | 16 | 7 | 4.2445 | 0 | 42.7453 | 0 | 11.1636 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 0 | 81.4178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531 | 0 | 3531 | 135109 | -51140.2 | 31 | 35 | 135109 | -1051140.2
11 | 5 | 17 | 7 | 5.6849 | 0 | 42.7453 | 0 | 10.2825 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 2.4 | 84.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531.51 | 0 | 3531.51 | 132090 | -55690.2 | 29 | 33 | 132090 | -1055690.2
11 | 5 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.8145 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3532.39 | 0 | 3532.39 | 130603 | -71776.1 | 27 | 30 | 130603 | -1071776.1
11 | 5 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6331 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.25 | 0 | 3533.25 | 129569 | -98405.4 | 27 | 30 | 129569 | -1098405.4
11 | 5 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5248 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3534.7 | 0 | 3534.7 | 129211 | -127848 | 27 | 29 | 129211 | -1127848
11 | 5 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4567 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536.21 | 0 | 3536.21 | 128647 | -137361 | 27 | 29 | 128647 | -1137361
11 | 5 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3973 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3537.83 | 0 | 3537.83 | 128344 | -145885 | 27 | 29 | 128344 | -1145885
11 | 5 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3677 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3539.31 | 0 | 3539.31 | 128050 | -147215 | 27 | 30 | 128050 | -1147215
11 | 5 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3971 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3540.76 | 0 | 3540.76 | 128285 | -151515 | 27 | 30 | 128285 | -1151515
11 | 6 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3827 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.9 | 0 | 9096.9 | 128011 | -145329 | 29 | 32 | 128011 | -1145329
11 | 6 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4347 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.21 | 0 | 9098.21 | 128673 | -147834 | 31 | 33 | 128673 | -1147834
11 | 6 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4027 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9098.62 | 0 | 9098.62 | 127954 | -143577 | 32 | 35 | 127954 | -1143577
11 | 6 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.5091 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9099.47 | 0 | 9099.47 | 129031 | -144901 | 33 | 35 | 129031 | -1144901
11 | 6 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.6904 | 0 | 5.8985 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10084.2 | 0 | 10084.2 | 131308 | -137425 | 33 | 36 | 131308 | -1137425
11 | 6 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 14.4462 | 0 | 5.9531 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24210.2 | 0 | 24210.2 | 183007 | -107445 | 34 | 36 | 183007 | -1107445
11 | 6 | 7 | 1 | 49.0171 | 0 | 140.608 | 41.5984 | 0 | 0 | 6.2346 | 19.1583 | 0 | 0 | 0 | 3.2 | 259.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71366.1 | 0 | 71366.1 | 313164 | -741108 | 35 | 37 | 313164 | -1741108
11 | 6 | 8 | 1 | 48.8494 | 0 | 168.222 | 35.1858 | 0 | 0 | 6.2409 | 19.0704 | 0 | 0 | 0 | 0.8 | 278.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86632.8 | 0 | 86632.8 | 403156 | -659362 | 36 | 38 | 403156 | -1659362
11 | 6 | 9 | 1 | 43.2847 | 0 | 173.795 | 0 | 27.6333 | 0 | 6.2606 | 19.0363 | 0 | 0 | 0 | 0 | 270.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119835 | 0 | 119835 | 421975 | -515502 | 36 | 39 | 421975 | -1515502
11 | 6 | 10 | 1 | 41.9476 | 0 | 172.186 | 0 | 29.0106 | 0 | 6.2774 | 19.0363 | 0 | 0 | 0 | 0 | 268.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140972 | 0 | 140972 | 434514 | -462495 | 38 | 41 | 434514 | -1462495
11 | 6 | 11 | 1 | 42.1031 | 0 | 163.102 | 0 | 28.1393 | 0 | 6.2856 | 19.0363 | 0 | 0 | 0 | 0 | 258.667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143984 | 0 | 143984 | 421815 | -426535 | 39 | 42 | 421815 | -1426535
11 | 6 | 12 | 1 | 41.4001 | 0 | 149.692 | 0 | 29.0353 | 0 | 6.2942 | 19.0363 | 0 | 0 | 0 | 0 | 245.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143982 | 0 | 143982 | 422983 | -383566 | 40 | 44 | 422983 | -1383566
11 | 6 | 13 | 1 | 39.9516 | 0 | 150.207 | 0 | 26.6811 | 0 | 6.2999 | 19.0363 | 0 | 0 | 0 | 0 | 242.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143979 | 0 | 143979 | 388428 | -336952 | 41 | 45 | 388428 | -1336952
11 | 6 | 14 | 1 | 42.3755 | 0 | 165.698 | 0 | 31.1173 | 0 | 6.3176 | 19.0363 | 0 | 0 | 0 | 0 | 264.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143976 | 0 | 143976 | 449439 | -313720 | 41 | 45 | 449439 | -1313720
11 | 6 | 15 | 1 | 41.5938 | 0 | 172.702 | 0 | 32.7379 | 0 | 6.3292 | 19.0363 | 0 | 0 | 0 | 0 | 272.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142115 | 0 | 142115 | 464326 | -288565 | 42 | 46 | 464326 | -1288565
11 | 6 | 16 | 1 | 43.782 | 0 | 173.986 | 0 | 32.0429 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129205 | 0 | 129205 | 455121 | -276241 | 42 | 46 | 455121 | -1276241
11 | 6 | 17 | 1 | 54.4528 | 0 | 169.782 | 0 | 32.2137 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 284.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105486 | 0 | 105486 | 457427 | -278946 | 42 | 46 | 457427 | -1278946
11 | 6 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 29.6091 | 0 | 6.3267 | 19.0363 | 0 | 0 | 0 | 6.4 | 263.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79134 | 0 | 79134 | 428326 | -293870 | 43 | 46 | 428326 | -1293870
11 | 6 | 19 | 1 | 34.11 | 0 | 93.4203 | 0 | 25.4923 | 0 | 6.3035 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49037.6 | 0 | 49037.6 | 358369 | -372939 | 43 | 45 | 358369 | -1372939
11 | 6 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 8.9204 | 0 | 5.4869 | 8.818 | 0 | 0 | 0 | 7.2 | 117.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35116.2 | 0 | 35116.2 | 179360 | 0 | 43 | 44 | 179360 | -1000000
11 | 6 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.1796 | 0 | 5.9147 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31181.1 | 0 | 31181.1 | 160181 | -11277.6 | 43 | 43 | 160181 | -1011277.6
11 | 6 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 7.3133 | 0 | 5.4789 | 8.818 | 0 | 0 | 0 | 7.2 | 91.5304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19182.9 | 0 | 19182.9 | 146943 | 0 | 43 | 43 | 146943 | -1000000
11 | 6 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 11.4587 | 0 | 5.9022 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10377.5 | 0 | 10377.5 | 136083 | -18398.9 | 43 | 44 | 136083 | -1018398.9
11 | 6 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 6.6039 | 0 | 5.901 | 12.9754 | 0 | 0 | 0 | 5.6 | 83.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9046.52 | 0 | 9046.52 | 131561 | -8540.79 | 43 | 44 | 131561 | -1008540.79
11 | 7 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.2665 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9049.08 | 0 | 9049.08 | 132113 | -13187.9 | 43 | 44 | 132113 | -1013187.9
11 | 7 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.7528 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9051.16 | 0 | 9051.16 | 129541 | -11450.6 | 43 | 44 | 129541 | -1011450.6
11 | 7 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.811 | 0 | 5.898 | 14.8767 | 0 | 0 | 0 | 4.8 | 88.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.86 | 0 | 9052.86 | 142884 | -14893.1 | 44 | 44 | 142884 | -1014893.1
11 | 7 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.9105 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9054.35 | 0 | 9054.35 | 128273 | -14078.5 | 43 | 44 | 128273 | -1014078.5
11 | 7 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 10.5549 | 0 | 5.9019 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.4118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10039.7 | 0 | 10039.7 | 151827 | -22807.4 | 43 | 43 | 151827 | -1022807.4
11 | 7 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 12.8596 | 0 | 5.9387 | 15.0234 | 0 | 0 | 0 | 4.8 | 132.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24166.2 | 0 | 24166.2 | 190898 | -17153.5 | 43 | 43 | 190898 | -1017153.5
11 | 7 | 7 | 2 | 49.0171 | 0 | 140.608 | 0 | 23.18 | 0 | 6.2781 | 19.0363 | 0 | 0 | 0 | 3.2 | 241.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71322.8 | 0 | 71322.8 | 323672 | -404502 | 44 | 44 | 323672 | -1404502
11 | 7 | 8 | 2 | 47.464 | 0 | 168.222 | 0 | 31.861 | 0 | 6.2912 | 19.0363 | 0 | 0 | 0 | 0.8 | 273.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86589.9 | 0 | 86589.9 | 468031 | -416916 | 44 | 44 | 468031 | -1416916
11 | 7 | 9 | 2 | 41.9501 | 0 | 173.795 | 0 | 33.0721 | 0 | 6.3111 | 19.0363 | 0 | 0 | 0 | 0 | 274.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119805 | 0 | 119805 | 476959 | -323708 | 45 | 45 | 476959 | -1323708
11 | 7 | 10 | 2 | 41.5496 | 0 | 172.186 | 0 | 34.0682 | 0 | 6.3258 | 19.0363 | 0 | 0 | 0 | 0 | 273.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140943 | 0 | 140943 | 484401 | -289888 | 46 | 46 | 484401 | -1289888
11 | 7 | 11 | 2 | 42.2146 | 0 | 163.102 | 0 | 32.7441 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143956 | 0 | 143956 | 462344 | -264192 | 47 | 47 | 462344 | -1264192
11 | 7 | 12 | 2 | 42.2085 | 0 | 149.692 | 0 | 32.3222 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143953 | 0 | 143953 | 448517 | -252206 | 48 | 48 | 448517 | -1252206
11 | 7 | 13 | 2 | 39.9799 | 0 | 150.207 | 0 | 29.993 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 245.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143951 | 0 | 143951 | 416686 | -211497 | 49 | 49 | 416686 | -1211497
11 | 7 | 14 | 2 | 42.6141 | 0 | 165.698 | 0 | 34.0077 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 267.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143948 | 0 | 143948 | 467292 | -193151 | 49 | 49 | 467292 | -1193151
11 | 7 | 15 | 2 | 45.0719 | 0 | 172.702 | 0 | 36.3961 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 279.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142088 | 0 | 142088 | 490433 | -174987 | 50 | 50 | 490433 | -1174987
11 | 7 | 16 | 2 | 46.5669 | 0 | 173.986 | 0 | 36.0397 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 281.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129179 | 0 | 129179 | 490134 | -170241 | 49 | 49 | 490134 | -1170241
11 | 7 | 17 | 2 | 54.872 | 0 | 169.782 | 0 | 35.7217 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 288.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105461 | 0 | 105461 | 495501 | -197920 | 47 | 47 | 495501 | -1197920
11 | 7 | 18 | 2 | 49.7836 | 0 | 152.497 | 0 | 32.292 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 266.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79109.9 | 0 | 79109.9 | 463353 | -228980 | 46 | 46 | 463353 | -1228980
11 | 7 | 19 | 2 | 34.11 | 0 | 93.4203 | 0 | 25.5616 | 0 | 6.322 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49014.8 | 0 | 49014.8 | 353952 | -295725 | 45 | 46 | 353952 | -1295725
11 | 7 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.1529 | 0 | 5.49 | 8.818 | 0 | 0 | 0 | 7.2 | 117.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35094.5 | 0 | 35094.5 | 184612 | 0 | 45 | 45 | 184612 | -1000000
11 | 7 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 11.1751 | 0 | 5.9098 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31158.4 | 0 | 31158.4 | 165031 | -7866.88 | 44 | 45 | 165031 | -1007866.88
11 | 7 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.5315 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19159 | 0 | 19159 | 151716 | 0 | 43 | 44 | 151716 | -1000000
11 | 7 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 11.2166 | 0 | 5.9021 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10353 | 0 | 10353 | 140583 | -14864.4 | 42 | 44 | 140583 | -1014864.4
11 | 7 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.8054 | 0 | 5.4812 | 8.818 | 0 | 0 | 0 | 5.6 | 79.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9021.9 | 0 | 9021.9 | 135970 | 0 | 42 | 43 | 135970 | -1000000
11 | 8 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3097 | 0 | 5.9011 | 12.8287 | 0 | 0 | 0 | 4.8 | 88.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9024.45 | 0 | 9024.45 | 134116 | -18352.2 | 39 | 41 | 134116 | -1018352.2
11 | 8 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6795 | 0 | 5.9003 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9026.77 | 0 | 9026.77 | 133278 | -8900 | 37 | 39 | 133278 | -1008900
11 | 8 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 9.7059 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.73 | 0 | 9028.73 | 132955 | -15513.5 | 35 | 37 | 132955 | -1015513.5
11 | 8 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.5042 | 0 | 5.9008 | 14.8767 | 0 | 0 | 0 | 4.8 | 89.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9030.76 | 0 | 9030.76 | 147604 | -19266.2 | 34 | 36 | 147604 | -1019266.2
11 | 8 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.9556 | 0 | 5.9111 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10016.8 | 0 | 10016.8 | 155997 | -33431 | 33 | 34 | 155997 | -1033431
11 | 8 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 15.1589 | 0 | 5.9817 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24144.1 | 0 | 24144.1 | 203366 | -32773.2 | 31 | 33 | 203366 | -1032773.2
11 | 8 | 7 | 3 | 48.9828 | 0 | 140.608 | 26.068 | 0 | 0 | 6.2575 | 19.0363 | 0 | 0 | 0 | 3.2 | 244.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71301.7 | 0 | 71301.7 | 325486 | -536457 | 30 | 32 | 325486 | -1536457
11 | 8 | 8 | 3 | 47.464 | 0 | 168.222 | 27.5967 | 0 | 0 | 6.2641 | 19.0363 | 0 | 0 | 0 | 0.8 | 269.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86570.4 | 0 | 86570.4 | 387209 | -535657 | 29 | 31 | 387209 | -1535657
11 | 8 | 9 | 3 | 40.4906 | 0 | 173.795 | 0 | 25.6982 | 0 | 6.2713 | 19.0363 | 0 | 0 | 0 | 0 | 265.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119788 | 0 | 119788 | 405551 | -469360 | 28 | 30 | 405551 | -1469360
11 | 8 | 10 | 3 | 41.4795 | 0 | 172.186 | 0 | 25.6276 | 0 | 6.2831 | 19.0363 | 0 | 0 | 0 | 0 | 264.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140929 | 0 | 140929 | 403756 | -425725 | 29 | 32 | 403756 | -1425725
11 | 8 | 11 | 3 | 41.6755 | 0 | 163.102 | 0 | 25.4368 | 0 | 25.2864 | 19.0363 | 0 | 0 | 0 | 0 | 274.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143945 | 0 | 143945 | 399679 | -435016 | 31 | 33 | 399679 | -1435016
11 | 8 | 12 | 3 | 40.7822 | 0 | 149.692 | 0 | 24.2925 | 0 | 25.294 | 19.0363 | 0 | 0 | 0 | 0 | 259.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143944 | 0 | 143944 | 381636 | -365987 | 31 | 35 | 381636 | -1365987
11 | 8 | 13 | 3 | 39.8379 | 0 | 150.207 | 0 | 22.8848 | 0 | 25.2992 | 19.0363 | 0 | 0 | 0 | 0 | 257.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143943 | 0 | 143943 | 358796 | -342080 | 32 | 36 | 358796 | -1342080
11 | 8 | 14 | 3 | 41.3135 | 0 | 165.698 | 0 | 24.9064 | 0 | 25.3194 | 19.0363 | 0 | 0 | 0 | 0 | 276.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143941 | 0 | 143941 | 391785 | -290145 | 33 | 36 | 391785 | -1290145
11 | 8 | 15 | 3 | 40.712 | 0 | 172.702 | 0 | 27.0866 | 0 | 25.3277 | 19.0363 | 0 | 0 | 0 | 0 | 284.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142082 | 0 | 142082 | 420427 | -283611 | 33 | 37 | 420427 | -1283611
11 | 8 | 16 | 3 | 45.6738 | 0 | 173.986 | 0 | 27.1429 | 0 | 25.3277 | 19.0363 | 0 | 0 | 0 | 0 | 291.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129174 | 0 | 129174 | 421904 | -300010 | 33 | 37 | 421904 | -1300010
11 | 8 | 17 | 3 | 54.5918 | 0 | 169.782 | 0 | 25.9346 | 0 | 25.3212 | 19.0363 | 0 | 0 | 0 | 2.4 | 297.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105457 | 0 | 105457 | 407645 | -316326 | 33 | 36 | 407645 | -1316326
11 | 8 | 18 | 3 | 49.7836 | 0 | 152.497 | 0 | 24.8468 | 0 | 25.3032 | 19.0363 | 0 | 0 | 0 | 6.4 | 277.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79107 | 0 | 79107 | 390472 | -357011 | 33 | 36 | 390472 | -1357011
11 | 8 | 19 | 3 | 34.11 | 0 | 93.4203 | 21.9225 | 0 | 0 | 6.295 | 19.0363 | 0 | 0 | 0 | 7.2 | 181.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49012.2 | 0 | 49012.2 | 313368 | -406037 | 33 | 36 | 313368 | -1406037
11 | 8 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 12.877 | 0 | 5.9371 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35092.2 | 0 | 35092.2 | 185668 | -8670.89 | 33 | 36 | 185668 | -1008670.89
11 | 8 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 11.0701 | 0 | 5.9092 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31156.7 | 0 | 31156.7 | 165266 | -11473.3 | 33 | 36 | 165266 | -1011473.3
11 | 8 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 11.0492 | 0 | 5.9043 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.8492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19156.4 | 0 | 19156.4 | 151799 | -15685 | 33 | 36 | 151799 | -1015685
11 | 8 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 10.4134 | 0 | 5.8992 | 12.9754 | 0 | 0 | 0 | 6.4 | 91.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10351.3 | 0 | 10351.3 | 140580 | -16429.4 | 33 | 35 | 140580 | -1016429.4
11 | 8 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 10.4195 | 0 | 5.8984 | 12.9754 | 0 | 0 | 0 | 5.6 | 87.7512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9020.44 | 0 | 9020.44 | 135725 | -18158.8 | 32 | 35 | 135725 | -1018158.8
11 | 9 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6468 | 0 | 5.9072 | 14.8767 | 0 | 0 | 0 | 4.8 | 90.2911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9023.68 | 0 | 9023.68 | 150996 | -24483.8 | 33 | 35 | 150996 | -1024483.8
11 | 9 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.1931 | 0 | 5.9127 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9026.42 | 0 | 9026.42 | 155569 | -35855.5 | 33 | 34 | 155569 | -1035855.5
11 | 9 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.6284 | 0 | 5.9058 | 14.8767 | 0 | 0 | 0 | 4.8 | 90.2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.98 | 0 | 9028.98 | 146318 | -31749.8 | 33 | 34 | 146318 | -1031749.8
11 | 9 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.2413 | 0 | 5.9113 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.67 | 0 | 9031.67 | 150887 | -50371.4 | 33 | 34 | 150887 | -1050371.4
11 | 9 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 12.4826 | 0 | 5.9142 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10017.9 | 0 | 10017.9 | 153469 | -56477.3 | 33 | 33 | 153469 | -1056477.3
11 | 9 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.9234 | 0 | 5.9935 | 17.5105 | 0 | 0 | 0 | 4.8 | 138.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24145.6 | 0 | 24145.6 | 201048 | -47694.7 | 33 | 33 | 201048 | -1047694.7
11 | 9 | 7 | 4 | 49.0171 | 0 | 140.608 | 27.0244 | 0 | 0 | 6.2517 | 19.0363 | 0 | 0 | 0 | 3.2 | 245.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71303.1 | 0 | 71303.1 | 325411 | -554621 | 33 | 33 | 325411 | -1554621
11 | 9 | 8 | 4 | 49.2901 | 0 | 168.222 | 27.4048 | 0 | 0 | 6.2645 | 19.0363 | 0 | 0 | 0 | 0.8 | 271.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86571.4 | 0 | 86571.4 | 387350 | -531879 | 33 | 33 | 387350 | -1531879
11 | 9 | 9 | 4 | 48.0019 | 0 | 173.795 | 0 | 25.7244 | 0 | 6.2786 | 19.0363 | 0 | 0 | 0 | 0 | 272.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119788 | 0 | 119788 | 405713 | -434697 | 32 | 33 | 405713 | -1434697
11 | 9 | 10 | 4 | 41.9625 | 0 | 172.186 | 0 | 25.6264 | 0 | 6.2859 | 19.0363 | 0 | 0 | 0 | 0 | 265.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140930 | 0 | 140930 | 403727 | -424730 | 32 | 33 | 403727 | -1424730
11 | 9 | 11 | 4 | 42.7384 | 0 | 163.102 | 0 | 25.4412 | 0 | 25.2861 | 19.0363 | 0 | 0 | 0 | 0 | 275.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143945 | 0 | 143945 | 399517 | -441837 | 32 | 33 | 399517 | -1441837
11 | 9 | 12 | 4 | 41.6179 | 0 | 149.692 | 0 | 24.4641 | 0 | 25.2882 | 19.0363 | 0 | 0 | 0 | 0 | 260.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143944 | 0 | 143944 | 384058 | -409167 | 32 | 33 | 384058 | -1409167
11 | 9 | 13 | 4 | 39.9616 | 0 | 150.207 | 0 | 22.8474 | 0 | 25.2821 | 19.0363 | 0 | 0 | 0 | 0 | 257.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143942 | 0 | 143942 | 358548 | -401997 | 33 | 33 | 358548 | -1401997
11 | 9 | 14 | 4 | 42.6141 | 0 | 165.698 | 0 | 24.875 | 0 | 25.2985 | 19.0363 | 0 | 0 | 0 | 0 | 277.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143941 | 0 | 143941 | 391716 | -349981 | 32 | 34 | 391716 | -1349981
11 | 9 | 15 | 4 | 41.9035 | 0 | 172.702 | 0 | 26.037 | 0 | 25.3091 | 19.0363 | 0 | 0 | 0 | 0 | 284.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142082 | 0 | 142082 | 409984 | -336856 | 33 | 34 | 409984 | -1336856
11 | 9 | 16 | 4 | 45.76 | 0 | 173.986 | 0 | 26.2182 | 0 | 25.3124 | 19.0363 | 0 | 0 | 0 | 0 | 290.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129174 | 0 | 129174 | 412640 | -339299 | 33 | 34 | 412640 | -1339299
11 | 9 | 17 | 4 | 54.9988 | 0 | 169.782 | 0 | 25.8148 | 0 | 25.3061 | 19.0363 | 0 | 0 | 0 | 2.4 | 297.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105458 | 0 | 105458 | 406212 | -363352 | 33 | 33 | 406212 | -1363352
11 | 9 | 18 | 4 | 49.7836 | 0 | 152.497 | 0 | 24.8668 | 0 | 25.2907 | 19.0363 | 0 | 0 | 0 | 6.4 | 277.875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79107.6 | 0 | 79107.6 | 391190 | -406630 | 33 | 33 | 391190 | -1406630
11 | 9 | 19 | 4 | 34.11 | 0 | 93.4203 | 24.0867 | 0 | 0 | 6.2905 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49013.1 | 0 | 49013.1 | 302493 | -438319 | 33 | 33 | 302493 | -1438319
11 | 9 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 13.1237 | 0 | 5.9389 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35093 | 0 | 35093 | 184392 | -9598.3 | 33 | 33 | 184392 | -1009598.3
11 | 9 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 11.4274 | 0 | 5.9114 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31157.5 | 0 | 31157.5 | 165094 | -13068.9 | 33 | 33 | 165094 | -1013068.9
11 | 9 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 11.0494 | 0 | 5.905 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19156.9 | 0 | 19156.9 | 153916 | -15455.2 | 33 | 33 | 153916 | -1015455.2
11 | 9 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 9.6936 | 0 | 5.8976 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.4971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10351.8 | 0 | 10351.8 | 140400 | -13611.9 | 33 | 34 | 140400 | -1013611.9
11 | 9 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.7806 | 0 | 5.9086 | 15.0234 | 0 | 0 | 0 | 5.6 | 91.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9020.72 | 0 | 9020.72 | 152424 | -23996.7 | 33 | 34 | 152424 | -1023996.7
11 | 10 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 12.0212 | 0 | 5.9116 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3468.93 | 0 | 3468.93 | 155902 | -35772.8 | 32 | 34 | 155902 | -1035772.8
11 | 10 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 12.5165 | 0 | 5.9145 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3471.74 | 0 | 3471.74 | 153430 | -47118.1 | 32 | 33 | 153430 | -1047118.1
11 | 10 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 12.2966 | 0 | 5.9118 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3475.55 | 0 | 3475.55 | 151020 | -56017.2 | 31 | 33 | 151020 | -1056017.2
11 | 10 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 12.1262 | 0 | 5.9099 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.76 | 0 | 3478.76 | 149310 | -68016.1 | 30 | 32 | 149310 | -1068016.1
11 | 10 | 5 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.978 | 0 | 5.9084 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481.72 | 0 | 3481.72 | 147860 | -76302.6 | 30 | 32 | 147860 | -1076302.6
11 | 10 | 6 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.8389 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3484.45 | 0 | 3484.45 | 146565 | -86759.8 | 29 | 31 | 146565 | -1086759.8
11 | 10 | 7 | 8 | 5.1054 | 0 | 42.7453 | 0 | 11.7141 | 0 | 5.9059 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3486.98 | 0 | 3486.98 | 145415 | -94354.3 | 29 | 31 | 145415 | -1094354.3
11 | 10 | 8 | 8 | 4.683 | 0 | 42.7453 | 0 | 11.6151 | 0 | 5.9051 | 17.3638 | 0 | 0 | 0 | 0.8 | 83.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3489.44 | 0 | 3489.44 | 144476 | -101438 | 29 | 30 | 144476 | -1101438
11 | 10 | 9 | 8 | 4.3013 | 0 | 42.7453 | 0 | 11.5174 | 0 | 5.9043 | 17.3638 | 0 | 0 | 0 | 0 | 81.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3491.82 | 0 | 3491.82 | 143366 | -96443.3 | 28 | 30 | 143366 | -1096443.3
11 | 10 | 10 | 8 | 4.7885 | 0 | 42.7453 | 0 | 11.5057 | 0 | 5.9042 | 17.3638 | 0 | 0 | 0 | 0 | 82.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3494.16 | 0 | 3494.16 | 143289 | -86175.6 | 29 | 31 | 143289 | -1086175.6
11 | 10 | 11 | 8 | 4.6936 | 0 | 42.7453 | 0 | 11.4506 | 0 | 5.9036 | 17.3638 | 0 | 0 | 0 | 0 | 82.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3496.38 | 0 | 3496.38 | 142126 | -77445.1 | 30 | 32 | 142126 | -1077445.1
11 | 10 | 12 | 8 | 4.6114 | 0 | 42.7453 | 0 | 11.4343 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 0 | 82.0582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3498.5 | 0 | 3498.5 | 141560 | -70410.8 | 30 | 33 | 141560 | -1070410.8
11 | 10 | 13 | 8 | 4.1669 | 0 | 42.7453 | 0 | 11.4236 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 0 | 81.6027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500.45 | 0 | 3500.45 | 141008 | -68972.1 | 31 | 34 | 141008 | -1068972.1
11 | 10 | 14 | 8 | 4.1519 | 0 | 42.7453 | 0 | 11.4123 | 0 | 5.903 | 17.3638 | 0 | 0 | 0 | 0 | 81.5762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502.29 | 0 | 3502.29 | 140425 | -59358.1 | 31 | 34 | 140425 | -1059358.1
11 | 10 | 15 | 8 | 4.1566 | 0 | 42.7453 | 0 | 11.406 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 0 | 81.5745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3504.02 | 0 | 3504.02 | 140092 | -52098.2 | 32 | 35 | 140092 | -1052098.2
11 | 10 | 16 | 8 | 4.2967 | 0 | 42.7453 | 0 | 11.4211 | 0 | 5.9029 | 17.3638 | 0 | 0 | 0 | 0 | 81.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3505.78 | 0 | 3505.78 | 140050 | -58121.1 | 31 | 34 | 140050 | -1058121.1
11 | 10 | 17 | 8 | 6.0593 | 0 | 42.7453 | 0 | 11.2969 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.7672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3507.34 | 0 | 3507.34 | 138468 | -79413.3 | 30 | 32 | 138468 | -1079413.3
11 | 10 | 18 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.1752 | 0 | 5.9012 | 17.3638 | 0 | 0 | 0 | 6.4 | 90.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3508.9 | 0 | 3508.9 | 137354 | -98983.2 | 29 | 31 | 137354 | -1098983.2
11 | 10 | 19 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.0884 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3510.65 | 0 | 3510.65 | 136636 | -109958 | 30 | 32 | 136636 | -1109958
11 | 10 | 20 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.0772 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3512.45 | 0 | 3512.45 | 136523 | -114741 | 31 | 33 | 136523 | -1114741
11 | 10 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.015 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514.32 | 0 | 3514.32 | 135381 | -113171 | 31 | 34 | 135381 | -1113171
11 | 10 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 11.0375 | 0 | 5.9003 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3516.11 | 0 | 3516.11 | 135438 | -115529 | 31 | 34 | 135438 | -1115529
11 | 10 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.9686 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 6.4 | 90.0409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3517.8 | 0 | 3517.8 | 134384 | -115970 | 31 | 34 | 134384 | -1115970
11 | 10 | 24 | 8 | 6.6633 | 0 | 42.7453 | 0 | 10.9244 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 5.6 | 89.1964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3519.4 | 0 | 3519.4 | 133895 | -118916 | 31 | 34 | 133895 | -1118916
11 | 11 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8768 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9075.66 | 0 | 9075.66 | 133491 | -121362 | 32 | 34 | 133491 | -1121362
11 | 11 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8522 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9077.19 | 0 | 9077.19 | 133313 | -126869 | 32 | 34 | 133313 | -1126869
11 | 11 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.817 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9078.5 | 0 | 9078.5 | 132730 | -130009 | 32 | 34 | 132730 | -1130009
11 | 11 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7956 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9079.91 | 0 | 9079.91 | 132410 | -132189 | 32 | 34 | 132410 | -1132189
11 | 11 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7712 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9081.29 | 0 | 9081.29 | 132070 | -131702 | 32 | 35 | 132070 | -1131702
11 | 11 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8123 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9082.63 | 0 | 9082.63 | 132375 | -132412 | 32 | 35 | 132375 | -1132412
11 | 11 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.761 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9083.96 | 0 | 9083.96 | 131469 | -131462 | 33 | 35 | 131469 | -1131462
11 | 11 | 8 | 6 | 5.9043 | 0 | 42.7453 | 56.2592 | 0 | 0 | 6.2233 | 19.3256 | 0 | 0 | 0 | 0.8 | 131.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9085.26 | 0 | 9085.26 | 123997 | -923000 | 33 | 35 | 123997 | -1923000
11 | 11 | 9 | 6 | 5.3665 | 0 | 42.7453 | 46.5259 | 0 | 0 | 6.2299 | 19.0173 | 0 | 0 | 0 | 0 | 119.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9086.31 | 0 | 9086.31 | 134562 | -783506 | 33 | 35 | 134562 | -1783506
11 | 11 | 10 | 6 | 5.5445 | 0 | 42.7453 | 37.0393 | 0 | 0 | 6.2382 | 18.8896 | 0 | 0 | 0 | 0 | 110.457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9068.13 | 0 | 9068.13 | 154966 | -659897 | 33 | 36 | 154966 | -1659897
11 | 11 | 11 | 6 | 5.5534 | 0 | 42.7453 | 32.9097 | 0 | 0 | 6.24 | 18.8896 | 0 | 0 | 0 | 0 | 106.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9065.34 | 0 | 9065.34 | 161317 | -594416 | 34 | 38 | 161317 | -1594416
11 | 11 | 12 | 6 | 6.1059 | 0 | 42.7453 | 31.0795 | 0 | 0 | 6.2387 | 18.8896 | 0 | 0 | 0 | 0 | 105.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9063.09 | 0 | 9063.09 | 171446 | -571803 | 34 | 39 | 171446 | -1571803
11 | 11 | 13 | 6 | 6.1993 | 0 | 42.7453 | 30.0398 | 0 | 0 | 6.2363 | 18.8896 | 0 | 0 | 0 | 0 | 104.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9061.81 | 0 | 9061.81 | 167693 | -561116 | 34 | 37 | 167693 | -1561116
11 | 11 | 14 | 6 | 6.4769 | 0 | 42.7453 | 29.5013 | 0 | 0 | 6.2339 | 18.8896 | 0 | 0 | 0 | 0 | 103.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9060.86 | 0 | 9060.86 | 157269 | -554815 | 34 | 36 | 157269 | -1554815
11 | 11 | 15 | 6 | 6.3161 | 0 | 42.7453 | 0 | 8.7391 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 0 | 76.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9060.12 | 0 | 9060.12 | 118377 | -9470.54 | 33 | 34 | 118377 | -1009470.54
11 | 11 | 16 | 6 | 7.6077 | 0 | 42.7453 | 0 | 9.0544 | 0 | 5.8975 | 12.8287 | 0 | 0 | 0 | 0 | 78.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9059.69 | 0 | 9059.69 | 118187 | -16309.1 | 31 | 32 | 118187 | -1016309.1
11 | 11 | 17 | 6 | 8.6213 | 0 | 42.7453 | 0 | 10.3562 | 0 | 5.8972 | 15.3158 | 0 | 0 | 0 | 2.4 | 85.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9063.46 | 0 | 9063.46 | 124994 | -34190.6 | 30 | 31 | 124994 | -1034190.6
11 | 11 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0426 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9067.1 | 0 | 9067.1 | 135373 | -69412.7 | 28 | 29 | 135373 | -1069412.7
11 | 11 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7786 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9070.18 | 0 | 9070.18 | 132777 | -91586.4 | 27 | 28 | 132777 | -1091586.4
11 | 11 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6232 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9073.29 | 0 | 9073.29 | 131559 | -116287 | 25 | 26 | 131559 | -1116287
11 | 11 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.4987 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9075.86 | 0 | 9075.86 | 130743 | -131455 | 24 | 25 | 130743 | -1131455
11 | 11 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3929 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9078.31 | 0 | 9078.31 | 130156 | -145891 | 23 | 24 | 130156 | -1145891
11 | 11 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.3118 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.5157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9080.45 | 0 | 9080.45 | 129646 | -153875 | 22 | 24 | 129646 | -1153875
11 | 11 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.2458 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9082.56 | 0 | 9082.56 | 129135 | -163970 | 21 | 23 | 129135 | -1163970
11 | 12 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.1501 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3529.84 | 0 | 3529.84 | 128410 | -174267 | 20 | 22 | 128410 | -1174267
11 | 12 | 2 | 7 | 5.1054 | 0 | 42.7453 | 10.7149 | 0 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.6288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531.81 | 0 | 3531.81 | 127818 | -193048 | 19 | 20 | 127818 | -1193048
11 | 12 | 3 | 7 | 5.1054 | 0 | 42.7453 | 11.3933 | 0 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.3124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.89 | 0 | 3533.89 | 127284 | -203518 | 17 | 19 | 127284 | -1203518
11 | 12 | 4 | 7 | 5.1054 | 0 | 42.7453 | 12.124 | 0 | 0 | 5.9127 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3535.87 | 0 | 3535.87 | 126841 | -217374 | 17 | 18 | 126841 | -1217374
11 | 12 | 5 | 7 | 5.1054 | 0 | 42.7453 | 12.7652 | 0 | 0 | 5.9207 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3537.85 | 0 | 3537.85 | 126319 | -226422 | 15 | 16 | 126319 | -1226422
11 | 12 | 6 | 7 | 5.1054 | 0 | 42.7453 | 13.5345 | 0 | 0 | 5.9322 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3539.85 | 0 | 3539.85 | 125801 | -240932 | 14 | 15 | 125801 | -1240932
11 | 12 | 7 | 7 | 5.1054 | 0 | 42.7453 | 13.9942 | 0 | 0 | 5.9371 | 17.3638 | 0 | 0 | 0 | 3.2 | 88.3457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3541.81 | 0 | 3541.81 | 125512 | -245665 | 16 | 17 | 125512 | -1245665
11 | 12 | 8 | 7 | 4.157 | 0 | 42.7453 | 12.5512 | 0 | 0 | 5.9069 | 17.3638 | 0 | 0 | 0 | 0.8 | 83.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3543.71 | 0 | 3543.71 | 125485 | -215987 | 17 | 18 | 125485 | -1215987
11 | 12 | 9 | 7 | 3.9402 | 0 | 42.7453 | 10.0236 | 0 | 0 | 5.8909 | 17.3638 | 0 | 0 | 0 | 0 | 79.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3545.59 | 0 | 3545.59 | 125844 | -172529 | 18 | 20 | 125844 | -1172529
11 | 12 | 10 | 7 | 4.2265 | 0 | 42.7453 | 0 | 9.9637 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 0 | 80.1962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3547.38 | 0 | 3547.38 | 128782 | -147030 | 20 | 22 | 128782 | -1147030
11 | 12 | 11 | 7 | 4.1732 | 0 | 42.7453 | 0 | 9.9694 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 0 | 80.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3548.87 | 0 | 3548.87 | 127872 | -130343 | 22 | 24 | 127872 | -1130343
11 | 12 | 12 | 7 | 4.157 | 0 | 42.7453 | 0 | 10.2253 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3549.9 | 0 | 3549.9 | 130655 | -126682 | 23 | 26 | 130655 | -1126682
11 | 12 | 13 | 7 | 4.1537 | 0 | 42.7453 | 0 | 10.2388 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 0 | 80.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3550.73 | 0 | 3550.73 | 129660 | -117566 | 25 | 28 | 129660 | -1117566
11 | 12 | 14 | 7 | 4.1727 | 0 | 42.7453 | 0 | 10.3404 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3551.37 | 0 | 3551.37 | 129966 | -111329 | 26 | 29 | 129966 | -1111329
11 | 12 | 15 | 7 | 4.21 | 0 | 42.7453 | 0 | 10.4023 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 0 | 80.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3552 | 0 | 3552 | 129932 | -102817 | 26 | 31 | 129932 | -1102817
11 | 12 | 16 | 7 | 4.249 | 0 | 42.7453 | 0 | 10.5341 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 0 | 80.7903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3552.49 | 0 | 3552.49 | 130986 | -103471 | 26 | 30 | 130986 | -1103471
11 | 12 | 17 | 7 | 6.1982 | 0 | 42.7453 | 0 | 10.3217 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 2.4 | 84.9263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3553.23 | 0 | 3553.23 | 127812 | -109204 | 25 | 28 | 127812 | -1109204
11 | 12 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.1602 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3554.05 | 0 | 3554.05 | 126124 | -131845 | 24 | 27 | 126124 | -1131845
11 | 12 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.0752 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3555.19 | 0 | 3555.19 | 125339 | -152564 | 25 | 27 | 125339 | -1152564
11 | 12 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.0556 | 0 | 5.8934 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.9214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3556.64 | 0 | 3556.64 | 125264 | -167993 | 25 | 28 | 125264 | -1167993
11 | 12 | 21 | 7 | 6.6633 | 0 | 42.7453 | 10.1667 | 0 | 0 | 5.89 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3558.09 | 0 | 3558.09 | 124972 | -175055 | 25 | 28 | 124972 | -1175055
11 | 12 | 22 | 7 | 6.6633 | 0 | 42.7453 | 10.2532 | 0 | 0 | 5.8888 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3559.21 | 0 | 3559.21 | 125035 | -176350 | 27 | 30 | 125035 | -1176350
11 | 12 | 23 | 7 | 6.6633 | 0 | 42.7453 | 10.3076 | 0 | 0 | 5.888 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3560.12 | 0 | 3560.12 | 125592 | -176525 | 28 | 31 | 125592 | -1176525
11 | 12 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.0766 | 0 | 5.8882 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.3372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3560.96 | 0 | 3560.96 | 124862 | -171554 | 28 | 33 | 124862 | -1171554
11 | 13 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1537 | 0 | 5.8933 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9116.46 | 0 | 9116.46 | 125591 | -167420 | 29 | 33 | 125591 | -1167420
11 | 13 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1495 | 0 | 5.8896 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9117.19 | 0 | 9117.19 | 125313 | -168404 | 29 | 33 | 125313 | -1168404
11 | 13 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1703 | 0 | 5.8901 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9117.38 | 0 | 9117.38 | 125524 | -171640 | 29 | 33 | 125524 | -1171640
11 | 13 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.1623 | 0 | 5.8886 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9117.9 | 0 | 9117.9 | 125350 | -172847 | 29 | 33 | 125350 | -1172847
11 | 13 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.4006 | 0 | 5.8917 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10102.4 | 0 | 10102.4 | 128716 | -173022 | 30 | 33 | 128716 | -1173022
11 | 13 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.8215 | 0 | 5.9399 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24228.2 | 0 | 24228.2 | 176366 | -134663 | 29 | 33 | 176366 | -1134663
11 | 13 | 7 | 1 | 49.0171 | 0 | 140.608 | 48.3507 | 0 | 0 | 6.2225 | 19.2733 | 0 | 0 | 0 | 3.2 | 266.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71383.9 | 0 | 71383.9 | 311760 | -845897 | 31 | 34 | 311760 | -1845897
11 | 13 | 8 | 1 | 45.952 | 0 | 168.222 | 39.4543 | 0 | 0 | 6.2345 | 19.1191 | 0 | 0 | 0 | 0.8 | 279.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86650.4 | 0 | 86650.4 | 389352 | -720125 | 32 | 36 | 389352 | -1720125
11 | 13 | 9 | 1 | 40.0577 | 0 | 173.795 | 26.8536 | 0 | 0 | 6.2474 | 19.0363 | 0 | 0 | 0 | 0 | 265.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119846 | 0 | 119846 | 401642 | -537094 | 33 | 37 | 401642 | -1537094
11 | 13 | 10 | 1 | 40.7063 | 0 | 172.186 | 0 | 27.2837 | 0 | 6.2772 | 19.0363 | 0 | 0 | 0 | 0 | 265.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140985 | 0 | 140985 | 416693 | -438731 | 35 | 40 | 416693 | -1438731
11 | 13 | 11 | 1 | 41.2433 | 0 | 163.102 | 0 | 28.2395 | 0 | 6.3035 | 19.0363 | 0 | 0 | 0 | 0 | 257.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143997 | 0 | 143997 | 420284 | -375223 | 36 | 43 | 420284 | -1375223
11 | 13 | 12 | 1 | 40.7983 | 0 | 149.692 | 0 | 29.5198 | 0 | 6.324 | 19.0363 | 0 | 0 | 0 | 0 | 245.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143994 | 0 | 143994 | 423112 | -315775 | 37 | 46 | 423112 | -1315775
11 | 13 | 13 | 1 | 39.8522 | 0 | 150.207 | 0 | 26.8564 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 242.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143991 | 0 | 143991 | 382347 | -256956 | 38 | 47 | 382347 | -1256956
11 | 13 | 14 | 1 | 41.3261 | 0 | 165.698 | 0 | 31.4729 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143988 | 0 | 143988 | 439840 | -229490 | 39 | 48 | 439840 | -1229490
11 | 13 | 15 | 1 | 40.783 | 0 | 172.702 | 0 | 32.976 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142126 | 0 | 142126 | 453757 | -212392 | 40 | 49 | 453757 | -1212392
11 | 13 | 16 | 1 | 41.6417 | 0 | 173.986 | 0 | 32.3254 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129215 | 0 | 129215 | 457486 | -236899 | 39 | 46 | 457486 | -1236899
11 | 13 | 17 | 1 | 53.7108 | 0 | 169.782 | 0 | 31.277 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 282.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105496 | 0 | 105496 | 456222 | -285210 | 38 | 43 | 456222 | -1285210
11 | 13 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 25.6605 | 0 | 6.3168 | 19.0363 | 0 | 0 | 0 | 6.4 | 259.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79144.4 | 0 | 79144.4 | 395311 | -331179 | 36 | 40 | 395311 | -1331179
11 | 13 | 19 | 1 | 34.11 | 0 | 93.4203 | 22.5361 | 0 | 0 | 6.2924 | 19.0363 | 0 | 0 | 0 | 7.2 | 182.595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49048.5 | 0 | 49048.5 | 322537 | -421252 | 35 | 38 | 322537 | -1421252
11 | 13 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 8.8339 | 0 | 5.4859 | 12.9754 | 0 | 0 | 0 | 7.2 | 121.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35128.2 | 0 | 35128.2 | 178041 | 0 | 34 | 37 | 178041 | -1000000
11 | 13 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 10.7094 | 0 | 5.9049 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31193.2 | 0 | 31193.2 | 158979 | -11201.8 | 33 | 35 | 158979 | -1011201.8
11 | 13 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.0222 | 0 | 5.9025 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19194.9 | 0 | 19194.9 | 145740 | -16978.6 | 31 | 33 | 145740 | -1016978.6
11 | 13 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 10.8137 | 0 | 5.8994 | 12.9754 | 0 | 0 | 0 | 6.4 | 91.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10390.2 | 0 | 10390.2 | 134618 | -21039.2 | 30 | 30 | 134618 | -1021039.2
11 | 13 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 12.2786 | 0 | 5.911 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9059.67 | 0 | 9059.67 | 149496 | -46173.7 | 28 | 28 | 149496 | -1046173.7
11 | 14 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 12.6419 | 0 | 5.9151 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.4752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9063.09 | 0 | 9063.09 | 152254 | -57735.6 | 28 | 29 | 152254 | -1057735.6
11 | 14 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.6377 | 0 | 5.9005 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9066.23 | 0 | 9066.23 | 144054 | -56298.2 | 29 | 29 | 144054 | -1056298.2
11 | 14 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.6561 | 0 | 5.9049 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9068.79 | 0 | 9068.79 | 143066 | -78813.4 | 29 | 30 | 143066 | -1078813.4
11 | 14 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4509 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9070.45 | 0 | 9070.45 | 141011 | -92067.7 | 27 | 28 | 141011 | -1092067.7
11 | 14 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.5235 | 0 | 5.9042 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10056.6 | 0 | 10056.6 | 143088 | -106976 | 25 | 27 | 143088 | -1106976
11 | 14 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.8472 | 0 | 5.9649 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24183.8 | 0 | 24183.8 | 190255 | -100709 | 23 | 25 | 190255 | -1100709
11 | 14 | 7 | 2 | 49.0171 | 0 | 140.608 | 43.0497 | 0 | 0 | 6.2203 | 19.0758 | 0 | 0 | 0 | 3.2 | 261.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71340.8 | 0 | 71340.8 | 320469 | -800249 | 24 | 26 | 320469 | -1800249
11 | 14 | 8 | 2 | 45.0374 | 0 | 168.222 | 38.9688 | 0 | 0 | 6.2378 | 19.0363 | 0 | 0 | 0 | 0.8 | 278.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86608.7 | 0 | 86608.7 | 382656 | -711905 | 25 | 28 | 382656 | -1711905
11 | 14 | 9 | 2 | 40.2165 | 0 | 173.795 | 27.0502 | 0 | 0 | 6.2475 | 19.0363 | 0 | 0 | 0 | 0 | 266.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119820 | 0 | 119820 | 401320 | -545958 | 25 | 29 | 401320 | -1545958
11 | 14 | 10 | 2 | 40.7732 | 0 | 172.186 | 0 | 25.3608 | 0 | 6.2732 | 19.0363 | 0 | 0 | 0 | 0 | 263.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140960 | 0 | 140960 | 399767 | -464296 | 27 | 31 | 399767 | -1464296
11 | 14 | 11 | 2 | 41.2356 | 0 | 163.102 | 0 | 26.1772 | 0 | 6.2978 | 19.0363 | 0 | 0 | 0 | 0 | 255.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143974 | 0 | 143974 | 393012 | -418488 | 29 | 34 | 393012 | -1418488
11 | 14 | 12 | 2 | 40.7891 | 0 | 149.692 | 0 | 25.1459 | 0 | 25.3194 | 19.0363 | 0 | 0 | 0 | 0 | 259.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143972 | 0 | 143972 | 379436 | -352844 | 30 | 36 | 379436 | -1352844
11 | 14 | 13 | 2 | 39.8419 | 0 | 150.207 | 0 | 22.7794 | 0 | 25.319 | 19.0363 | 0 | 0 | 0 | 0 | 257.184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143970 | 0 | 143970 | 355362 | -321378 | 31 | 37 | 355362 | -1321378
11 | 14 | 14 | 2 | 41.3263 | 0 | 165.698 | 0 | 25.6991 | 0 | 25.3314 | 19.0363 | 0 | 0 | 0 | 0 | 277.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143967 | 0 | 143967 | 398992 | -283625 | 31 | 38 | 398992 | -1283625
11 | 14 | 15 | 2 | 40.724 | 0 | 172.702 | 0 | 27.9964 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 285.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142106 | 0 | 142106 | 428217 | -279454 | 32 | 39 | 428217 | -1279454
11 | 14 | 16 | 2 | 41.2808 | 0 | 173.986 | 0 | 26.082 | 0 | 25.3298 | 19.0363 | 0 | 0 | 0 | 0 | 285.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129196 | 0 | 129196 | 409856 | -305938 | 31 | 36 | 409856 | -1305938
11 | 14 | 17 | 2 | 54.224 | 0 | 169.782 | 0 | 25.7388 | 0 | 25.3104 | 19.0363 | 0 | 0 | 0 | 2.4 | 296.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105479 | 0 | 105479 | 405066 | -369641 | 29 | 33 | 405066 | -1369641
11 | 14 | 18 | 2 | 49.7836 | 0 | 152.497 | 0 | 24.9793 | 0 | 25.2819 | 19.0363 | 0 | 0 | 0 | 6.4 | 277.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79128.9 | 0 | 79128.9 | 393496 | -467968 | 27 | 30 | 393496 | -1467968
11 | 14 | 19 | 2 | 34.11 | 0 | 93.4203 | 28.3711 | 0 | 0 | 6.2823 | 19.0363 | 0 | 0 | 0 | 7.2 | 188.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49034.1 | 0 | 49034.1 | 306946 | -500578 | 27 | 30 | 306946 | -1500578
11 | 14 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.2303 | 0 | 5.9511 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35114.3 | 0 | 35114.3 | 181682 | -12316.4 | 27 | 29 | 181682 | -1012316.4
11 | 14 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.41 | 0 | 5.9177 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31178.5 | 0 | 31178.5 | 162618 | -17356.3 | 26 | 29 | 162618 | -1017356.3
11 | 14 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 12.1566 | 0 | 5.9102 | 12.9754 | 0 | 0 | 0 | 7.2 | 100.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19179.8 | 0 | 19179.8 | 149233 | -22697 | 26 | 29 | 149233 | -1022697
11 | 14 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.9412 | 0 | 5.9216 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.3038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10375.4 | 0 | 10375.4 | 160902 | -38573.4 | 26 | 29 | 160902 | -1038573.4
11 | 14 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 12.3484 | 0 | 5.913 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9045.09 | 0 | 9045.09 | 153020 | -53630.3 | 26 | 29 | 153020 | -1053630.3
11 | 15 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 12.0776 | 0 | 5.9098 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9049.12 | 0 | 9049.12 | 149968 | -63470.6 | 27 | 30 | 149968 | -1063470.6
11 | 15 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.913 | 0 | 5.908 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9052.35 | 0 | 9052.35 | 148049 | -72121.2 | 28 | 31 | 148049 | -1072121.2
11 | 15 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.8077 | 0 | 5.9069 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9055.13 | 0 | 9055.13 | 146595 | -78932.2 | 29 | 32 | 146595 | -1078932.2
11 | 15 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.7311 | 0 | 5.9061 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9057.53 | 0 | 9057.53 | 145457 | -82227 | 30 | 33 | 145457 | -1082227
11 | 15 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.9196 | 0 | 5.908 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10043.7 | 0 | 10043.7 | 147897 | -83121.8 | 31 | 34 | 147897 | -1083121.8
11 | 15 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 15.6399 | 0 | 5.986 | 17.5105 | 0 | 0 | 0 | 4.8 | 138.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24170.8 | 0 | 24170.8 | 198834 | -65032.6 | 32 | 35 | 198834 | -1065032.6
11 | 15 | 7 | 3 | 49.0171 | 0 | 140.608 | 30.2907 | 0 | 0 | 6.245 | 19.0363 | 0 | 0 | 0 | 3.2 | 248.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71327.7 | 0 | 71327.7 | 323763 | -587510 | 33 | 36 | 323763 | -1587510
11 | 15 | 8 | 3 | 47.4734 | 0 | 168.222 | 27.1655 | 0 | 0 | 6.2631 | 19.0363 | 0 | 0 | 0 | 0.8 | 268.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86595.4 | 0 | 86595.4 | 398052 | -524787 | 35 | 38 | 398052 | -1524787
11 | 15 | 9 | 3 | 40.3597 | 0 | 173.795 | 0 | 26.907 | 0 | 6.2968 | 19.0363 | 0 | 0 | 0 | 0 | 266.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119807 | 0 | 119807 | 417036 | -373703 | 36 | 39 | 417036 | -1373703
11 | 15 | 10 | 3 | 40.7689 | 0 | 172.186 | 0 | 28.5598 | 0 | 6.3154 | 19.0363 | 0 | 0 | 0 | 0 | 266.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140947 | 0 | 140947 | 432146 | -330225 | 37 | 41 | 432146 | -1330225
11 | 15 | 11 | 3 | 41.2274 | 0 | 163.102 | 0 | 29.9474 | 0 | 25.3232 | 19.0363 | 0 | 0 | 0 | 0 | 278.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143961 | 0 | 143961 | 440649 | -318528 | 39 | 44 | 440649 | -1318528
11 | 15 | 12 | 3 | 40.7899 | 0 | 149.692 | 0 | 30.4088 | 0 | 6.3288 | 19.0363 | 0 | 0 | 0 | 0 | 246.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143957 | 0 | 143957 | 434865 | -285411 | 41 | 46 | 434865 | -1285411
11 | 15 | 13 | 3 | 39.8497 | 0 | 150.207 | 0 | 27.9292 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143955 | 0 | 143955 | 394312 | -207806 | 42 | 48 | 394312 | -1207806
11 | 15 | 14 | 3 | 41.3344 | 0 | 165.698 | 0 | 31.8815 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143952 | 0 | 143952 | 441708 | -192140 | 43 | 49 | 441708 | -1192140
11 | 15 | 15 | 3 | 40.727 | 0 | 172.702 | 0 | 34.2145 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 273.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142092 | 0 | 142092 | 459825 | -153912 | 44 | 51 | 459825 | -1153912
11 | 15 | 16 | 3 | 41.1781 | 0 | 173.986 | 0 | 33.9564 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129183 | 0 | 129183 | 458522 | -152696 | 44 | 50 | 458522 | -1152696
11 | 15 | 17 | 3 | 55.6966 | 0 | 169.782 | 0 | 33.7113 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105464 | 0 | 105464 | 463558 | -179078 | 43 | 48 | 463558 | -1179078
11 | 15 | 18 | 3 | 49.7836 | 0 | 152.497 | 0 | 30.7056 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 264.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79112.2 | 0 | 79112.2 | 436126 | -217482 | 43 | 47 | 436126 | -1217482
11 | 15 | 19 | 3 | 34.11 | 0 | 93.4203 | 0 | 25.675 | 0 | 6.3257 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49016.6 | 0 | 49016.6 | 360369 | -306065 | 41 | 45 | 360369 | -1306065
11 | 15 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.1681 | 0 | 5.4902 | 8.818 | 0 | 0 | 0 | 7.2 | 117.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35096 | 0 | 35096 | 184841 | 0 | 40 | 42 | 184841 | -1000000
11 | 15 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 12.16 | 0 | 5.917 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31160.7 | 0 | 31160.7 | 165396 | -10221.2 | 39 | 40 | 165396 | -1010221.2
11 | 15 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.5409 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19161.3 | 0 | 19161.3 | 151920 | 0 | 39 | 40 | 151920 | -1000000
11 | 15 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.7642 | 0 | 5.905 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10355.6 | 0 | 10355.6 | 140795 | -19466 | 39 | 40 | 140795 | -1019466
11 | 15 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8055 | 0 | 5.8994 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9024.76 | 0 | 9024.76 | 135969 | -8784.4 | 39 | 40 | 135969 | -1008784.4
11 | 16 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.8484 | 0 | 5.8974 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9027.56 | 0 | 9027.56 | 136395 | -14448 | 39 | 40 | 136395 | -1014448
11 | 16 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.2457 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.8316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9030.04 | 0 | 9030.04 | 133436 | -12684.1 | 39 | 40 | 133436 | -1012684.1
11 | 16 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.6055 | 0 | 5.9014 | 14.8767 | 0 | 0 | 0 | 4.8 | 89.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9032.14 | 0 | 9032.14 | 148916 | -16287.9 | 39 | 40 | 148916 | -1016287.9
11 | 16 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 9.4946 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 86.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9034.08 | 0 | 9034.08 | 131712 | -15823.2 | 38 | 40 | 131712 | -1015823.2
11 | 16 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.4183 | 0 | 5.9081 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10019.9 | 0 | 10019.9 | 157638 | -26248.3 | 38 | 39 | 157638 | -1026248.3
11 | 16 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 13.5814 | 0 | 5.9511 | 15.0234 | 0 | 0 | 0 | 4.8 | 133.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24146.8 | 0 | 24146.8 | 195566 | -19275 | 38 | 39 | 195566 | -1019275
11 | 16 | 7 | 4 | 49.0171 | 0 | 140.608 | 0 | 23.0301 | 0 | 6.2863 | 19.0363 | 0 | 0 | 0 | 3.2 | 241.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71304 | 0 | 71304 | 326100 | -395155 | 38 | 39 | 326100 | -1395155
11 | 16 | 8 | 4 | 46.1288 | 0 | 168.222 | 0 | 27.6052 | 0 | 6.2884 | 19.0363 | 0 | 0 | 0 | 0.8 | 268.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86571.4 | 0 | 86571.4 | 419613 | -405835 | 39 | 40 | 419613 | -1405835
11 | 16 | 9 | 4 | 40.2035 | 0 | 173.795 | 0 | 28.6734 | 0 | 6.3212 | 19.0363 | 0 | 0 | 0 | 0 | 268.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119788 | 0 | 119788 | 434413 | -301714 | 39 | 40 | 434413 | -1301714
11 | 16 | 10 | 4 | 40.7936 | 0 | 172.186 | 0 | 33.5878 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140929 | 0 | 140929 | 479641 | -247243 | 42 | 45 | 479641 | -1247243
11 | 16 | 11 | 4 | 41.2308 | 0 | 163.102 | 0 | 32.4261 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143943 | 0 | 143943 | 443856 | -185733 | 44 | 49 | 443856 | -1185733
11 | 16 | 12 | 4 | 40.7934 | 0 | 149.692 | 0 | 33.0766 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 248.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143940 | 0 | 143940 | 426546 | -129733 | 46 | 54 | 426546 | -1129733
11 | 16 | 13 | 4 | 39.8419 | 0 | 150.207 | 0 | 30.7585 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143937 | 0 | 143937 | 411900 | -98660.5 | 47 | 55 | 411900 | -1098660.5
11 | 16 | 14 | 4 | 41.3229 | 0 | 165.698 | 0 | 31.7304 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143934 | 0 | 143934 | 473583 | -70710.6 | 47 | 57 | 473583 | -1070710.6
11 | 16 | 15 | 4 | 40.728 | 0 | 172.702 | 0 | 31.2498 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 270.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142074 | 0 | 142074 | 497419 | -46338.4 | 48 | 58 | 497419 | -1046338.4
11 | 16 | 16 | 4 | 43.2506 | 0 | 173.986 | 0 | 25.981 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 287.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129166 | 0 | 129166 | 455791 | -56027.3 | 46 | 53 | 455791 | -1056027.3
11 | 16 | 17 | 4 | 55.7322 | 0 | 169.782 | 0 | 27.154 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 2.4 | 299.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105449 | 0 | 105449 | 460684 | -107147 | 43 | 48 | 460684 | -1107147
11 | 16 | 18 | 4 | 49.7836 | 0 | 152.497 | 0 | 27.0835 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 6.4 | 280.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79098 | 0 | 79098 | 428150 | -180174 | 40 | 43 | 428150 | -1180174
11 | 16 | 19 | 4 | 34.11 | 0 | 93.4203 | 0 | 24.8434 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49003.5 | 0 | 49003.5 | 350324 | -238223 | 40 | 43 | 350324 | -1238223
11 | 16 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 9.2289 | 0 | 5.4911 | 8.818 | 0 | 0 | 0 | 7.2 | 117.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35084.4 | 0 | 35084.4 | 186366 | 0 | 40 | 42 | 186366 | -1000000
11 | 16 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 8.2272 | 0 | 5.4805 | 8.818 | 0 | 0 | 0 | 7.2 | 103.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31149.2 | 0 | 31149.2 | 166843 | 0 | 40 | 42 | 166843 | -1000000
11 | 16 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 10.5066 | 0 | 5.9023 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19146.9 | 0 | 19146.9 | 153370 | -7939.85 | 40 | 42 | 153370 | -1007939.85
11 | 16 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 7.0933 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 6.4 | 83.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10340.3 | 0 | 10340.3 | 142162 | 0 | 40 | 41 | 142162 | -1000000
11 | 16 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.038 | 0 | 5.9006 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9008.72 | 0 | 9008.72 | 137261 | -15617.4 | 40 | 41 | 137261 | -1015617.4
11 | 17 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.7834 | 0 | 5.8995 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9011.28 | 0 | 9011.28 | 135536 | -6438.61 | 39 | 41 | 135536 | -1006438.61
11 | 17 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.8178 | 0 | 5.8993 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9013.42 | 0 | 9013.42 | 136333 | -11863.9 | 39 | 40 | 136333 | -1011863.9
11 | 17 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 6.701 | 0 | 5.9002 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9015.53 | 0 | 9015.53 | 133719 | -10499.1 | 39 | 40 | 133719 | -1010499.1
11 | 17 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.9999 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9017.4 | 0 | 9017.4 | 132853 | -12725 | 38 | 39 | 132853 | -1012725
11 | 17 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 10.3276 | 0 | 5.9015 | 15.0234 | 0 | 0 | 0 | 4.8 | 92.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10003.2 | 0 | 10003.2 | 153606 | -14235.2 | 38 | 39 | 153606 | -1014235.2
11 | 17 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.6726 | 0 | 5.958 | 15.0234 | 0 | 0 | 0 | 4.8 | 133.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24130.2 | 0 | 24130.2 | 202476 | -16580.2 | 38 | 38 | 202476 | -1016580.2
11 | 17 | 7 | 5 | 49.0171 | 0 | 140.608 | 0 | 22.7276 | 0 | 6.3036 | 19.0363 | 0 | 0 | 0 | 3.2 | 240.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71287.1 | 0 | 71287.1 | 326933 | -330581 | 38 | 39 | 326933 | -1330581
11 | 17 | 8 | 5 | 51.0385 | 0 | 168.222 | 0 | 26.7173 | 0 | 6.2995 | 19.0363 | 0 | 0 | 0 | 0.8 | 272.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86554.6 | 0 | 86554.6 | 409343 | -354133 | 39 | 40 | 409343 | -1354133
11 | 17 | 9 | 5 | 42.1929 | 0 | 173.795 | 0 | 29.0095 | 0 | 6.3185 | 19.0363 | 0 | 0 | 0 | 0 | 270.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119774 | 0 | 119774 | 438216 | -289453 | 40 | 41 | 438216 | -1289453
11 | 17 | 10 | 5 | 40.8911 | 0 | 172.186 | 0 | 32.8293 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140916 | 0 | 140916 | 473052 | -252901 | 42 | 45 | 473052 | -1252901
11 | 17 | 11 | 5 | 41.2283 | 0 | 163.102 | 0 | 31.8591 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 261.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143931 | 0 | 143931 | 439308 | -181536 | 45 | 49 | 439308 | -1181536
11 | 17 | 12 | 5 | 40.7786 | 0 | 149.692 | 0 | 32.0849 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143929 | 0 | 143929 | 421800 | -129540 | 48 | 53 | 421800 | -1129540
11 | 17 | 13 | 5 | 39.8443 | 0 | 150.207 | 0 | 28.9546 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 244.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143927 | 0 | 143927 | 398376 | -140241 | 45 | 49 | 398376 | -1140241
11 | 17 | 14 | 5 | 41.3115 | 0 | 165.698 | 0 | 33.2132 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143925 | 0 | 143925 | 466701 | -167555 | 43 | 46 | 466701 | -1167555
11 | 17 | 15 | 5 | 45.5974 | 0 | 172.702 | 0 | 32.7103 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 276.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142066 | 0 | 142066 | 472928 | -194122 | 40 | 42 | 472928 | -1194122
11 | 17 | 16 | 5 | 50.2256 | 0 | 173.986 | 0 | 32.7429 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 282.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129159 | 0 | 129159 | 475625 | -200176 | 40 | 42 | 475625 | -1200176
11 | 17 | 17 | 5 | 56.7556 | 0 | 169.782 | 0 | 32.0898 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105443 | 0 | 105443 | 467217 | -218237 | 40 | 42 | 467217 | -1218237
11 | 17 | 18 | 5 | 49.7836 | 0 | 152.497 | 0 | 28.2075 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 262.257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79093.9 | 0 | 79093.9 | 422108 | -235578 | 40 | 42 | 422108 | -1235578
11 | 17 | 19 | 5 | 34.11 | 0 | 93.4203 | 0 | 22.5425 | 0 | 6.316 | 19.0363 | 0 | 0 | 0 | 7.2 | 182.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48999.8 | 0 | 48999.8 | 331506 | -310906 | 38 | 40 | 331506 | -1310906
11 | 17 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.1912 | 0 | 5.4906 | 8.818 | 0 | 0 | 0 | 7.2 | 117.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35080.4 | 0 | 35080.4 | 185845 | 0 | 36 | 39 | 185845 | -1000000
11 | 17 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 13.3006 | 0 | 5.9285 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31145 | 0 | 31145 | 166610 | -13158.8 | 34 | 37 | 166610 | -1013158.8
11 | 17 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 7.5912 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19143.2 | 0 | 19143.2 | 153019 | 0 | 33 | 36 | 153019 | -1000000
11 | 17 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.629 | 0 | 5.9045 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10337.3 | 0 | 10337.3 | 141785 | -23689.4 | 33 | 35 | 141785 | -1023689.4
11 | 17 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 6.8457 | 0 | 5.8991 | 12.9754 | 0 | 0 | 0 | 5.6 | 84.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9006.3 | 0 | 9006.3 | 136847 | -11522.6 | 31 | 34 | 136847 | -1011522.6
11 | 18 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8403 | 0 | 5.8998 | 12.8287 | 0 | 0 | 0 | 4.8 | 83.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9009.4 | 0 | 9009.4 | 136448 | -19668 | 30 | 32 | 136448 | -1019668
11 | 18 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.1173 | 0 | 5.9142 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.3223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9012.35 | 0 | 9012.35 | 160723 | -31779.6 | 28 | 31 | 160723 | -1031779.6
11 | 18 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.731 | 0 | 5.9177 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9015.72 | 0 | 9015.72 | 156606 | -39432.9 | 26 | 29 | 156606 | -1039432.9
11 | 18 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.4471 | 0 | 5.9142 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9019.19 | 0 | 9019.19 | 153975 | -46532.4 | 25 | 28 | 153975 | -1046532.4
11 | 18 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.1805 | 0 | 5.9112 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9022.6 | 0 | 9022.6 | 151642 | -70744.1 | 24 | 26 | 151642 | -1070744.1
11 | 18 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.9667 | 0 | 5.909 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9025.77 | 0 | 9025.77 | 149851 | -85577.2 | 23 | 25 | 149851 | -1085577.2
11 | 18 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7752 | 0 | 5.9072 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.85 | 0 | 9028.85 | 148373 | -97672.8 | 22 | 25 | 148373 | -1097672.8
11 | 18 | 8 | 6 | 5.524 | 0 | 42.7453 | 44.6136 | 0 | 0 | 6.2378 | 18.9777 | 0 | 0 | 0 | 0.8 | 118.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.81 | 0 | 9031.81 | 129024 | -768364 | 22 | 25 | 129024 | -1768364
11 | 18 | 9 | 6 | 5.1032 | 0 | 42.7453 | 39.4988 | 0 | 0 | 6.2366 | 18.8896 | 0 | 0 | 0 | 0 | 112.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9034.44 | 0 | 9034.44 | 129574 | -674025 | 22 | 25 | 129574 | -1674025
11 | 18 | 10 | 6 | 5.5461 | 0 | 42.7453 | 30.7429 | 0 | 0 | 6.2421 | 18.8896 | 0 | 0 | 0 | 0 | 104.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.78 | 0 | 9031.78 | 127063 | -557612 | 23 | 26 | 127063 | -1557612
11 | 18 | 11 | 6 | 5.5365 | 0 | 42.7453 | 27.3214 | 0 | 0 | 6.2413 | 18.8896 | 0 | 0 | 0 | 0 | 100.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.19 | 0 | 9029.19 | 126356 | -501634 | 23 | 27 | 126356 | -1501634
11 | 18 | 12 | 6 | 5.4937 | 0 | 42.7453 | 24.7047 | 0 | 0 | 6.2509 | 18.8896 | 0 | 0 | 0 | 0 | 98.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.98 | 0 | 9028.98 | 125761 | -462953 | 23 | 28 | 125761 | -1462953
11 | 18 | 13 | 6 | 5.4813 | 0 | 42.7453 | 23.3437 | 0 | 0 | 6.2562 | 18.8896 | 0 | 0 | 0 | 0 | 96.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.92 | 0 | 9028.92 | 125310 | -440910 | 24 | 29 | 125310 | -1440910
11 | 18 | 14 | 6 | 5.4907 | 0 | 42.7453 | 22.7728 | 0 | 0 | 6.2534 | 18.8896 | 0 | 0 | 0 | 0 | 96.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.15 | 0 | 9029.15 | 124733 | -435856 | 24 | 29 | 124733 | -1435856
11 | 18 | 15 | 6 | 5.5011 | 0 | 42.7453 | 0 | 10.3604 | 0 | 5.8973 | 12.8287 | 0 | 0 | 0 | 0 | 77.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.3 | 0 | 9029.3 | 125607 | -16526.2 | 24 | 30 | 125607 | -1016526.2
11 | 18 | 16 | 6 | 5.691 | 0 | 42.7453 | 0 | 10.2421 | 0 | 5.897 | 12.8287 | 0 | 0 | 0 | 0 | 77.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.83 | 0 | 9029.83 | 123892 | -21398.1 | 24 | 28 | 123892 | -1021398.1
11 | 18 | 17 | 6 | 8.2913 | 0 | 42.7453 | 0 | 10.899 | 0 | 5.8995 | 15.3158 | 0 | 0 | 0 | 2.4 | 85.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9032.6 | 0 | 9032.6 | 134035 | -37839.9 | 23 | 27 | 134035 | -1037839.9
11 | 18 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.8592 | 0 | 5.9077 | 17.3638 | 0 | 0 | 0 | 6.4 | 93.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9035.34 | 0 | 9035.34 | 148342 | -47579.9 | 21 | 25 | 148342 | -1047579.9
11 | 18 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.462 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9038.4 | 0 | 9038.4 | 143978 | -67405.8 | 21 | 24 | 143978 | -1067405.8
11 | 18 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2199 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9042.01 | 0 | 9042.01 | 141556 | -86036.7 | 20 | 22 | 141556 | -1086036.7
11 | 18 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0224 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9044.97 | 0 | 9044.97 | 139575 | -100894 | 19 | 21 | 139575 | -1100894
11 | 18 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.915 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.97 | 0 | 9047.97 | 138505 | -118080 | 18 | 20 | 138505 | -1118080
11 | 18 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8267 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9050.77 | 0 | 9050.77 | 137142 | -126405 | 18 | 20 | 137142 | -1126405
11 | 18 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8518 | 0 | 5.8999 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9053.49 | 0 | 9053.49 | 137143 | -134222 | 17 | 19 | 137143 | -1134222
11 | 19 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0189 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3501.27 | 0 | 3501.27 | 137562 | -139926 | 17 | 19 | 137562 | -1139926
11 | 19 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8901 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503.63 | 0 | 3503.63 | 134139 | -136513 | 17 | 18 | 134139 | -1136513
11 | 19 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0304 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3506.02 | 0 | 3506.02 | 135380 | -144096 | 17 | 18 | 135380 | -1144096
11 | 19 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8851 | 0 | 5.8993 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3507.84 | 0 | 3507.84 | 132664 | -148314 | 16 | 17 | 132664 | -1148314
11 | 19 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.6481 | 0 | 5.8985 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3509.7 | 0 | 3509.7 | 132020 | -161977 | 16 | 17 | 132020 | -1161977
11 | 19 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.382 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511.41 | 0 | 3511.41 | 131349 | -186090 | 15 | 16 | 131349 | -1186090
11 | 19 | 7 | 7 | 5.1054 | 0 | 42.7453 | 10.4226 | 0 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 3.2 | 84.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3513.06 | 0 | 3513.06 | 130837 | -185003 | 17 | 18 | 130837 | -1185003
11 | 19 | 8 | 7 | 4.4345 | 0 | 42.7453 | 0 | 10.2468 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0.8 | 81.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515.31 | 0 | 3515.31 | 131774 | -177745 | 18 | 20 | 131774 | -1177745
11 | 19 | 9 | 7 | 3.9281 | 0 | 42.7453 | 0 | 10.2111 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3517.55 | 0 | 3517.55 | 130854 | -135741 | 20 | 22 | 130854 | -1135741
11 | 19 | 10 | 7 | 4.2082 | 0 | 42.7453 | 0 | 10.4697 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 80.6853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3519.84 | 0 | 3519.84 | 133918 | -112517 | 23 | 25 | 133918 | -1112517
11 | 19 | 11 | 7 | 4.1724 | 0 | 42.7453 | 0 | 10.4812 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 0 | 80.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3521.79 | 0 | 3521.79 | 132890 | -95641.8 | 25 | 29 | 132890 | -1095641.8
11 | 19 | 12 | 7 | 4.1601 | 0 | 42.7453 | 0 | 10.8185 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 0 | 80.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3523.1 | 0 | 3523.1 | 136317 | -91360.2 | 27 | 32 | 136317 | -1091360.2
11 | 19 | 13 | 7 | 4.1513 | 0 | 42.7453 | 0 | 10.7643 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 0 | 80.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524.24 | 0 | 3524.24 | 133932 | -80452.8 | 28 | 33 | 133932 | -1080452.8
11 | 19 | 14 | 7 | 4.1522 | 0 | 42.7453 | 0 | 10.7955 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 0 | 80.9559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525.05 | 0 | 3525.05 | 133452 | -77492.4 | 28 | 33 | 133452 | -1077492.4
11 | 19 | 15 | 7 | 5.0443 | 0 | 42.7453 | 0 | 10.7182 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 81.7702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526.09 | 0 | 3526.09 | 132110 | -77677 | 28 | 34 | 132110 | -1077677
11 | 19 | 16 | 7 | 4.7434 | 0 | 42.7453 | 0 | 10.6951 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 81.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526.98 | 0 | 3526.98 | 131687 | -89974.6 | 28 | 33 | 131687 | -1089974.6
11 | 19 | 17 | 7 | 6.3551 | 0 | 42.7453 | 0 | 10.5657 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3528.35 | 0 | 3528.35 | 129995 | -99235.2 | 27 | 31 | 129995 | -1099235.2
11 | 19 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4594 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530.02 | 0 | 3530.02 | 129207 | -120472 | 26 | 30 | 129207 | -1120472
11 | 19 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3957 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531.51 | 0 | 3531.51 | 128804 | -134727 | 27 | 31 | 128804 | -1134727
11 | 19 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3945 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.14 | 0 | 3533.14 | 128758 | -136392 | 28 | 33 | 128758 | -1136392
11 | 19 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4005 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3534.73 | 0 | 3534.73 | 128322 | -134785 | 29 | 34 | 128322 | -1134785
11 | 19 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4252 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3536.25 | 0 | 3536.25 | 128152 | -133138 | 29 | 34 | 128152 | -1133138
11 | 19 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4299 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.4998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3537.63 | 0 | 3537.63 | 128026 | -132423 | 30 | 35 | 128026 | -1132423
11 | 19 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4778 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.7479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3538.87 | 0 | 3538.87 | 128439 | -132859 | 30 | 35 | 128439 | -1132859
11 | 20 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4505 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9094.79 | 0 | 9094.79 | 128049 | -127439 | 30 | 35 | 128049 | -1127439
11 | 20 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4814 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9095.96 | 0 | 9095.96 | 128562 | -127516 | 30 | 36 | 128562 | -1127516
11 | 20 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4726 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.24 | 0 | 9096.24 | 128077 | -128078 | 30 | 36 | 128077 | -1128078
11 | 20 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4852 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9097.02 | 0 | 9097.02 | 128025 | -130688 | 31 | 35 | 128025 | -1130688
11 | 20 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.7248 | 0 | 5.8986 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10081.7 | 0 | 10081.7 | 131328 | -132614 | 31 | 35 | 131328 | -1132614
11 | 20 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 14.1432 | 0 | 5.9461 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24207.7 | 0 | 24207.7 | 179247 | -108924 | 30 | 34 | 179247 | -1108924
11 | 20 | 7 | 1 | 49.0171 | 0 | 140.608 | 42.8027 | 0 | 0 | 6.2327 | 19.1668 | 0 | 0 | 0 | 3.2 | 261.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71363.6 | 0 | 71363.6 | 313019 | -760346 | 31 | 35 | 313019 | -1760346
11 | 20 | 8 | 1 | 47.3033 | 0 | 168.222 | 36.2857 | 0 | 0 | 6.2409 | 19.0672 | 0 | 0 | 0 | 0.8 | 277.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86630.4 | 0 | 86630.4 | 375360 | -672888 | 32 | 35 | 375360 | -1672888
11 | 20 | 9 | 1 | 40.5742 | 0 | 173.795 | 0 | 24.9925 | 0 | 6.253 | 19.0363 | 0 | 0 | 0 | 0 | 264.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119832 | 0 | 119832 | 394392 | -491139 | 32 | 36 | 394392 | -1491139
11 | 20 | 10 | 1 | 40.8903 | 0 | 172.186 | 0 | 25.7419 | 0 | 6.2849 | 19.0363 | 0 | 0 | 0 | 0 | 264.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140970 | 0 | 140970 | 401185 | -410871 | 34 | 38 | 401185 | -1410871
11 | 20 | 11 | 1 | 41.2451 | 0 | 163.102 | 0 | 26.8036 | 0 | 6.3046 | 19.0363 | 0 | 0 | 0 | 0 | 256.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143983 | 0 | 143983 | 408014 | -376230 | 35 | 40 | 408014 | -1376230
11 | 20 | 12 | 1 | 40.7964 | 0 | 149.692 | 0 | 27.5544 | 0 | 6.3199 | 19.0363 | 0 | 0 | 0 | 0 | 243.399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143980 | 0 | 143980 | 410234 | -331023 | 36 | 42 | 410234 | -1331023
11 | 20 | 13 | 1 | 39.8534 | 0 | 150.207 | 0 | 26.2194 | 0 | 6.3281 | 19.0363 | 0 | 0 | 0 | 0 | 241.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143978 | 0 | 143978 | 390166 | -292495 | 37 | 43 | 390166 | -1292495
11 | 20 | 14 | 1 | 41.3388 | 0 | 165.698 | 0 | 30.477 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143975 | 0 | 143975 | 443637 | -261823 | 37 | 44 | 443637 | -1261823
11 | 20 | 15 | 1 | 40.8873 | 0 | 172.702 | 0 | 32.415 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142113 | 0 | 142113 | 464585 | -246337 | 38 | 45 | 464585 | -1246337
11 | 20 | 16 | 1 | 41.7546 | 0 | 173.986 | 0 | 30.6623 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 271.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129204 | 0 | 129204 | 452582 | -266485 | 36 | 42 | 452582 | -1266485
11 | 20 | 17 | 1 | 54.7027 | 0 | 169.782 | 0 | 27.2188 | 0 | 6.3276 | 19.0363 | 0 | 0 | 0 | 2.4 | 279.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105485 | 0 | 105485 | 417686 | -308908 | 34 | 38 | 417686 | -1308908
11 | 20 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 24.5367 | 0 | 6.2992 | 19.0363 | 0 | 0 | 0 | 6.4 | 258.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79133.7 | 0 | 79133.7 | 385472 | -388324 | 32 | 35 | 385472 | -1388324
11 | 20 | 19 | 1 | 34.11 | 0 | 93.4203 | 24.1758 | 0 | 0 | 6.2955 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49038.7 | 0 | 49038.7 | 297367 | -441638 | 32 | 34 | 297367 | -1441638
11 | 20 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 12.9404 | 0 | 5.9326 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35118.6 | 0 | 35118.6 | 178230 | -9783.54 | 31 | 34 | 178230 | -1009783.54
11 | 20 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 11.3466 | 0 | 5.9085 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31183.3 | 0 | 31183.3 | 159200 | -13989.8 | 31 | 33 | 159200 | -1013989.8
11 | 20 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.5579 | 0 | 5.9053 | 12.9754 | 0 | 0 | 0 | 7.2 | 100.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19184.8 | 0 | 19184.8 | 146058 | -19282.5 | 31 | 33 | 146058 | -1019282.5
11 | 20 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.6267 | 0 | 5.9175 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.9852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10380.2 | 0 | 10380.2 | 158409 | -30292.4 | 31 | 33 | 158409 | -1030292.4
11 | 20 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 12.3105 | 0 | 5.9117 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9049.65 | 0 | 9049.65 | 150362 | -38429.3 | 31 | 33 | 150362 | -1038429.3
11 | 21 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 12.0372 | 0 | 5.9086 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9053.38 | 0 | 9053.38 | 147269 | -49433.8 | 30 | 32 | 147269 | -1049433.8
11 | 21 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.8238 | 0 | 5.9065 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9056.41 | 0 | 9056.41 | 145049 | -64216.4 | 29 | 30 | 145049 | -1064216.4
11 | 21 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.6364 | 0 | 5.9049 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9058.93 | 0 | 9058.93 | 143408 | -76721.2 | 28 | 29 | 143408 | -1076721.2
11 | 21 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4944 | 0 | 5.9039 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9061.23 | 0 | 9061.23 | 142296 | -84845.8 | 29 | 31 | 142296 | -1084845.8
11 | 21 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.6647 | 0 | 5.9054 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10047.3 | 0 | 10047.3 | 144752 | -89808.4 | 31 | 32 | 144752 | -1089808.4
11 | 21 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 15.1303 | 0 | 5.9715 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24174.5 | 0 | 24174.5 | 192667 | -70121.8 | 32 | 34 | 192667 | -1070121.8
11 | 21 | 7 | 2 | 49.0171 | 0 | 140.608 | 32.0224 | 0 | 0 | 6.2421 | 19.0363 | 0 | 0 | 0 | 3.2 | 250.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71331.4 | 0 | 71331.4 | 321663 | -613186 | 33 | 35 | 321663 | -1613186
11 | 21 | 8 | 2 | 51.2555 | 0 | 168.222 | 28.8018 | 0 | 0 | 6.2592 | 19.0363 | 0 | 0 | 0 | 0.8 | 274.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86599.2 | 0 | 86599.2 | 383812 | -552092 | 34 | 36 | 383812 | -1552092
11 | 21 | 9 | 2 | 42.4994 | 0 | 173.795 | 0 | 25.866 | 0 | 6.2744 | 19.0363 | 0 | 0 | 0 | 0 | 267.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119811 | 0 | 119811 | 406067 | -440153 | 34 | 37 | 406067 | -1440153
11 | 21 | 10 | 2 | 40.8321 | 0 | 172.186 | 0 | 27.3889 | 0 | 6.2928 | 19.0363 | 0 | 0 | 0 | 0 | 265.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140950 | 0 | 140950 | 420550 | -391431 | 36 | 39 | 420550 | -1391431
11 | 21 | 11 | 2 | 41.2337 | 0 | 163.102 | 0 | 27.7077 | 0 | 6.3037 | 19.0363 | 0 | 0 | 0 | 0 | 257.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143964 | 0 | 143964 | 420006 | -361892 | 37 | 41 | 420006 | -1361892
11 | 21 | 12 | 2 | 40.7825 | 0 | 149.692 | 0 | 28.6649 | 0 | 25.3348 | 19.0363 | 0 | 0 | 0 | 0 | 263.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143962 | 0 | 143962 | 422592 | -294697 | 39 | 43 | 422592 | -1294697
11 | 21 | 13 | 2 | 39.8383 | 0 | 150.207 | 0 | 26.9613 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 261.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143959 | 0 | 143959 | 398187 | -268796 | 40 | 44 | 398187 | -1268796
11 | 21 | 14 | 2 | 41.3233 | 0 | 165.698 | 0 | 31.2321 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 263.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143956 | 0 | 143956 | 447821 | -241444 | 41 | 46 | 447821 | -1241444
11 | 21 | 15 | 2 | 41.6349 | 0 | 172.702 | 0 | 33.1934 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142096 | 0 | 142096 | 467107 | -226491 | 41 | 47 | 467107 | -1226491
11 | 21 | 16 | 2 | 47.8195 | 0 | 173.986 | 0 | 32.8703 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 280.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129187 | 0 | 129187 | 460697 | -212484 | 41 | 47 | 460697 | -1212484
11 | 21 | 17 | 2 | 56.807 | 0 | 169.782 | 0 | 33.0614 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 287.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105469 | 0 | 105469 | 462682 | -223435 | 41 | 47 | 462682 | -1223435
11 | 21 | 18 | 2 | 49.7836 | 0 | 152.497 | 0 | 30.2711 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 264.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79117.1 | 0 | 79117.1 | 431757 | -241034 | 41 | 47 | 431757 | -1241034
11 | 21 | 19 | 2 | 34.11 | 0 | 93.4203 | 0 | 24.9952 | 0 | 6.3224 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49021.1 | 0 | 49021.1 | 341784 | -288109 | 42 | 48 | 341784 | -1288109
11 | 21 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.1074 | 0 | 5.4893 | 8.818 | 0 | 0 | 0 | 7.2 | 117.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35100.2 | 0 | 35100.2 | 183805 | 0 | 42 | 48 | 183805 | -1000000
11 | 21 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 11.5348 | 0 | 5.9119 | 12.9754 | 0 | 0 | 0 | 7.2 | 110.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31164.4 | 0 | 31164.4 | 164489 | -8643.7 | 43 | 49 | 164489 | -1008643.7
11 | 21 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 7.5028 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19165.2 | 0 | 19165.2 | 151089 | 0 | 43 | 49 | 151089 | -1000000
11 | 21 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 10.8757 | 0 | 5.9006 | 12.9754 | 0 | 0 | 0 | 6.4 | 91.6823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10359.1 | 0 | 10359.1 | 140123 | -13093.1 | 43 | 48 | 140123 | -1013093.1
11 | 21 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 6.7763 | 0 | 5.4814 | 8.818 | 0 | 0 | 0 | 5.6 | 79.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9027.71 | 0 | 9027.71 | 135330 | 0 | 43 | 48 | 135330 | -1000000
11 | 22 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.6878 | 0 | 5.8989 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.3948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9029.88 | 0 | 9029.88 | 134026 | -14827.8 | 44 | 48 | 134026 | -1014827.8
11 | 22 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6739 | 0 | 5.4822 | 8.818 | 0 | 0 | 0 | 4.8 | 78.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.77 | 0 | 9031.77 | 133154 | 0 | 45 | 49 | 133154 | -1000000
11 | 22 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.6211 | 0 | 5.8985 | 12.8287 | 0 | 0 | 0 | 4.8 | 87.3276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9033.26 | 0 | 9033.26 | 132384 | -15452.4 | 45 | 49 | 132384 | -1015452.4
11 | 22 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 6.6128 | 0 | 5.4828 | 8.818 | 0 | 0 | 0 | 4.8 | 78.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9034.65 | 0 | 9034.65 | 131824 | 0 | 46 | 49 | 131824 | -1000000
11 | 22 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 10.6771 | 0 | 5.899 | 12.9754 | 0 | 0 | 0 | 4.8 | 90.9959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10019.8 | 0 | 10019.8 | 134844 | -15465.5 | 47 | 50 | 134844 | -1015465.5
11 | 22 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 8.851 | 0 | 5.9042 | 12.9754 | 0 | 0 | 0 | 4.8 | 126.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24146.1 | 0 | 24146.1 | 181603 | -5931.58 | 48 | 50 | 181603 | -1005931.58
11 | 22 | 7 | 3 | 49.0171 | 0 | 140.608 | 0 | 23.4806 | 0 | 6.3245 | 19.0363 | 0 | 0 | 0 | 3.2 | 241.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71302.2 | 0 | 71302.2 | 327133 | -220665 | 49 | 50 | 327133 | -1220665
11 | 22 | 8 | 3 | 51.5198 | 0 | 168.222 | 0 | 31.568 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0.8 | 277.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86569 | 0 | 86569 | 431166 | -235615 | 49 | 51 | 431166 | -1235615
11 | 22 | 9 | 3 | 45.9466 | 0 | 173.795 | 0 | 34.1785 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 279.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119786 | 0 | 119786 | 462690 | -180743 | 50 | 51 | 462690 | -1180743
11 | 22 | 10 | 3 | 41.8405 | 0 | 172.186 | 0 | 35.7294 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140926 | 0 | 140926 | 474649 | -158929 | 51 | 52 | 474649 | -1158929
11 | 22 | 11 | 3 | 42.3116 | 0 | 163.102 | 0 | 34.4198 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 265.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143939 | 0 | 143939 | 452093 | -137724 | 51 | 53 | 452093 | -1137724
11 | 22 | 12 | 3 | 41.6889 | 0 | 149.692 | 0 | 32.7596 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 249.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143936 | 0 | 143936 | 437850 | -120973 | 52 | 54 | 437850 | -1120973
11 | 22 | 13 | 3 | 39.988 | 0 | 150.207 | 0 | 31.9258 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143934 | 0 | 143934 | 433673 | -99952.5 | 53 | 55 | 433673 | -1099952.5
11 | 22 | 14 | 3 | 42.5594 | 0 | 165.698 | 0 | 33.324 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 266.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143932 | 0 | 143932 | 475806 | -80711.8 | 54 | 56 | 475806 | -1080711.8
11 | 22 | 15 | 3 | 42.0969 | 0 | 172.702 | 0 | 34.6747 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 274.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142074 | 0 | 142074 | 516401 | -66570.7 | 55 | 57 | 516401 | -1066570.7
11 | 22 | 16 | 3 | 47.8195 | 0 | 173.986 | 0 | 31.2331 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 278.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129166 | 0 | 129166 | 504950 | -56734.2 | 54 | 56 | 504950 | -1056734.2
11 | 22 | 17 | 3 | 56.356 | 0 | 169.782 | 0 | 30.0374 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 283.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105449 | 0 | 105449 | 502983 | -68203 | 53 | 54 | 502983 | -1068203
11 | 22 | 18 | 3 | 49.7836 | 0 | 152.497 | 0 | 27.7855 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 261.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79098.4 | 0 | 79098.4 | 451879 | -83596.9 | 52 | 53 | 451879 | -1083596.9
11 | 22 | 19 | 3 | 34.11 | 0 | 93.4203 | 0 | 23.6703 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 183.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49003.3 | 0 | 49003.3 | 343861 | -143171 | 51 | 52 | 343861 | -1143171
11 | 22 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 9.2468 | 0 | 5.4914 | 8.818 | 0 | 0 | 0 | 7.2 | 117.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35083.4 | 0 | 35083.4 | 186872 | 0 | 50 | 51 | 186872 | -1000000
11 | 22 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 8.2462 | 0 | 5.4807 | 8.818 | 0 | 0 | 0 | 7.2 | 103.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31148.2 | 0 | 31148.2 | 167258 | 0 | 49 | 50 | 167258 | -1000000
11 | 22 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 7.6395 | 0 | 5.4786 | 8.818 | 0 | 0 | 0 | 7.2 | 91.8564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19146.2 | 0 | 19146.2 | 154085 | 0 | 50 | 50 | 154085 | -1000000
11 | 22 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 9.2872 | 0 | 5.8972 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10339.1 | 0 | 10339.1 | 142890 | -6221.13 | 50 | 50 | 142890 | -1006221.13
11 | 22 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 6.8984 | 0 | 5.4806 | 8.818 | 0 | 0 | 0 | 5.6 | 79.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9007.1 | 0 | 9007.1 | 138002 | 0 | 50 | 50 | 138002 | -1000000
11 | 23 | 1 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.9 | 0 | 5.8987 | 12.8287 | 0 | 0 | 0 | 4.8 | 78.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454.22 | 0 | 3454.22 | 138119 | -869.778 | 50 | 50 | 138119 | -1000869.778
11 | 23 | 2 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.7665 | 0 | 5.4815 | 8.818 | 0 | 0 | 0 | 4.8 | 73.7167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455.82 | 0 | 3455.82 | 135147 | 0 | 50 | 50 | 135147 | -1000000
11 | 23 | 3 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.7268 | 0 | 5.4818 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3457.82 | 0 | 3457.82 | 134312 | 0 | 50 | 50 | 134312 | -1000000
11 | 23 | 4 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.688 | 0 | 5.4821 | 8.818 | 0 | 0 | 0 | 4.8 | 73.6388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459.22 | 0 | 3459.22 | 133464 | 0 | 49 | 49 | 133464 | -1000000
11 | 23 | 5 | 8 | 5.1054 | 0 | 42.7453 | 0 | 8.6145 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3460.46 | 0 | 3460.46 | 135143 | -7600.02 | 49 | 49 | 135143 | -1007600.02
11 | 23 | 6 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.6232 | 0 | 5.4827 | 8.818 | 0 | 0 | 0 | 4.8 | 73.5745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461.53 | 0 | 3461.53 | 132007 | 0 | 48 | 48 | 132007 | -1000000
11 | 23 | 7 | 8 | 5.1054 | 0 | 42.7453 | 0 | 6.5935 | 0 | 5.4829 | 8.818 | 0 | 0 | 0 | 3.2 | 71.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3462.65 | 0 | 3462.65 | 131399 | 0 | 48 | 48 | 131399 | -1000000
11 | 23 | 8 | 8 | 4.8806 | 0 | 42.7453 | 0 | 8.68 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0.8 | 75.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.75 | 0 | 3463.75 | 135383 | -6127.32 | 49 | 49 | 135383 | -1006127.32
11 | 23 | 9 | 8 | 4.9213 | 0 | 42.7453 | 0 | 6.5424 | 0 | 5.4834 | 8.818 | 0 | 0 | 0 | 0 | 68.5104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3464.76 | 0 | 3464.76 | 130205 | 0 | 49 | 49 | 130205 | -1000000
11 | 23 | 10 | 8 | 4.844 | 0 | 42.7453 | 0 | 6.9103 | 0 | 5.8987 | 12.8287 | 0 | 0 | 0 | 0 | 73.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465.73 | 0 | 3465.73 | 138482 | -3199.51 | 49 | 49 | 138482 | -1003199.51
11 | 23 | 11 | 8 | 4.7593 | 0 | 42.7453 | 0 | 6.4988 | 0 | 5.4838 | 8.818 | 0 | 0 | 0 | 0 | 68.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3466.68 | 0 | 3466.68 | 129183 | 0 | 50 | 50 | 129183 | -1000000
11 | 23 | 12 | 8 | 4.9531 | 0 | 42.7453 | 0 | 6.4675 | 0 | 5.9022 | 12.8287 | 0 | 0 | 0 | 0 | 72.8969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467.45 | 0 | 3467.45 | 128644 | -3322.98 | 50 | 50 | 128644 | -1003322.98
11 | 23 | 13 | 8 | 4.6984 | 0 | 42.7453 | 0 | 6.7816 | 0 | 5.8995 | 12.8287 | 0 | 0 | 0 | 0 | 72.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467.92 | 0 | 3467.92 | 135643 | -3514.18 | 50 | 50 | 135643 | -1003514.18
11 | 23 | 14 | 8 | 4.7778 | 0 | 42.7453 | 0 | 6.4303 | 0 | 5.4845 | 8.818 | 0 | 0 | 0 | 0 | 68.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3468.65 | 0 | 3468.65 | 127705 | 0 | 50 | 50 | 127705 | -1000000
11 | 23 | 15 | 8 | 5.378 | 0 | 42.7453 | 0 | 8.4078 | 0 | 5.8976 | 12.8287 | 0 | 0 | 0 | 0 | 75.2573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3469.66 | 0 | 3469.66 | 127328 | -10016.9 | 50 | 50 | 127328 | -1010016.9
11 | 23 | 16 | 8 | 5.5132 | 0 | 42.7453 | 0 | 6.5426 | 0 | 5.9015 | 12.8287 | 0 | 0 | 0 | 0 | 73.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470.39 | 0 | 3470.39 | 130345 | -3779.3 | 49 | 49 | 130345 | -1003779.3
11 | 23 | 17 | 8 | 6.5408 | 0 | 42.7453 | 0 | 8.1483 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 2.4 | 78.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3471.26 | 0 | 3471.26 | 127962 | -6566.75 | 48 | 48 | 127962 | -1006566.75
11 | 23 | 18 | 8 | 6.6633 | 0 | 42.7453 | 0 | 8.0247 | 0 | 5.8984 | 12.8287 | 0 | 0 | 0 | 6.4 | 82.5604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472.46 | 0 | 3472.46 | 126020 | -6242.17 | 47 | 47 | 126020 | -1006242.17
11 | 23 | 19 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.8276 | 0 | 5.8982 | 14.8767 | 0 | 0 | 0 | 7.2 | 87.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3473.61 | 0 | 3473.61 | 143979 | -8690.26 | 47 | 47 | 143979 | -1008690.26
11 | 23 | 20 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.3316 | 0 | 5.9037 | 12.8287 | 0 | 0 | 0 | 7.2 | 81.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3474.99 | 0 | 3474.99 | 125369 | -8118.55 | 47 | 47 | 125369 | -1008118.55
11 | 23 | 21 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.5918 | 0 | 5.8975 | 14.8767 | 0 | 0 | 0 | 7.2 | 86.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476.42 | 0 | 3476.42 | 142036 | -9830.86 | 47 | 47 | 142036 | -1009830.86
11 | 23 | 22 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.3004 | 0 | 5.904 | 12.8287 | 0 | 0 | 0 | 7.2 | 81.6417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3477.86 | 0 | 3477.86 | 124707 | -8854 | 47 | 47 | 124707 | -1008854
11 | 23 | 23 | 8 | 6.6633 | 0 | 42.7453 | 0 | 9.4941 | 0 | 5.8973 | 14.8767 | 0 | 0 | 0 | 6.4 | 86.0766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3479.27 | 0 | 3479.27 | 140837 | -10515.6 | 48 | 48 | 140837 | -1010515.6
11 | 23 | 24 | 8 | 6.6633 | 0 | 42.7453 | 0 | 6.2739 | 0 | 5.9044 | 12.8287 | 0 | 0 | 0 | 5.6 | 80.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480.63 | 0 | 3480.63 | 124138 | -9044.63 | 48 | 48 | 124138 | -1009044.63
11 | 24 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.4178 | 0 | 5.8971 | 14.8767 | 0 | 0 | 0 | 4.8 | 88.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9036.71 | 0 | 9036.71 | 139862 | -10411.4 | 47 | 47 | 139862 | -1010411.4
11 | 24 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.8692 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9037.99 | 0 | 9037.99 | 147947 | -16406.4 | 46 | 46 | 147947 | -1016406.4
11 | 24 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 8.0688 | 0 | 5.8987 | 12.8287 | 0 | 0 | 0 | 4.8 | 84.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9038.42 | 0 | 9038.42 | 123569 | -10313.2 | 45 | 45 | 123569 | -1010313.2
11 | 24 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 9.331 | 0 | 5.897 | 14.8767 | 0 | 0 | 0 | 4.8 | 88.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9039.65 | 0 | 9039.65 | 138638 | -13145.2 | 46 | 46 | 138638 | -1013145.2
11 | 24 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 9.9371 | 0 | 5.8993 | 17.5105 | 0 | 0 | 0 | 4.8 | 94.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10024.8 | 0 | 10024.8 | 149175 | -20912.3 | 46 | 46 | 149175 | -1020912.3
11 | 24 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 10.8941 | 0 | 5.9116 | 12.9754 | 0 | 0 | 0 | 4.8 | 128.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24150.9 | 0 | 24150.9 | 173876 | -11448.6 | 47 | 47 | 173876 | -1011448.6
11 | 24 | 7 | 5 | 49.0171 | 0 | 140.608 | 0 | 23.5518 | 0 | 6.2999 | 19.0363 | 0 | 0 | 0 | 3.2 | 241.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71307.5 | 0 | 71307.5 | 319385 | -340163 | 46 | 46 | 319385 | -1340163
11 | 24 | 8 | 5 | 51.2829 | 0 | 168.222 | 0 | 32.2682 | 0 | 6.3092 | 19.0363 | 0 | 0 | 0 | 0.8 | 277.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86574.4 | 0 | 86574.4 | 466375 | -346403 | 46 | 46 | 466375 | -1346403
11 | 24 | 9 | 5 | 42.3063 | 0 | 173.795 | 0 | 33.2692 | 0 | 6.3191 | 19.0363 | 0 | 0 | 0 | 0 | 274.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119791 | 0 | 119791 | 480947 | -297150 | 45 | 45 | 480947 | -1297150
11 | 24 | 10 | 5 | 41.8524 | 0 | 172.186 | 0 | 34.3754 | 0 | 6.329 | 19.0363 | 0 | 0 | 0 | 0 | 273.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140930 | 0 | 140930 | 491687 | -288708 | 45 | 45 | 491687 | -1288708
11 | 24 | 11 | 5 | 42.3555 | 0 | 163.102 | 0 | 32.1833 | 0 | 6.3302 | 19.0363 | 0 | 0 | 0 | 0 | 263.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143944 | 0 | 143944 | 466588 | -287215 | 44 | 44 | 466588 | -1287215
11 | 24 | 12 | 5 | 41.4231 | 0 | 149.692 | 0 | 30.8025 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143942 | 0 | 143942 | 443973 | -269892 | 44 | 44 | 443973 | -1269892
11 | 24 | 13 | 5 | 39.9718 | 0 | 150.207 | 0 | 27.5105 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 243.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143940 | 0 | 143940 | 403249 | -255169 | 43 | 44 | 403249 | -1255169
11 | 24 | 14 | 5 | 42.5867 | 0 | 165.698 | 0 | 30.8126 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143938 | 0 | 143938 | 449942 | -243403 | 43 | 43 | 449942 | -1243403
11 | 24 | 15 | 5 | 45.4764 | 0 | 172.702 | 0 | 33.2213 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 276.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142078 | 0 | 142078 | 479241 | -242654 | 43 | 43 | 479241 | -1242654
11 | 24 | 16 | 5 | 47.3737 | 0 | 173.986 | 0 | 34.0783 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 280.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129170 | 0 | 129170 | 491375 | -237364 | 43 | 43 | 491375 | -1237364
11 | 24 | 17 | 5 | 56.3988 | 0 | 169.782 | 0 | 32.9299 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105453 | 0 | 105453 | 477375 | -246571 | 42 | 42 | 477375 | -1246571
11 | 24 | 18 | 5 | 49.7836 | 0 | 152.497 | 0 | 28.5877 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 262.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79102.6 | 0 | 79102.6 | 425325 | -260314 | 42 | 42 | 425325 | -1260314
11 | 24 | 19 | 5 | 34.11 | 0 | 93.4203 | 0 | 24.7432 | 0 | 6.3152 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49007.8 | 0 | 49007.8 | 352303 | -321356 | 42 | 42 | 352303 | -1321356
11 | 24 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 9.0419 | 0 | 5.4885 | 8.818 | 0 | 0 | 0 | 7.2 | 117.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35087.7 | 0 | 35087.7 | 182167 | 0 | 42 | 42 | 182167 | -1000000
11 | 24 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 8.0504 | 0 | 5.4796 | 8.818 | 0 | 0 | 0 | 7.2 | 102.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31151.6 | 0 | 31151.6 | 162979 | 0 | 42 | 42 | 162979 | -1000000
11 | 24 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 11.0097 | 0 | 5.9035 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19150.6 | 0 | 19150.6 | 149713 | -12428.5 | 42 | 42 | 149713 | -1012428.5
11 | 24 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 6.9293 | 0 | 5.4804 | 8.818 | 0 | 0 | 0 | 6.4 | 83.1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10344.3 | 0 | 10344.3 | 138573 | 0 | 41 | 42 | 138573 | -1000000
11 | 24 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.1562 | 0 | 5.9005 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9012.98 | 0 | 9012.98 | 134056 | -17683.9 | 41 | 42 | 134056 | -1017683.9
11 | 25 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 6.6349 | 0 | 5.9007 | 12.8287 | 0 | 0 | 0 | 4.8 | 79.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9015.68 | 0 | 9015.68 | 132288 | -7890.83 | 40 | 41 | 132288 | -1007890.83
11 | 25 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 9.3081 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 4.8 | 81.9605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9017.93 | 0 | 9017.93 | 132643 | -13545.4 | 39 | 40 | 132643 | -1013545.4
11 | 25 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.0648 | 0 | 5.8995 | 14.8767 | 0 | 0 | 0 | 4.8 | 84.7679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9020.75 | 0 | 9020.75 | 148208 | -14894.7 | 38 | 39 | 148208 | -1014894.7
11 | 25 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.3065 | 0 | 5.8997 | 14.8767 | 0 | 0 | 0 | 4.8 | 85.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9023.04 | 0 | 9023.04 | 145245 | -17506.9 | 37 | 39 | 145245 | -1017506.9
11 | 25 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.886 | 0 | 5.9036 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9025.34 | 0 | 9025.34 | 152390 | -27505.9 | 37 | 38 | 152390 | -1027505.9
11 | 25 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.4602 | 0 | 5.8997 | 14.8767 | 0 | 0 | 0 | 4.8 | 85.1636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9027.57 | 0 | 9027.57 | 142658 | -21663.3 | 36 | 38 | 142658 | -1021663.3
11 | 25 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0225 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9030.13 | 0 | 9030.13 | 148736 | -34977.4 | 37 | 38 | 148736 | -1034977.4
11 | 25 | 8 | 6 | 6.154 | 0 | 42.7453 | 32.4858 | 0 | 0 | 6.255 | 18.8896 | 0 | 0 | 0 | 0.8 | 107.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9032.31 | 0 | 9032.31 | 133298 | -576473 | 37 | 39 | 133298 | -1576473
11 | 25 | 9 | 6 | 6.0292 | 0 | 42.7453 | 32.1518 | 0 | 0 | 6.2494 | 18.8896 | 0 | 0 | 0 | 0 | 106.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9034.45 | 0 | 9034.45 | 185508 | -566285 | 37 | 39 | 185508 | -1566285
11 | 25 | 10 | 6 | 6.4875 | 0 | 42.7453 | 25.4357 | 0 | 0 | 6.2525 | 18.8896 | 0 | 0 | 0 | 0 | 99.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9033.99 | 0 | 9033.99 | 167971 | -472848 | 38 | 39 | 167971 | -1472848
11 | 25 | 11 | 6 | 6.1808 | 0 | 42.7453 | 23.8247 | 0 | 0 | 6.2509 | 18.8896 | 0 | 0 | 0 | 0 | 97.8913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.74 | 0 | 9031.74 | 183467 | -447192 | 37 | 40 | 183467 | -1447192
11 | 25 | 12 | 6 | 6.1557 | 0 | 42.7453 | 22.7936 | 0 | 0 | 6.2525 | 18.8896 | 0 | 0 | 0 | 0 | 96.8367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.76 | 0 | 9031.76 | 180527 | -426320 | 38 | 40 | 180527 | -1426320
11 | 25 | 13 | 6 | 5.4795 | 0 | 42.7453 | 19.6123 | 0 | 0 | 6.1479 | 18.8896 | 0 | 0 | 0 | 0 | 92.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.71 | 0 | 9031.71 | 179404 | -365370 | 38 | 41 | 179404 | -1365370
11 | 25 | 14 | 6 | 5.4793 | 0 | 42.7453 | 19.9141 | 0 | 0 | 6.1602 | 18.8896 | 0 | 0 | 0 | 0 | 93.1884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9031.9 | 0 | 9031.9 | 186708 | -368102 | 39 | 42 | 186708 | -1368102
11 | 25 | 15 | 6 | 5.5024 | 0 | 42.7453 | 0 | 8.6327 | 0 | 5.8972 | 12.8287 | 0 | 0 | 0 | 0 | 75.6063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9032.13 | 0 | 9032.13 | 126910 | -7250.43 | 39 | 43 | 126910 | -1007250.43
11 | 25 | 16 | 6 | 5.7221 | 0 | 42.7453 | 0 | 6.2611 | 0 | 5.9045 | 12.8287 | 0 | 0 | 0 | 0 | 73.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9032.47 | 0 | 9032.47 | 124089 | -7477.22 | 38 | 41 | 124089 | -1007477.22
11 | 25 | 17 | 6 | 8.5534 | 0 | 42.7453 | 0 | 8.4387 | 0 | 5.8979 | 12.8287 | 0 | 0 | 0 | 2.4 | 80.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9033.69 | 0 | 9033.69 | 123756 | -11739.1 | 37 | 40 | 123756 | -1011739.1
11 | 25 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 8.7175 | 0 | 5.8975 | 12.8287 | 0 | 0 | 0 | 6.4 | 85.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9035.33 | 0 | 9035.33 | 123488 | -13551.1 | 36 | 38 | 123488 | -1013551.1
11 | 25 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 9.0562 | 0 | 5.8971 | 12.8287 | 0 | 0 | 0 | 7.2 | 86.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9036.91 | 0 | 9036.91 | 123206 | -15575.2 | 36 | 37 | 123206 | -1015575.2
11 | 25 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9991 | 0 | 5.9027 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9039 | 0 | 9039 | 147332 | -28158.6 | 35 | 36 | 147332 | -1028158.6
11 | 25 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.129 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9041.04 | 0 | 9041.04 | 144539 | -32198.4 | 34 | 35 | 144539 | -1032198.4
11 | 25 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2224 | 0 | 5.9027 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9043.47 | 0 | 9043.47 | 142881 | -38032.4 | 35 | 36 | 142881 | -1038032.4
11 | 25 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3401 | 0 | 5.9029 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9045.93 | 0 | 9045.93 | 141706 | -45153.2 | 35 | 36 | 141706 | -1045153.2
11 | 25 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.1544 | 0 | 5.9018 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9048.19 | 0 | 9048.19 | 140499 | -47163.6 | 36 | 37 | 140499 | -1047163.6
11 | 26 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.1419 | 0 | 5.9015 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.0578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3495.6 | 0 | 3495.6 | 139310 | -55634 | 36 | 37 | 139310 | -1055634
11 | 26 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.1786 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3497.56 | 0 | 3497.56 | 138511 | -62394.6 | 36 | 37 | 138511 | -1062394.6
11 | 26 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.1995 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3499.61 | 0 | 3499.61 | 137975 | -67777.7 | 37 | 37 | 137975 | -1067777.7
11 | 26 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.2017 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3501.51 | 0 | 3501.51 | 137245 | -72054.1 | 37 | 37 | 137245 | -1072054.1
11 | 26 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.1491 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503.35 | 0 | 3503.35 | 136646 | -73689.5 | 37 | 38 | 136646 | -1073689.5
11 | 26 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.2579 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3505.12 | 0 | 3505.12 | 136885 | -76680.7 | 38 | 38 | 136885 | -1076680.7
11 | 26 | 7 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0062 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 3.2 | 85.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3506.85 | 0 | 3506.85 | 135746 | -75474.1 | 38 | 39 | 135746 | -1075474.1
11 | 26 | 8 | 7 | 4.8234 | 0 | 42.7453 | 0 | 11.0926 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.7256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3508.53 | 0 | 3508.53 | 136101 | -73672.6 | 39 | 39 | 136101 | -1073672.6
11 | 26 | 9 | 7 | 4.8929 | 0 | 42.7453 | 0 | 10.8165 | 0 | 5.8995 | 17.3638 | 0 | 0 | 0 | 0 | 81.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3510.13 | 0 | 3510.13 | 135321 | -68639.1 | 40 | 40 | 135321 | -1068639.1
11 | 26 | 10 | 7 | 5.0501 | 0 | 42.7453 | 0 | 10.8118 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 0 | 81.8706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511.7 | 0 | 3511.7 | 136419 | -60059.7 | 41 | 41 | 136419 | -1060059.7
11 | 26 | 11 | 7 | 4.8278 | 0 | 42.7453 | 0 | 10.4026 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 81.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3513.14 | 0 | 3513.14 | 135302 | -49473.3 | 43 | 43 | 135302 | -1049473.3
11 | 26 | 12 | 7 | 4.7542 | 0 | 42.7453 | 0 | 10.3168 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 81.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3514.54 | 0 | 3514.54 | 136972 | -41376.3 | 44 | 44 | 136972 | -1041376.3
11 | 26 | 13 | 7 | 4.7915 | 0 | 42.7453 | 0 | 9.4738 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 77.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3515.8 | 0 | 3515.8 | 129401 | -25182.5 | 45 | 45 | 129401 | -1025182.5
11 | 26 | 14 | 7 | 4.7601 | 0 | 42.7453 | 0 | 9.7845 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 80.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3516.9 | 0 | 3516.9 | 135601 | -35476.9 | 45 | 45 | 135601 | -1035476.9
11 | 26 | 15 | 7 | 4.9345 | 0 | 42.7453 | 0 | 9.5764 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 0 | 80.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3517.63 | 0 | 3517.63 | 135188 | -32640.1 | 45 | 46 | 135188 | -1032640.1
11 | 26 | 16 | 7 | 5.6972 | 0 | 42.7453 | 0 | 9.3659 | 0 | 5.8967 | 14.8767 | 0 | 0 | 0 | 0 | 78.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3518.85 | 0 | 3518.85 | 130062 | -24795.3 | 45 | 46 | 130062 | -1024795.3
11 | 26 | 17 | 7 | 6.5946 | 0 | 42.7453 | 0 | 9.4998 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 2.4 | 84.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3519.76 | 0 | 3519.76 | 133422 | -42410.5 | 45 | 46 | 133422 | -1042410.5
11 | 26 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.6281 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520.61 | 0 | 3520.61 | 134398 | -46432.2 | 45 | 46 | 134398 | -1046432.2
11 | 26 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5625 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3521.91 | 0 | 3521.91 | 133779 | -47747.9 | 45 | 46 | 133779 | -1047747.9
11 | 26 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5433 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522.96 | 0 | 3522.96 | 133590 | -50499.7 | 45 | 45 | 133590 | -1050499.7
11 | 26 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5186 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524.06 | 0 | 3524.06 | 133266 | -52102.9 | 45 | 45 | 133266 | -1052102.9
11 | 26 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5762 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 7.2 | 89.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525.05 | 0 | 3525.05 | 133243 | -53630.8 | 45 | 45 | 133243 | -1053630.8
11 | 26 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5662 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 6.4 | 88.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3526.05 | 0 | 3526.05 | 132786 | -56811.7 | 44 | 44 | 132786 | -1056811.7
11 | 26 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 9.5593 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 5.6 | 87.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3527.04 | 0 | 3527.04 | 132631 | -58462.2 | 44 | 44 | 132631 | -1058462.2
11 | 27 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.6859 | 0 | 5.8969 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9082.74 | 0 | 9082.74 | 132752 | -58934.5 | 44 | 44 | 132752 | -1058934.5
11 | 27 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.7559 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.9961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9083.71 | 0 | 9083.71 | 132777 | -60467.8 | 44 | 44 | 132777 | -1060467.8
11 | 27 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.8464 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9083.89 | 0 | 9083.89 | 132646 | -62534.4 | 44 | 44 | 132646 | -1062534.4
11 | 27 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 9.9261 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9084.53 | 0 | 9084.53 | 132208 | -68420.8 | 41 | 42 | 132208 | -1068420.8
11 | 27 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.2463 | 0 | 5.898 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10069.2 | 0 | 10069.2 | 135565 | -74813.1 | 39 | 40 | 135565 | -1074813.1
11 | 27 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.7944 | 0 | 5.9445 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24195.1 | 0 | 24195.1 | 183564 | -63633.6 | 36 | 38 | 183564 | -1063633.6
11 | 27 | 7 | 1 | 49.0171 | 0 | 140.608 | 33.2207 | 0 | 0 | 6.2408 | 19.0363 | 0 | 0 | 0 | 3.2 | 251.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71351.1 | 0 | 71351.1 | 314865 | -622726 | 35 | 37 | 314865 | -1622726
11 | 27 | 8 | 1 | 51.4457 | 0 | 168.222 | 29.8075 | 0 | 0 | 6.2501 | 19.0363 | 0 | 0 | 0 | 0.8 | 275.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86618 | 0 | 86618 | 384845 | -575665 | 35 | 37 | 384845 | -1575665
11 | 27 | 9 | 1 | 49.0338 | 0 | 173.795 | 0 | 25.1122 | 0 | 6.2676 | 19.0363 | 0 | 0 | 0 | 0 | 273.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119824 | 0 | 119824 | 396042 | -471762 | 34 | 36 | 396042 | -1471762
11 | 27 | 10 | 1 | 41.8524 | 0 | 172.186 | 0 | 25.443 | 0 | 6.2793 | 19.0363 | 0 | 0 | 0 | 0 | 264.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140963 | 0 | 140963 | 398820 | -451116 | 34 | 36 | 398820 | -1451116
11 | 27 | 11 | 1 | 42.5238 | 0 | 163.102 | 0 | 24.9644 | 0 | 6.2822 | 19.0363 | 0 | 0 | 0 | 0 | 255.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143976 | 0 | 143976 | 387774 | -451723 | 33 | 36 | 387774 | -1451723
11 | 27 | 12 | 1 | 41.543 | 0 | 149.692 | 0 | 23.933 | 0 | 6.2856 | 19.0363 | 0 | 0 | 0 | 0 | 240.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143974 | 0 | 143974 | 371272 | -417226 | 33 | 36 | 371272 | -1417226
11 | 27 | 13 | 1 | 39.9758 | 0 | 150.207 | 0 | 22.3646 | 0 | 6.2776 | 19.0363 | 0 | 0 | 0 | 0 | 237.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143973 | 0 | 143973 | 350927 | -410668 | 33 | 36 | 350927 | -1410668
11 | 27 | 14 | 1 | 42.788 | 0 | 165.698 | 0 | 24.3906 | 0 | 6.2874 | 19.0363 | 0 | 0 | 0 | 0 | 258.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143969 | 0 | 143969 | 384226 | -388742 | 32 | 35 | 384226 | -1388742
11 | 27 | 15 | 1 | 42.0969 | 0 | 172.702 | 0 | 25.5693 | 0 | 6.2957 | 19.0363 | 0 | 0 | 0 | 0 | 265.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142109 | 0 | 142109 | 402792 | -376160 | 32 | 35 | 402792 | -1376160
11 | 27 | 16 | 1 | 47.8195 | 0 | 173.986 | 0 | 25.7715 | 0 | 6.2952 | 19.0363 | 0 | 0 | 0 | 0 | 272.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129200 | 0 | 129200 | 405873 | -389509 | 31 | 34 | 405873 | -1389509
11 | 27 | 17 | 1 | 56.6611 | 0 | 169.782 | 0 | 25.364 | 0 | 6.2925 | 19.0363 | 0 | 0 | 0 | 2.4 | 279.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105484 | 0 | 105484 | 399277 | -402820 | 31 | 34 | 399277 | -1402820
11 | 27 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 24.9142 | 0 | 6.2791 | 19.0363 | 0 | 0 | 0 | 6.4 | 258.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79133.4 | 0 | 79133.4 | 385489 | -462050 | 30 | 33 | 385489 | -1462050
11 | 27 | 19 | 1 | 34.11 | 0 | 93.4203 | 28.424 | 0 | 0 | 6.2828 | 19.0363 | 0 | 0 | 0 | 7.2 | 188.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49037.9 | 0 | 49037.9 | 298622 | -506400 | 29 | 32 | 298622 | -1506400
11 | 27 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 13.7483 | 0 | 5.9423 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35117.5 | 0 | 35117.5 | 178545 | -11927.6 | 27 | 30 | 178545 | -1011927.6
11 | 27 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.3382 | 0 | 5.9158 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31182 | 0 | 31182 | 159639 | -18403.4 | 26 | 29 | 159639 | -1018403.4
11 | 27 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 12.5118 | 0 | 5.9153 | 15.4625 | 0 | 0 | 0 | 7.2 | 103.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19183.4 | 0 | 19183.4 | 155334 | -32621.2 | 26 | 28 | 155334 | -1032621.2
11 | 27 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.5454 | 0 | 5.9162 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10379.4 | 0 | 10379.4 | 156849 | -59363.4 | 25 | 28 | 156849 | -1059363.4
11 | 27 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.9436 | 0 | 5.9086 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9049.62 | 0 | 9049.62 | 148975 | -78088.5 | 24 | 27 | 148975 | -1078088.5
11 | 28 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.6721 | 0 | 5.9059 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9053.73 | 0 | 9053.73 | 146185 | -96168.5 | 24 | 26 | 146185 | -1096168.5
11 | 28 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.4782 | 0 | 5.9043 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9056.91 | 0 | 9056.91 | 144372 | -110415 | 22 | 25 | 144372 | -1110415
11 | 28 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3078 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9059.83 | 0 | 9059.83 | 142838 | -126161 | 21 | 24 | 142838 | -1126161
11 | 28 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.1697 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9062.3 | 0 | 9062.3 | 141699 | -141183 | 21 | 23 | 141699 | -1141183
11 | 28 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.288 | 0 | 5.9032 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10048.7 | 0 | 10048.7 | 143801 | -151723 | 20 | 23 | 143801 | -1151723
11 | 28 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.4659 | 0 | 5.9595 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24176.1 | 0 | 24176.1 | 190941 | -135500 | 19 | 22 | 190941 | -1135500
11 | 28 | 7 | 2 | 49.0171 | 0 | 140.608 | 47.556 | 0 | 0 | 6.2144 | 19.1248 | 0 | 0 | 0 | 3.2 | 265.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71333.4 | 0 | 71333.4 | 321027 | -866570 | 20 | 23 | 321027 | -1866570
11 | 28 | 8 | 2 | 49.5486 | 0 | 168.222 | 43.2683 | 0 | 0 | 6.2268 | 19.0393 | 0 | 0 | 0 | 0.8 | 287.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86601.4 | 0 | 86601.4 | 382778 | -789343 | 20 | 23 | 382778 | -1789343
11 | 28 | 9 | 2 | 41.1303 | 0 | 173.795 | 31.1969 | 0 | 0 | 6.2358 | 19.0363 | 0 | 0 | 0 | 0 | 271.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119812 | 0 | 119812 | 401557 | -628196 | 20 | 24 | 401557 | -1628196
11 | 28 | 10 | 2 | 41.16 | 0 | 172.186 | 26.8688 | 0 | 0 | 6.2585 | 19.0363 | 0 | 0 | 0 | 0 | 265.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140952 | 0 | 140952 | 399943 | -532724 | 23 | 27 | 399943 | -1532724
11 | 28 | 11 | 2 | 41.3657 | 0 | 163.102 | 27.1879 | 0 | 0 | 6.2773 | 19.0363 | 0 | 0 | 0 | 0 | 256.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143967 | 0 | 143967 | 389704 | -501120 | 24 | 29 | 389704 | -1501120
11 | 28 | 12 | 2 | 40.8097 | 0 | 149.692 | 0 | 25.4885 | 0 | 6.3008 | 19.0363 | 0 | 0 | 0 | 0 | 241.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143966 | 0 | 143966 | 376572 | -412593 | 26 | 32 | 376572 | -1412593
11 | 28 | 13 | 2 | 39.8614 | 0 | 150.207 | 0 | 23.2825 | 0 | 25.3044 | 19.0363 | 0 | 0 | 0 | 0 | 257.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143964 | 0 | 143964 | 355377 | -381154 | 27 | 33 | 355377 | -1381154
11 | 28 | 14 | 2 | 41.3652 | 0 | 165.698 | 0 | 24.6863 | 0 | 25.3159 | 19.0363 | 0 | 0 | 0 | 0 | 276.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143961 | 0 | 143961 | 388531 | -327681 | 27 | 34 | 388531 | -1327681
11 | 28 | 15 | 2 | 41.134 | 0 | 172.702 | 0 | 25.8603 | 0 | 25.325 | 19.0363 | 0 | 0 | 0 | 0 | 284.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142101 | 0 | 142101 | 406957 | -310235 | 28 | 35 | 406957 | -1310235
11 | 28 | 16 | 2 | 42.1056 | 0 | 173.986 | 0 | 26.0354 | 0 | 25.3151 | 19.0363 | 0 | 0 | 0 | 0 | 286.478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129193 | 0 | 129193 | 409792 | -349333 | 27 | 33 | 409792 | -1349333
11 | 28 | 17 | 2 | 55.5768 | 0 | 169.782 | 0 | 25.626 | 0 | 25.2978 | 19.0363 | 0 | 0 | 0 | 2.4 | 297.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105476 | 0 | 105476 | 403600 | -418311 | 25 | 30 | 403600 | -1418311
11 | 28 | 18 | 2 | 49.7836 | 0 | 152.497 | 27.2358 | 0 | 0 | 6.2763 | 19.0363 | 0 | 0 | 0 | 6.4 | 261.229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79125.3 | 0 | 79125.3 | 395953 | -513958 | 23 | 28 | 395953 | -1513958
11 | 28 | 19 | 2 | 34.11 | 0 | 93.4203 | 32.5054 | 0 | 0 | 6.2782 | 19.0363 | 0 | 0 | 0 | 7.2 | 192.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49030.8 | 0 | 49030.8 | 310084 | -559854 | 23 | 27 | 310084 | -1559854
11 | 28 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.6456 | 0 | 5.9572 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35110.8 | 0 | 35110.8 | 181494 | -15801.9 | 22 | 26 | 181494 | -1015801.9
11 | 28 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.9699 | 0 | 5.9229 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31175.1 | 0 | 31175.1 | 162419 | -23392.7 | 21 | 25 | 162419 | -1023392.7
11 | 28 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.6722 | 0 | 5.9368 | 17.5105 | 0 | 0 | 0 | 7.2 | 107.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19176.3 | 0 | 19176.3 | 173856 | -41367.4 | 21 | 24 | 173856 | -1041367.4
11 | 28 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.4714 | 0 | 5.9162 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.8286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10372.5 | 0 | 10372.5 | 158078 | -70177.6 | 21 | 24 | 158078 | -1070177.6
11 | 28 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.9311 | 0 | 5.9093 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9042.92 | 0 | 9042.92 | 151214 | -88180 | 20 | 23 | 151214 | -1088180
11 | 29 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.6519 | 0 | 5.9065 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.19 | 0 | 9047.19 | 148354 | -106766 | 20 | 23 | 148354 | -1106766
11 | 29 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.4728 | 0 | 5.9049 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9050.57 | 0 | 9050.57 | 146552 | -120363 | 20 | 23 | 146552 | -1120363
11 | 29 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3328 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9053.61 | 0 | 9053.61 | 145018 | -130649 | 20 | 23 | 145018 | -1130649
11 | 29 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.2147 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9056.25 | 0 | 9056.25 | 143728 | -141483 | 20 | 23 | 143728 | -1141483
11 | 29 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.3401 | 0 | 5.904 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10042.7 | 0 | 10042.7 | 145807 | -149125 | 20 | 23 | 145807 | -1149125
11 | 29 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.567 | 0 | 5.9627 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24170.2 | 0 | 24170.2 | 192986 | -129633 | 20 | 23 | 192986 | -1129633
11 | 29 | 7 | 3 | 49.0171 | 0 | 140.608 | 46.4397 | 0 | 0 | 6.2166 | 19.1195 | 0 | 0 | 0 | 3.2 | 264.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71327.5 | 0 | 71327.5 | 322819 | -845743 | 21 | 24 | 322819 | -1845743
11 | 29 | 8 | 3 | 49.4627 | 0 | 168.222 | 41.5185 | 0 | 0 | 6.2315 | 19.0363 | 0 | 0 | 0 | 0.8 | 285.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86595.6 | 0 | 86595.6 | 384332 | -757546 | 21 | 24 | 384332 | -1757546
11 | 29 | 9 | 3 | 41.4344 | 0 | 173.795 | 29.1636 | 0 | 0 | 6.2413 | 19.0363 | 0 | 0 | 0 | 0 | 269.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119806 | 0 | 119806 | 403101 | -587800 | 22 | 25 | 403101 | -1587800
11 | 29 | 10 | 3 | 41.6316 | 0 | 172.186 | 0 | 25.4493 | 0 | 6.2668 | 19.0363 | 0 | 0 | 0 | 0 | 264.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140947 | 0 | 140947 | 401391 | -492035 | 25 | 29 | 401391 | -1492035
11 | 29 | 11 | 3 | 41.4955 | 0 | 163.102 | 0 | 26.3746 | 0 | 6.2922 | 19.0363 | 0 | 0 | 0 | 0 | 256.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143962 | 0 | 143962 | 393476 | -436279 | 27 | 33 | 393476 | -1436279
11 | 29 | 12 | 3 | 40.8077 | 0 | 149.692 | 0 | 25.1977 | 0 | 25.3223 | 19.0363 | 0 | 0 | 0 | 0 | 260.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143960 | 0 | 143960 | 378778 | -342059 | 29 | 37 | 378778 | -1342059
11 | 29 | 13 | 3 | 39.857 | 0 | 150.207 | 0 | 22.902 | 0 | 25.3209 | 19.0363 | 0 | 0 | 0 | 0 | 257.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143958 | 0 | 143958 | 356902 | -313477 | 30 | 38 | 356902 | -1313477
11 | 29 | 14 | 3 | 41.3301 | 0 | 165.698 | 0 | 26.0774 | 0 | 25.3283 | 19.0363 | 0 | 0 | 0 | 0 | 277.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143956 | 0 | 143956 | 403365 | -293367 | 30 | 39 | 403365 | -1293367
11 | 29 | 15 | 3 | 40.7776 | 0 | 172.702 | 0 | 28.5116 | 0 | 25.335 | 19.0363 | 0 | 0 | 0 | 0 | 286.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142096 | 0 | 142096 | 433590 | -285360 | 30 | 40 | 433590 | -1285360
11 | 29 | 16 | 3 | 43.5789 | 0 | 173.986 | 0 | 27.5233 | 0 | 25.3318 | 19.0363 | 0 | 0 | 0 | 0 | 289.456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129187 | 0 | 129187 | 425071 | -299755 | 30 | 38 | 425071 | -1299755
11 | 29 | 17 | 3 | 55.5706 | 0 | 169.782 | 0 | 25.7864 | 0 | 25.3174 | 19.0363 | 0 | 0 | 0 | 2.4 | 297.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105470 | 0 | 105470 | 405302 | -332571 | 30 | 36 | 405302 | -1332571
11 | 29 | 18 | 3 | 49.7836 | 0 | 152.497 | 0 | 24.8459 | 0 | 25.291 | 19.0363 | 0 | 0 | 0 | 6.4 | 277.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79119.3 | 0 | 79119.3 | 390900 | -411796 | 28 | 34 | 390900 | -1411796
11 | 29 | 19 | 3 | 34.11 | 0 | 93.4203 | 25.3989 | 0 | 0 | 6.2899 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49024.2 | 0 | 49024.2 | 302041 | -459105 | 28 | 33 | 302041 | -1459105
11 | 29 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.0895 | 0 | 5.9501 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35104.1 | 0 | 35104.1 | 182987 | -11951.2 | 28 | 33 | 182987 | -1011951.2
11 | 29 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 12.3356 | 0 | 5.9177 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31168.3 | 0 | 31168.3 | 163734 | -16514.3 | 26 | 32 | 163734 | -1016514.3
11 | 29 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.2036 | 0 | 5.911 | 12.9754 | 0 | 0 | 0 | 7.2 | 101.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19169.1 | 0 | 19169.1 | 150494 | -20826.1 | 28 | 32 | 150494 | -1020826.1
11 | 29 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.3769 | 0 | 5.9025 | 12.9754 | 0 | 0 | 0 | 6.4 | 92.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10364.5 | 0 | 10364.5 | 139258 | -21129.9 | 28 | 33 | 139258 | -1021129.9
11 | 29 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 12.7557 | 0 | 5.9181 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9033.92 | 0 | 9033.92 | 157285 | -37976.1 | 29 | 33 | 157285 | -1037976.1
11 | 30 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.5048 | 0 | 5.9144 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9037.38 | 0 | 9037.38 | 153319 | -44193.3 | 29 | 33 | 153319 | -1044193.3
11 | 30 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.2837 | 0 | 5.9117 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.4196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9040.52 | 0 | 9040.52 | 150979 | -52490.4 | 29 | 34 | 150979 | -1052490.4
11 | 30 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.1218 | 0 | 5.9098 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9043.3 | 0 | 9043.3 | 149156 | -61733.3 | 28 | 34 | 149156 | -1061733.3
11 | 30 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 12.0136 | 0 | 5.9087 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9045.67 | 0 | 9045.67 | 147946 | -67948.9 | 29 | 34 | 147946 | -1067948.9
11 | 30 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 12.1604 | 0 | 5.9105 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10031.9 | 0 | 10031.9 | 150231 | -72281.1 | 29 | 35 | 150231 | -1072281.1
11 | 30 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 15.9093 | 0 | 5.9937 | 17.5105 | 0 | 0 | 0 | 4.8 | 138.501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24159.1 | 0 | 24159.1 | 201647 | -58452.2 | 29 | 35 | 201647 | -1058452.2
11 | 30 | 7 | 4 | 49.0171 | 0 | 140.608 | 32.18 | 0 | 0 | 6.2363 | 19.0363 | 0 | 0 | 0 | 3.2 | 250.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71316.2 | 0 | 71316.2 | 324231 | -635641 | 27 | 31 | 324231 | -1635641
11 | 30 | 8 | 4 | 51.1255 | 0 | 168.222 | 34.489 | 0 | 0 | 6.2436 | 19.0363 | 0 | 0 | 0 | 0.8 | 279.917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86584.1 | 0 | 86584.1 | 385599 | -654608 | 23 | 27 | 385599 | -1654608
11 | 30 | 9 | 4 | 41.0695 | 0 | 173.795 | 29.1259 | 0 | 0 | 6.2465 | 19.0363 | 0 | 0 | 0 | 0 | 269.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119798 | 0 | 119798 | 404251 | -584204 | 20 | 23 | 404251 | -1584204
11 | 30 | 10 | 4 | 41.0549 | 0 | 172.186 | 27.7438 | 0 | 0 | 6.2548 | 19.0363 | 0 | 0 | 0 | 0 | 266.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140940 | 0 | 140940 | 402311 | -547531 | 20 | 24 | 402311 | -1547531
11 | 30 | 11 | 4 | 41.2576 | 0 | 163.102 | 29.2365 | 0 | 0 | 6.2666 | 19.0363 | 0 | 0 | 0 | 0 | 258.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143956 | 0 | 143956 | 389963 | -546648 | 20 | 24 | 389963 | -1546648
11 | 30 | 12 | 4 | 40.7976 | 0 | 149.692 | 25.747 | 0 | 0 | 6.283 | 19.0363 | 0 | 0 | 0 | 0 | 241.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143955 | 0 | 143955 | 378214 | -483558 | 20 | 25 | 378214 | -1483558
11 | 30 | 13 | 4 | 39.8542 | 0 | 150.207 | 27.0866 | 0 | 0 | 6.2661 | 19.0363 | 0 | 0 | 0 | 0 | 242.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143954 | 0 | 143954 | 356895 | -515424 | 19 | 24 | 356895 | -1515424
11 | 30 | 14 | 4 | 41.3318 | 0 | 165.698 | 24.9181 | 0 | 0 | 6.2669 | 19.0363 | 0 | 0 | 0 | 0 | 257.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143952 | 0 | 143952 | 389554 | -498250 | 18 | 22 | 389554 | -1498250
11 | 30 | 15 | 4 | 42.6857 | 0 | 172.702 | 26.9589 | 0 | 0 | 6.2635 | 19.0363 | 0 | 0 | 0 | 0 | 267.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142093 | 0 | 142093 | 408055 | -533775 | 17 | 21 | 408055 | -1533775
11 | 30 | 16 | 4 | 48.225 | 0 | 173.986 | 29.0026 | 0 | 0 | 6.2579 | 19.0363 | 0 | 0 | 0 | 0 | 276.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129186 | 0 | 129186 | 410973 | -572465 | 16 | 20 | 410973 | -1572465
11 | 30 | 17 | 4 | 56.9034 | 0 | 169.782 | 33.0967 | 0 | 0 | 6.252 | 19.0363 | 0 | 0 | 0 | 2.4 | 287.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105471 | 0 | 105471 | 402718 | -637556 | 15 | 18 | 402718 | -1637556
11 | 30 | 18 | 4 | 49.7836 | 0 | 152.497 | 39.6039 | 0 | 0 | 6.2459 | 19.0363 | 0 | 0 | 0 | 6.4 | 273.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79122.5 | 0 | 79122.5 | 392182 | -716548 | 14 | 17 | 392182 | -1716548
11 | 30 | 19 | 4 | 34.11 | 0 | 93.4203 | 43.8 | 0 | 0 | 6.2559 | 19.0363 | 0 | 0 | 0 | 7.2 | 203.822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49028.9 | 0 | 49028.9 | 309589 | -727806 | 14 | 17 | 309589 | -1727806
11 | 30 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.1319 | 0 | 5.9499 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35108.5 | 0 | 35108.5 | 181796 | -19525.9 | 14 | 17 | 181796 | -1019525.9
11 | 30 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.1112 | 0 | 5.9291 | 15.4625 | 0 | 0 | 0 | 7.2 | 115.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31172.3 | 0 | 31172.3 | 171437 | -40659.1 | 15 | 17 | 171437 | -1040659.1
11 | 30 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.1089 | 0 | 5.9295 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19173.2 | 0 | 19173.2 | 172274 | -74992 | 16 | 19 | 172274 | -1074992
11 | 30 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.0228 | 0 | 5.9122 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10370.6 | 0 | 10370.6 | 157131 | -106835 | 17 | 20 | 157131 | -1106835
11 | 30 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.6245 | 0 | 5.9072 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9041.06 | 0 | 9041.06 | 150911 | -119778 | 19 | 21 | 150911 | -1119778
12 | 1 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.471 | 0 | 5.9055 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9844.31 | 0 | 9844.31 | 148613 | -129530 | 22 | 24 | 148613 | -1129530
12 | 1 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3859 | 0 | 5.9045 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.56 | 0 | 9847.56 | 146654 | -130932 | 23 | 26 | 146654 | -1130932
12 | 1 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3406 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9850.46 | 0 | 9850.46 | 145047 | -129516 | 25 | 27 | 145047 | -1129516
12 | 1 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3165 | 0 | 5.9034 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.99 | 0 | 9852.99 | 143998 | -127790 | 27 | 29 | 143998 | -1127790
12 | 1 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.5293 | 0 | 5.9052 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.3895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10938.2 | 0 | 10938.2 | 146443 | -126749 | 28 | 30 | 146443 | -1126749
12 | 1 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 15.0243 | 0 | 5.9711 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26487.7 | 0 | 26487.7 | 194284 | -95681 | 29 | 32 | 194284 | -1095681
12 | 1 | 7 | 5 | 49.0171 | 0 | 140.608 | 37.032 | 0 | 0 | 6.2408 | 19.0633 | 0 | 0 | 0 | 3.2 | 255.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78393 | 0 | 78393 | 323473 | -675225 | 32 | 34 | 323473 | -1675225
12 | 1 | 8 | 5 | 52.7252 | 0 | 168.222 | 32.3513 | 0 | 0 | 6.255 | 19.0363 | 0 | 0 | 0 | 0.8 | 279.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95198.5 | 0 | 95198.5 | 385156 | -602498 | 32 | 34 | 385156 | -1602498
12 | 1 | 9 | 5 | 45.4899 | 0 | 173.795 | 0 | 25.5701 | 0 | 6.2667 | 19.0363 | 0 | 0 | 0 | 0 | 270.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131754 | 0 | 131754 | 403583 | -480803 | 32 | 35 | 403583 | -1480803
12 | 1 | 10 | 5 | 44.215 | 0 | 172.186 | 0 | 25.5018 | 0 | 6.2795 | 19.0363 | 0 | 0 | 0 | 0 | 267.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155024 | 0 | 155024 | 401922 | -449942 | 33 | 35 | 401922 | -1449942
12 | 1 | 11 | 5 | 42.4986 | 0 | 163.102 | 0 | 26.0423 | 0 | 6.2882 | 19.0363 | 0 | 0 | 0 | 0 | 256.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158342 | 0 | 158342 | 394536 | -438076 | 33 | 36 | 394536 | -1438076
12 | 1 | 12 | 5 | 41.6911 | 0 | 149.692 | 0 | 25.0674 | 0 | 6.2913 | 19.0363 | 0 | 0 | 0 | 0 | 241.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158341 | 0 | 158341 | 380044 | -406205 | 33 | 36 | 380044 | -1406205
12 | 1 | 13 | 5 | 40.0836 | 0 | 150.207 | 0 | 23.0273 | 0 | 6.2829 | 19.0363 | 0 | 0 | 0 | 0 | 238.637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158339 | 0 | 158339 | 357054 | -402056 | 33 | 36 | 357054 | -1402056
12 | 1 | 14 | 5 | 42.7761 | 0 | 165.698 | 0 | 24.7758 | 0 | 6.2895 | 19.0363 | 0 | 0 | 0 | 0 | 258.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158338 | 0 | 158338 | 390262 | -368754 | 34 | 35 | 390262 | -1368754
12 | 1 | 15 | 5 | 42.6437 | 0 | 172.702 | 0 | 25.9388 | 0 | 25.3026 | 19.0363 | 0 | 0 | 0 | 0 | 285.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156291 | 0 | 156291 | 408556 | -355881 | 34 | 35 | 408556 | -1355881
12 | 1 | 16 | 5 | 48.749 | 0 | 173.986 | 0 | 26.1185 | 0 | 25.3078 | 19.0363 | 0 | 0 | 0 | 0 | 293.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142083 | 0 | 142083 | 411144 | -352535 | 34 | 35 | 411144 | -1352535
12 | 1 | 17 | 5 | 56.7046 | 0 | 169.782 | 0 | 25.676 | 0 | 25.3016 | 19.0363 | 0 | 0 | 0 | 2.4 | 298.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115978 | 0 | 115978 | 404080 | -377104 | 33 | 34 | 404080 | -1377104
12 | 1 | 18 | 5 | 49.7836 | 0 | 152.497 | 0 | 25.2618 | 0 | 25.2902 | 19.0363 | 0 | 0 | 0 | 6.4 | 278.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86973.9 | 0 | 86973.9 | 388999 | -421222 | 33 | 34 | 388999 | -1421222
12 | 1 | 19 | 5 | 34.11 | 0 | 93.4203 | 25.771 | 0 | 0 | 6.2916 | 19.0363 | 0 | 0 | 0 | 7.2 | 185.829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53848.5 | 0 | 53848.5 | 302031 | -459168 | 33 | 34 | 302031 | -1459168
12 | 1 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 13.7995 | 0 | 5.9461 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38526.6 | 0 | 38526.6 | 182958 | -11201.2 | 33 | 33 | 182958 | -1011201.2
12 | 1 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.1829 | 0 | 5.9164 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34194.5 | 0 | 34194.5 | 163745 | -15959.7 | 32 | 33 | 163745 | -1015959.7
12 | 1 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.0861 | 0 | 5.91 | 12.9754 | 0 | 0 | 0 | 7.2 | 100.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20986.5 | 0 | 20986.5 | 150267 | -20324 | 32 | 33 | 150267 | -1020324
12 | 1 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.5428 | 0 | 5.9155 | 15.0234 | 0 | 0 | 0 | 6.4 | 95.4122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11294.9 | 0 | 11294.9 | 155338 | -23551.8 | 32 | 33 | 155338 | -1023551.8
12 | 1 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 12.6607 | 0 | 5.9166 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.5457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9830.04 | 0 | 9830.04 | 155431 | -38737.1 | 32 | 33 | 155431 | -1038737.1
12 | 2 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.3877 | 0 | 5.913 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9833.51 | 0 | 9833.51 | 152147 | -49253.8 | 32 | 33 | 152147 | -1049253.8
12 | 2 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.1857 | 0 | 5.9105 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9836.69 | 0 | 9836.69 | 149733 | -58215.7 | 33 | 33 | 149733 | -1058215.7
12 | 2 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 12.0522 | 0 | 5.909 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9840.22 | 0 | 9840.22 | 148056 | -66149.6 | 33 | 33 | 148056 | -1066149.6
12 | 2 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.932 | 0 | 5.9077 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9842.93 | 0 | 9842.93 | 146533 | -73726.2 | 33 | 33 | 146533 | -1073726.2
12 | 2 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.8276 | 0 | 5.9066 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.0249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9845.5 | 0 | 9845.5 | 145307 | -78951.2 | 33 | 33 | 145307 | -1078951.2
12 | 2 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.7697 | 0 | 5.906 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.74 | 0 | 9847.74 | 144460 | -85308.3 | 33 | 33 | 144460 | -1085308.3
12 | 2 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.676 | 0 | 5.9051 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.88 | 0 | 9849.88 | 143129 | -89123.8 | 33 | 33 | 143129 | -1089123.8
12 | 2 | 8 | 6 | 6.2587 | 0 | 42.7453 | 45.0139 | 0 | 0 | 6.2408 | 19.0548 | 0 | 0 | 0 | 0.8 | 120.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.91 | 0 | 9851.91 | 130039 | -774514 | 33 | 34 | 130039 | -1774514
12 | 2 | 9 | 6 | 6.2345 | 0 | 42.7453 | 41.6017 | 0 | 0 | 6.2399 | 18.9351 | 0 | 0 | 0 | 0 | 115.756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.63 | 0 | 9853.63 | 154255 | -705970 | 33 | 34 | 154255 | -1705970
12 | 2 | 10 | 6 | 6.4875 | 0 | 42.7453 | 33.3401 | 0 | 0 | 6.2439 | 18.8896 | 0 | 0 | 0 | 0 | 107.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9846.95 | 0 | 9846.95 | 159236 | -596370 | 34 | 35 | 159236 | -1596370
12 | 2 | 11 | 6 | 6.3422 | 0 | 42.7453 | 30.5715 | 0 | 0 | 6.2439 | 18.8896 | 0 | 0 | 0 | 0 | 104.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9843.41 | 0 | 9843.41 | 155283 | -556721 | 34 | 35 | 155283 | -1556721
12 | 2 | 12 | 6 | 6.118 | 0 | 42.7453 | 28.2065 | 0 | 0 | 6.2441 | 18.8896 | 0 | 0 | 0 | 0 | 102.204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9842.34 | 0 | 9842.34 | 155051 | -519923 | 35 | 36 | 155051 | -1519923
12 | 2 | 13 | 6 | 6.2436 | 0 | 42.7453 | 27.1131 | 0 | 0 | 6.2428 | 18.8896 | 0 | 0 | 0 | 0 | 101.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9841.68 | 0 | 9841.68 | 152082 | -505877 | 35 | 36 | 152082 | -1505877
12 | 2 | 14 | 6 | 6.2916 | 0 | 42.7453 | 26.2128 | 0 | 0 | 6.2416 | 18.8896 | 0 | 0 | 0 | 0 | 100.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9841.4 | 0 | 9841.4 | 149364 | -492722 | 35 | 36 | 149364 | -1492722
12 | 2 | 15 | 6 | 6.6586 | 0 | 42.7453 | 0 | 9.6466 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 77.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9841.23 | 0 | 9841.23 | 124120 | -11267.9 | 35 | 36 | 124120 | -1011267.9
12 | 2 | 16 | 6 | 7.6617 | 0 | 42.7453 | 0 | 9.3256 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 0 | 78.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9841.34 | 0 | 9841.34 | 123202 | -15045.9 | 35 | 36 | 123202 | -1015045.9
12 | 2 | 17 | 6 | 8.7164 | 0 | 42.7453 | 0 | 10.0189 | 0 | 5.8968 | 12.8287 | 0 | 0 | 0 | 2.4 | 82.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9843.89 | 0 | 9843.89 | 123123 | -19434 | 35 | 36 | 123123 | -1019434
12 | 2 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.5036 | 0 | 5.9042 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.7142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.28 | 0 | 9847.28 | 143731 | -37347.4 | 36 | 36 | 143731 | -1037347.4
12 | 2 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.6291 | 0 | 5.9042 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.6397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.52 | 0 | 9849.52 | 140872 | -45753.2 | 35 | 36 | 140872 | -1045753.2
12 | 2 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.4948 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.37 | 0 | 9852.37 | 139277 | -51620.8 | 35 | 36 | 139277 | -1051620.8
12 | 2 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.3939 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.81 | 0 | 9854.81 | 138156 | -61306.4 | 36 | 36 | 138156 | -1061306.4
12 | 2 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.304 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.01 | 0 | 9857.01 | 137085 | -68895.2 | 35 | 36 | 137085 | -1068895.2
12 | 2 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.2428 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.06 | 0 | 9859.06 | 136469 | -74617.9 | 35 | 36 | 136469 | -1074617.9
12 | 2 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.1789 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.94 | 0 | 9860.94 | 135826 | -79404.6 | 35 | 36 | 135826 | -1079404.6
12 | 3 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0819 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3748.7 | 0 | 3748.7 | 134932 | -85305.4 | 35 | 36 | 134932 | -1085305.4
12 | 3 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 11.0326 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3750.43 | 0 | 3750.43 | 134522 | -91682.9 | 35 | 36 | 134522 | -1091682.9
12 | 3 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9772 | 0 | 5.8998 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3752.28 | 0 | 3752.28 | 133788 | -94355.4 | 35 | 36 | 133788 | -1094355.4
12 | 3 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9466 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3754.01 | 0 | 3754.01 | 133425 | -97824.4 | 35 | 36 | 133425 | -1097824.4
12 | 3 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.9034 | 0 | 5.8994 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3755.7 | 0 | 3755.7 | 132790 | -100273 | 34 | 36 | 132790 | -1100273
12 | 3 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8734 | 0 | 5.8992 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3757.34 | 0 | 3757.34 | 132407 | -103693 | 34 | 36 | 132407 | -1103693
12 | 3 | 7 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.8646 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 3.2 | 85.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3758.93 | 0 | 3758.93 | 132239 | -107432 | 34 | 36 | 132239 | -1107432
12 | 3 | 8 | 7 | 4.9862 | 0 | 42.7453 | 0 | 10.8169 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3760.48 | 0 | 3760.48 | 131549 | -110649 | 34 | 35 | 131549 | -1110649
12 | 3 | 9 | 7 | 4.7051 | 0 | 42.7453 | 0 | 10.7801 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 0 | 81.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3762.01 | 0 | 3762.01 | 131311 | -106553 | 33 | 35 | 131311 | -1106553
12 | 3 | 10 | 7 | 4.9279 | 0 | 42.7453 | 0 | 10.7988 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 0 | 81.7346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3763.49 | 0 | 3763.49 | 131619 | -96620.1 | 34 | 36 | 131619 | -1096620.1
12 | 3 | 11 | 7 | 4.8245 | 0 | 42.7453 | 0 | 10.7717 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 0 | 81.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3764.93 | 0 | 3764.93 | 131050 | -90542.5 | 34 | 36 | 131050 | -1090542.5
12 | 3 | 12 | 7 | 4.6897 | 0 | 42.7453 | 0 | 10.7579 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 81.4553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.36 | 0 | 3766.36 | 130884 | -81995.3 | 34 | 37 | 130884 | -1081995.3
12 | 3 | 13 | 7 | 4.7071 | 0 | 42.7453 | 0 | 10.8035 | 0 | 5.8988 | 17.3638 | 0 | 0 | 0 | 0 | 81.5184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3767.65 | 0 | 3767.65 | 131361 | -80541.6 | 34 | 37 | 131361 | -1080541.6
12 | 3 | 14 | 7 | 4.8206 | 0 | 42.7453 | 0 | 10.753 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 0 | 81.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3768.93 | 0 | 3768.93 | 130510 | -84567.8 | 34 | 36 | 130510 | -1084567.8
12 | 3 | 15 | 7 | 4.9951 | 0 | 42.7453 | 0 | 10.7111 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 0 | 81.7138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3770.15 | 0 | 3770.15 | 130157 | -92182.1 | 33 | 36 | 130157 | -1092182.1
12 | 3 | 16 | 7 | 5.7477 | 0 | 42.7453 | 0 | 10.6889 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 82.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3771.37 | 0 | 3771.37 | 129976 | -103511 | 33 | 36 | 129976 | -1103511
12 | 3 | 17 | 7 | 6.6025 | 0 | 42.7453 | 0 | 10.6454 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3772.64 | 0 | 3772.64 | 129406 | -114727 | 33 | 35 | 129406 | -1114727
12 | 3 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.6032 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3773.97 | 0 | 3773.97 | 129115 | -121998 | 33 | 35 | 129115 | -1121998
12 | 3 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5673 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3775.32 | 0 | 3775.32 | 128858 | -126690 | 33 | 35 | 128858 | -1126690
12 | 3 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5483 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.4185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3776.61 | 0 | 3776.61 | 128612 | -128806 | 33 | 35 | 128612 | -1128806
12 | 3 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5295 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.91 | 0 | 3777.91 | 128386 | -131195 | 33 | 35 | 128386 | -1131195
12 | 3 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.5174 | 0 | 5.8978 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.3875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.16 | 0 | 3779.16 | 128238 | -133264 | 33 | 35 | 128238 | -1133264
12 | 3 | 23 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4922 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.5622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3780.38 | 0 | 3780.38 | 127920 | -137024 | 32 | 34 | 127920 | -1137024
12 | 3 | 24 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4592 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.7291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3781.59 | 0 | 3781.59 | 127666 | -139463 | 32 | 34 | 127666 | -1139463
12 | 4 | 1 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4456 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9896.79 | 0 | 9896.79 | 127795 | -141291 | 31 | 33 | 127795 | -1141291
12 | 4 | 2 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4194 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9897.96 | 0 | 9897.96 | 127738 | -146842 | 31 | 33 | 127738 | -1146842
12 | 4 | 3 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.4232 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9898.32 | 0 | 9898.32 | 127852 | -153305 | 30 | 32 | 127852 | -1153305
12 | 4 | 4 | 1 | 10.8489 | 0 | 42.3304 | 0 | 10.3753 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9899.18 | 0 | 9899.18 | 127361 | -161484 | 29 | 30 | 127361 | -1161484
12 | 4 | 5 | 1 | 11.8202 | 0 | 44.8242 | 0 | 10.5359 | 0 | 5.898 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.3889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10983.1 | 0 | 10983.1 | 130346 | -172413 | 27 | 28 | 130346 | -1172413
12 | 4 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.8568 | 0 | 5.9413 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26531.5 | 0 | 26531.5 | 177773 | -151749 | 25 | 26 | 177773 | -1151749
12 | 4 | 7 | 1 | 49.0171 | 0 | 140.608 | 52.7096 | 0 | 0 | 6.2143 | 19.3693 | 0 | 0 | 0 | 3.2 | 271.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78436 | 0 | 78436 | 312320 | -935579 | 26 | 27 | 312320 | -1935579
12 | 4 | 8 | 1 | 52.1636 | 0 | 168.222 | 45.4357 | 0 | 0 | 6.2283 | 19.1604 | 0 | 0 | 0 | 0.8 | 292.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95240.7 | 0 | 95240.7 | 374733 | -810962 | 27 | 27 | 374733 | -1810962
12 | 4 | 9 | 1 | 49.0821 | 0 | 173.795 | 33.5299 | 0 | 0 | 6.2344 | 19.0363 | 0 | 0 | 0 | 0 | 281.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131788 | 0 | 131788 | 393875 | -663496 | 27 | 28 | 393875 | -1663496
12 | 4 | 10 | 1 | 43.1955 | 0 | 172.186 | 32.1994 | 0 | 0 | 6.2486 | 19.0363 | 0 | 0 | 0 | 0 | 272.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155056 | 0 | 155056 | 392472 | -613799 | 28 | 30 | 392472 | -1613799
12 | 4 | 11 | 1 | 42.8477 | 0 | 163.102 | 33.0413 | 0 | 0 | 6.2607 | 19.0363 | 0 | 0 | 0 | 0 | 264.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158373 | 0 | 158373 | 382950 | -599893 | 29 | 31 | 382950 | -1599893
12 | 4 | 12 | 1 | 41.8362 | 0 | 149.692 | 28.6021 | 0 | 0 | 6.2705 | 19.0363 | 0 | 0 | 0 | 0 | 245.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158371 | 0 | 158371 | 364759 | -527982 | 30 | 33 | 364759 | -1527982
12 | 4 | 13 | 1 | 40.4203 | 0 | 150.207 | 26.8055 | 0 | 0 | 6.2691 | 19.0363 | 0 | 0 | 0 | 0 | 242.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158369 | 0 | 158369 | 348934 | -507589 | 31 | 34 | 348934 | -1507589
12 | 4 | 14 | 1 | 44.0023 | 0 | 165.698 | 0 | 24.2766 | 0 | 6.2776 | 19.0363 | 0 | 0 | 0 | 0 | 259.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158366 | 0 | 158366 | 382686 | -428568 | 32 | 36 | 382686 | -1428568
12 | 4 | 15 | 1 | 45.9865 | 0 | 172.702 | 0 | 26.538 | 0 | 6.2887 | 19.0363 | 0 | 0 | 0 | 0 | 270.551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156319 | 0 | 156319 | 412264 | -402889 | 32 | 37 | 412264 | -1402889
12 | 4 | 16 | 1 | 49.2137 | 0 | 173.986 | 0 | 26.6765 | 0 | 6.2966 | 19.0363 | 0 | 0 | 0 | 0 | 275.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142110 | 0 | 142110 | 414512 | -376229 | 34 | 38 | 414512 | -1376229
12 | 4 | 17 | 1 | 56.9121 | 0 | 169.782 | 0 | 26.9176 | 0 | 6.3012 | 19.0363 | 0 | 0 | 0 | 2.4 | 281.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116004 | 0 | 116004 | 414287 | -374214 | 35 | 39 | 414287 | -1374214
12 | 4 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 25.0862 | 0 | 6.2943 | 19.0363 | 0 | 0 | 0 | 6.4 | 259.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86998.7 | 0 | 86998.7 | 386272 | -383191 | 36 | 40 | 386272 | -1383191
12 | 4 | 19 | 1 | 34.11 | 0 | 93.4203 | 26.3631 | 0 | 0 | 6.286 | 19.0363 | 0 | 0 | 0 | 7.2 | 186.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53871.8 | 0 | 53871.8 | 322761 | -474929 | 34 | 38 | 322761 | -1474929
12 | 4 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 12.4436 | 0 | 5.9273 | 12.9754 | 0 | 0 | 0 | 7.2 | 125.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38548.8 | 0 | 38548.8 | 177403 | -9020.24 | 31 | 35 | 177403 | -1009020.24
12 | 4 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 11.615 | 0 | 5.9099 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34217.4 | 0 | 34217.4 | 158373 | -15389.6 | 28 | 33 | 158373 | -1015389.6
12 | 4 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 11.7782 | 0 | 5.9064 | 12.9754 | 0 | 0 | 0 | 7.2 | 100.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21010.8 | 0 | 21010.8 | 145302 | -21029.9 | 28 | 31 | 145302 | -1021029.9
12 | 4 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.4385 | 0 | 5.9141 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11319.7 | 0 | 11319.7 | 154292 | -55608.5 | 26 | 30 | 154292 | -1055608.5
12 | 4 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.8419 | 0 | 5.9072 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.2 | 0 | 9855.2 | 146723 | -75569.7 | 24 | 28 | 146723 | -1075569.7
12 | 5 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.516 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.31 | 0 | 9859.31 | 143846 | -92382.6 | 24 | 27 | 143846 | -1092382.6
12 | 5 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.3038 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.48 | 0 | 9862.48 | 141990 | -113379 | 23 | 25 | 141990 | -1113379
12 | 5 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.129 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9865.4 | 0 | 9865.4 | 140644 | -130533 | 21 | 24 | 140644 | -1130533
12 | 5 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 10.9779 | 0 | 5.9008 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.93 | 0 | 9867.93 | 139525 | -148845 | 20 | 23 | 139525 | -1148845
12 | 5 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.0671 | 0 | 5.9017 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10953.3 | 0 | 10953.3 | 141641 | -163619 | 19 | 21 | 141641 | -1163619
12 | 5 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.2407 | 0 | 5.9543 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26503 | 0 | 26503 | 188574 | -150503 | 17 | 20 | 188574 | -1150503
12 | 5 | 7 | 2 | 49.0171 | 0 | 140.608 | 51.3269 | 0 | 0 | 6.2095 | 19.2117 | 0 | 0 | 0 | 3.2 | 269.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78408.6 | 0 | 78408.6 | 319653 | -935244 | 17 | 20 | 319653 | -1935244
12 | 5 | 8 | 2 | 51.0124 | 0 | 168.222 | 46.0893 | 0 | 0 | 6.2198 | 19.0775 | 0 | 0 | 0 | 0.8 | 291.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95214.4 | 0 | 95214.4 | 381641 | -846037 | 17 | 20 | 381641 | -1846037
12 | 5 | 9 | 2 | 42.0699 | 0 | 173.795 | 36.8617 | 0 | 0 | 6.2292 | 19.0363 | 0 | 0 | 0 | 0 | 277.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131770 | 0 | 131770 | 400522 | -724247 | 17 | 20 | 400522 | -1724247
12 | 5 | 10 | 2 | 41.0269 | 0 | 172.186 | 36.076 | 0 | 0 | 6.2406 | 19.0363 | 0 | 0 | 0 | 0 | 274.566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155040 | 0 | 155040 | 398597 | -681751 | 18 | 21 | 398597 | -1681751
12 | 5 | 11 | 2 | 41.27 | 0 | 163.102 | 38.4617 | 0 | 0 | 6.2485 | 19.0363 | 0 | 0 | 0 | 0 | 268.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158359 | 0 | 158359 | 387371 | -694764 | 19 | 22 | 387371 | -1694764
12 | 5 | 12 | 2 | 40.8231 | 0 | 149.692 | 33.6663 | 0 | 0 | 6.2591 | 19.0363 | 0 | 0 | 0 | 0 | 249.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158358 | 0 | 158358 | 366282 | -604235 | 19 | 23 | 366282 | -1604235
12 | 5 | 13 | 2 | 39.8585 | 0 | 150.207 | 31.2945 | 0 | 0 | 6.2538 | 19.0363 | 0 | 0 | 0 | 0 | 246.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158356 | 0 | 158356 | 353606 | -582876 | 19 | 23 | 353606 | -1582876
12 | 5 | 14 | 2 | 41.3465 | 0 | 165.698 | 27.9147 | 0 | 0 | 6.2493 | 19.0363 | 0 | 0 | 0 | 0 | 260.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 386628 | -554757 | 19 | 22 | 386628 | -1554757
12 | 5 | 15 | 2 | 41.3716 | 0 | 172.702 | 27.1078 | 0 | 0 | 6.258 | 19.0363 | 0 | 0 | 0 | 0 | 266.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156307 | 0 | 156307 | 405102 | -539078 | 19 | 22 | 405102 | -1539078
12 | 5 | 16 | 2 | 42.8565 | 0 | 173.986 | 28.8392 | 0 | 0 | 6.2577 | 19.0363 | 0 | 0 | 0 | 0 | 270.976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142100 | 0 | 142100 | 408068 | -571698 | 18 | 21 | 408068 | -1571698
12 | 5 | 17 | 2 | 55.721 | 0 | 169.782 | 33.315 | 0 | 0 | 6.253 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115996 | 0 | 115996 | 402253 | -633456 | 17 | 20 | 402253 | -1633456
12 | 5 | 18 | 2 | 49.7836 | 0 | 152.497 | 39.5798 | 0 | 0 | 6.2464 | 19.0363 | 0 | 0 | 0 | 6.4 | 273.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86993.3 | 0 | 86993.3 | 389466 | -711602 | 16 | 19 | 389466 | -1711602
12 | 5 | 19 | 2 | 34.11 | 0 | 93.4203 | 44.7895 | 0 | 0 | 6.2535 | 19.0363 | 0 | 0 | 0 | 7.2 | 204.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53868.4 | 0 | 53868.4 | 307715 | -742631 | 16 | 18 | 307715 | -1742631
12 | 5 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 13.9822 | 0 | 5.9462 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38546.4 | 0 | 38546.4 | 179515 | -19328.3 | 15 | 18 | 179515 | -1019328.3
12 | 5 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 14.0291 | 0 | 5.9488 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34213.7 | 0 | 34213.7 | 184412 | -51907.3 | 14 | 17 | 184412 | -1051907.3
12 | 5 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 12.647 | 0 | 5.9217 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21007 | 0 | 21007 | 166244 | -94728.4 | 14 | 16 | 166244 | -1094728.4
12 | 5 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 11.6265 | 0 | 5.9077 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.9753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11317.7 | 0 | 11317.7 | 152295 | -135080 | 14 | 16 | 152295 | -1135080
12 | 5 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.1375 | 0 | 5.9031 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.97 | 0 | 9853.97 | 146127 | -156272 | 13 | 15 | 146127 | -1156272
12 | 6 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.9283 | 0 | 5.9016 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858.36 | 0 | 9858.36 | 143800 | -177940 | 13 | 15 | 143800 | -1177940
12 | 6 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.7897 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.73 | 0 | 9861.73 | 142216 | -194107 | 13 | 14 | 142216 | -1194107
12 | 6 | 3 | 3 | 10.8489 | 0 | 42.3304 | 11.2663 | 0 | 0 | 5.9047 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9864.73 | 0 | 9864.73 | 140925 | -205142 | 12 | 14 | 140925 | -1205142
12 | 6 | 4 | 3 | 10.8489 | 0 | 42.3304 | 11.8777 | 0 | 0 | 5.9117 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.42 | 0 | 9867.42 | 139780 | -216337 | 12 | 14 | 139780 | -1216337
12 | 6 | 5 | 3 | 11.8202 | 0 | 44.8242 | 12.8658 | 0 | 0 | 5.9199 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10953 | 0 | 10953 | 141689 | -228706 | 12 | 13 | 141689 | -1228706
12 | 6 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 13.7255 | 0 | 5.9471 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26502.9 | 0 | 26502.9 | 188288 | -207721 | 12 | 13 | 188288 | -1207721
12 | 6 | 7 | 3 | 49.0171 | 0 | 140.608 | 60.1833 | 0 | 0 | 6.2043 | 19.3576 | 0 | 0 | 0 | 3.2 | 278.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78408.7 | 0 | 78408.7 | 319939 | -1081220 | 13 | 14 | 319939 | -2081220
12 | 6 | 8 | 3 | 51.245 | 0 | 168.222 | 52.0208 | 0 | 0 | 6.2085 | 19.1534 | 0 | 0 | 0 | 0.8 | 297.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95214.6 | 0 | 95214.6 | 382006 | -965776 | 13 | 15 | 382006 | -1965776
12 | 6 | 9 | 3 | 42.1302 | 0 | 173.795 | 41.2836 | 0 | 0 | 6.2222 | 19.0363 | 0 | 0 | 0 | 0 | 282.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131768 | 0 | 131768 | 400979 | -790816 | 14 | 16 | 400979 | -1790816
12 | 6 | 10 | 3 | 41.7117 | 0 | 172.186 | 36.7054 | 0 | 0 | 6.2325 | 19.0363 | 0 | 0 | 0 | 0 | 275.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155038 | 0 | 155038 | 399009 | -703798 | 16 | 18 | 399009 | -1703798
12 | 6 | 11 | 3 | 41.5814 | 0 | 163.102 | 35.0889 | 0 | 0 | 6.244 | 19.0363 | 0 | 0 | 0 | 0 | 265.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158356 | 0 | 158356 | 380532 | -652303 | 18 | 21 | 380532 | -1652303
12 | 6 | 12 | 3 | 40.9622 | 0 | 149.692 | 31.7918 | 0 | 0 | 6.268 | 19.0363 | 0 | 0 | 0 | 0 | 247.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158356 | 0 | 158356 | 368544 | -564846 | 19 | 23 | 368544 | -1564846
12 | 6 | 13 | 3 | 39.8656 | 0 | 150.207 | 30.2872 | 0 | 0 | 6.2669 | 19.0363 | 0 | 0 | 0 | 0 | 245.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158354 | 0 | 158354 | 354014 | -551980 | 20 | 23 | 354014 | -1551980
12 | 6 | 14 | 3 | 41.4751 | 0 | 165.698 | 0 | 25.0255 | 0 | 25.2742 | 19.0363 | 0 | 0 | 0 | 0 | 276.509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158351 | 0 | 158351 | 387138 | -493080 | 20 | 24 | 387138 | -1493080
12 | 6 | 15 | 3 | 40.8542 | 0 | 172.702 | 0 | 25.6879 | 0 | 25.2762 | 19.0363 | 0 | 0 | 0 | 0 | 283.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156304 | 0 | 156304 | 405586 | -495878 | 20 | 24 | 405586 | -1495878
12 | 6 | 16 | 3 | 42.1465 | 0 | 173.986 | 26.6231 | 0 | 0 | 6.269 | 19.0363 | 0 | 0 | 0 | 0 | 268.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142097 | 0 | 142097 | 408607 | -526208 | 20 | 23 | 408607 | -1526208
12 | 6 | 17 | 3 | 55.7681 | 0 | 169.782 | 31.9695 | 0 | 0 | 6.2576 | 19.0363 | 0 | 0 | 0 | 2.4 | 285.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115993 | 0 | 115993 | 402045 | -607537 | 19 | 21 | 402045 | -1607537
12 | 6 | 18 | 3 | 49.7836 | 0 | 152.497 | 38.5134 | 0 | 0 | 6.248 | 19.0363 | 0 | 0 | 0 | 6.4 | 272.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86990.3 | 0 | 86990.3 | 392153 | -692399 | 17 | 20 | 392153 | -1692399
12 | 6 | 19 | 3 | 34.11 | 0 | 93.4203 | 43.7753 | 0 | 0 | 6.256 | 19.0363 | 0 | 0 | 0 | 7.2 | 203.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53865.6 | 0 | 53865.6 | 309742 | -726408 | 17 | 19 | 309742 | -1726408
12 | 6 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.037 | 0 | 5.9472 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38543.7 | 0 | 38543.7 | 179907 | -19527.7 | 16 | 18 | 179907 | -1019527.7
12 | 6 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.0836 | 0 | 5.9503 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34211.1 | 0 | 34211.1 | 185444 | -47663.6 | 15 | 17 | 185444 | -1047663.6
12 | 6 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.6934 | 0 | 5.9225 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21004.3 | 0 | 21004.3 | 166989 | -93285.3 | 15 | 16 | 166989 | -1093285.3
12 | 6 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.671 | 0 | 5.9082 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11314.9 | 0 | 11314.9 | 152857 | -130546 | 14 | 15 | 152857 | -1130546
12 | 6 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.17 | 0 | 5.9034 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.0418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.17 | 0 | 9851.17 | 146533 | -157070 | 13 | 14 | 146533 | -1157070
12 | 7 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.9235 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.56 | 0 | 9855.56 | 144233 | -178973 | 13 | 14 | 144233 | -1178973
12 | 7 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.7928 | 0 | 5.9008 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.04 | 0 | 9859.04 | 142675 | -193068 | 13 | 14 | 142675 | -1193068
12 | 7 | 3 | 4 | 10.73 | 0 | 42.3304 | 11.1366 | 0 | 0 | 5.9035 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.1 | 0 | 9862.1 | 141349 | -201767 | 13 | 14 | 141349 | -1201767
12 | 7 | 4 | 4 | 10.73 | 0 | 42.3304 | 11.694 | 0 | 0 | 5.9093 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9864.86 | 0 | 9864.86 | 140327 | -211992 | 13 | 14 | 140327 | -1211992
12 | 7 | 5 | 4 | 11.8202 | 0 | 44.8242 | 12.135 | 0 | 0 | 5.9138 | 17.5105 | 0 | 0 | 0 | 4.8 | 97.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10950.5 | 0 | 10950.5 | 142106 | -217575 | 14 | 15 | 142106 | -1217575
12 | 7 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 13.7958 | 0 | 5.9484 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26500.3 | 0 | 26500.3 | 188858 | -196325 | 14 | 15 | 188858 | -1196325
12 | 7 | 7 | 4 | 49.0171 | 0 | 140.608 | 58.3899 | 0 | 0 | 6.2046 | 19.3145 | 0 | 0 | 0 | 3.2 | 276.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78406.1 | 0 | 78406.1 | 320209 | -1048080 | 15 | 16 | 320209 | -2048080
12 | 7 | 8 | 4 | 52.3617 | 0 | 168.222 | 50.3859 | 0 | 0 | 6.2113 | 19.1343 | 0 | 0 | 0 | 0.8 | 297.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95212 | 0 | 95212 | 382257 | -926930 | 16 | 18 | 382257 | -1926930
12 | 7 | 9 | 4 | 42.8056 | 0 | 173.795 | 41.867 | 0 | 0 | 6.7016 | 19.0363 | 0 | 0 | 0 | 0 | 284.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131765 | 0 | 131765 | 401303 | -789389 | 17 | 19 | 401303 | -1789389
12 | 7 | 10 | 4 | 41.211 | 0 | 172.186 | 38.1095 | 0 | 0 | 6.7109 | 19.0363 | 0 | 0 | 0 | 0 | 277.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155035 | 0 | 155035 | 399270 | -717385 | 18 | 20 | 399270 | -1717385
12 | 7 | 11 | 4 | 41.3085 | 0 | 163.102 | 38.2262 | 0 | 0 | 6.5414 | 19.0363 | 0 | 0 | 0 | 0 | 268.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158354 | 0 | 158354 | 380556 | -707717 | 18 | 20 | 380556 | -1707717
12 | 7 | 12 | 4 | 40.8133 | 0 | 149.692 | 34.1567 | 0 | 0 | 6.2565 | 19.0363 | 0 | 0 | 0 | 0 | 249.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 364405 | -609612 | 18 | 21 | 364405 | -1609612
12 | 7 | 13 | 4 | 39.8656 | 0 | 150.207 | 32.0768 | 0 | 0 | 6.2596 | 19.0363 | 0 | 0 | 0 | 0 | 247.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158351 | 0 | 158351 | 354092 | -583490 | 19 | 22 | 354092 | -1583490
12 | 7 | 14 | 4 | 41.3422 | 0 | 165.698 | 27.1974 | 0 | 0 | 6.2637 | 19.0363 | 0 | 0 | 0 | 0 | 259.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158349 | 0 | 158349 | 387043 | -533729 | 19 | 22 | 387043 | -1533729
12 | 7 | 15 | 4 | 41.4225 | 0 | 172.702 | 0 | 25.6841 | 0 | 25.2726 | 19.0363 | 0 | 0 | 0 | 0 | 284.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156302 | 0 | 156302 | 405632 | -509844 | 20 | 23 | 405632 | -1509844
12 | 7 | 16 | 4 | 42.4845 | 0 | 173.986 | 27.7387 | 0 | 0 | 6.2642 | 19.0363 | 0 | 0 | 0 | 0 | 269.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142096 | 0 | 142096 | 408651 | -548147 | 19 | 22 | 408651 | -1548147
12 | 7 | 17 | 4 | 55.8112 | 0 | 169.782 | 33.1679 | 0 | 0 | 6.2515 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115992 | 0 | 115992 | 401788 | -633799 | 18 | 20 | 401788 | -1633799
12 | 7 | 18 | 4 | 49.7836 | 0 | 152.497 | 39.9472 | 0 | 0 | 6.2434 | 19.0363 | 0 | 0 | 0 | 6.4 | 273.908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86989 | 0 | 86989 | 392343 | -719693 | 17 | 19 | 392343 | -1719693
12 | 7 | 19 | 4 | 34.11 | 0 | 93.4203 | 45.3767 | 0 | 0 | 6.2506 | 19.0363 | 0 | 0 | 0 | 7.2 | 205.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53864.4 | 0 | 53864.4 | 309886 | -753434 | 16 | 18 | 309886 | -1753434
12 | 7 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 13.9661 | 0 | 5.9462 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38542.4 | 0 | 38542.4 | 179755 | -19725.8 | 15 | 16 | 179755 | -1019725.8
12 | 7 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.9734 | 0 | 5.9483 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34209.7 | 0 | 34209.7 | 184900 | -52497.4 | 14 | 15 | 184900 | -1052497.4
12 | 7 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 12.6039 | 0 | 5.9215 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21002.9 | 0 | 21002.9 | 166592 | -101885 | 13 | 14 | 166592 | -1101885
12 | 7 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.5953 | 0 | 5.9075 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11313.7 | 0 | 11313.7 | 152461 | -143874 | 12 | 12 | 152461 | -1143874
12 | 7 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.072 | 0 | 5.9028 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9850.05 | 0 | 9850.05 | 146228 | -167726 | 10 | 11 | 146228 | -1167726
12 | 8 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.8581 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.5 | 0 | 9854.5 | 143903 | -194094 | 9 | 10 | 143903 | -1194094
12 | 8 | 2 | 5 | 10.8489 | 0 | 42.3304 | 11.3245 | 0 | 0 | 5.905 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.97 | 0 | 9857.97 | 142240 | -207152 | 9 | 10 | 142240 | -1207152
12 | 8 | 3 | 5 | 10.8489 | 0 | 42.3304 | 12.2541 | 0 | 0 | 5.9142 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.5114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.12 | 0 | 9861.12 | 141507 | -222839 | 8 | 9 | 141507 | -1222839
12 | 8 | 4 | 5 | 10.8489 | 0 | 42.3304 | 12.7323 | 0 | 0 | 5.9192 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.9947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.91 | 0 | 9863.91 | 139563 | -229059 | 8 | 9 | 139563 | -1229059
12 | 8 | 5 | 5 | 11.8202 | 0 | 44.8242 | 13.6246 | 0 | 0 | 5.9292 | 17.5105 | 0 | 0 | 0 | 4.8 | 98.5087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10949.6 | 0 | 10949.6 | 143528 | -242778 | 8 | 9 | 143528 | -1242778
12 | 8 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 13.7506 | 0 | 5.9451 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26499.6 | 0 | 26499.6 | 187891 | -211279 | 8 | 9 | 187891 | -1211279
12 | 8 | 7 | 5 | 49.0171 | 0 | 140.608 | 61.3481 | 0 | 0 | 6.2052 | 19.3466 | 0 | 0 | 0 | 3.2 | 279.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78405.5 | 0 | 78405.5 | 319479 | -1119880 | 10 | 10 | 319479 | -2119880
12 | 8 | 8 | 5 | 50.8053 | 0 | 168.222 | 52.291 | 0 | 0 | 6.2064 | 19.1208 | 0 | 0 | 0 | 0.8 | 297.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95211.3 | 0 | 95211.3 | 381538 | -984383 | 11 | 12 | 381538 | -1984383
12 | 8 | 9 | 5 | 42.3291 | 0 | 173.795 | 41.1801 | 0 | 0 | 6.2179 | 19.0363 | 0 | 0 | 0 | 0 | 282.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131765 | 0 | 131765 | 400810 | -804492 | 12 | 13 | 400810 | -1804492
12 | 8 | 10 | 5 | 42.095 | 0 | 172.186 | 36.2715 | 0 | 0 | 6.2316 | 19.0363 | 0 | 0 | 0 | 0 | 275.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155035 | 0 | 155035 | 398706 | -709063 | 14 | 16 | 398706 | -1709063
12 | 8 | 11 | 5 | 41.6454 | 0 | 163.102 | 36.6689 | 0 | 0 | 6.2371 | 19.0363 | 0 | 0 | 0 | 0 | 266.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158354 | 0 | 158354 | 380064 | -690521 | 17 | 18 | 380064 | -1690521
12 | 8 | 12 | 5 | 41.0682 | 0 | 149.692 | 32.7156 | 0 | 0 | 6.2637 | 19.0363 | 0 | 0 | 0 | 0 | 248.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 366660 | -584626 | 18 | 21 | 366660 | -1584626
12 | 8 | 13 | 5 | 39.8665 | 0 | 150.207 | 31.3055 | 0 | 0 | 6.2666 | 19.0363 | 0 | 0 | 0 | 0 | 246.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158351 | 0 | 158351 | 353658 | -562135 | 19 | 22 | 353658 | -1562135
12 | 8 | 14 | 5 | 41.7305 | 0 | 165.698 | 0 | 25.3003 | 0 | 25.2779 | 19.0363 | 0 | 0 | 0 | 0 | 277.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158348 | 0 | 158348 | 386757 | -486527 | 20 | 24 | 386757 | -1486527
12 | 8 | 15 | 5 | 41.6759 | 0 | 172.702 | 0 | 25.6882 | 0 | 25.2836 | 19.0363 | 0 | 0 | 0 | 0 | 284.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156302 | 0 | 156302 | 405340 | -462052 | 21 | 25 | 405340 | -1462052
12 | 8 | 16 | 5 | 42.9441 | 0 | 173.986 | 0 | 25.8735 | 0 | 25.2776 | 19.0363 | 0 | 0 | 0 | 0 | 287.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142095 | 0 | 142095 | 408351 | -501635 | 20 | 23 | 408351 | -1501635
12 | 8 | 17 | 5 | 55.1949 | 0 | 169.782 | 29.2671 | 0 | 0 | 6.264 | 19.0363 | 0 | 0 | 0 | 2.4 | 281.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115991 | 0 | 115991 | 401611 | -571667 | 18 | 21 | 401611 | -1571667
12 | 8 | 18 | 5 | 49.7836 | 0 | 152.497 | 37.106 | 0 | 0 | 6.2517 | 19.0363 | 0 | 0 | 0 | 6.4 | 271.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86988 | 0 | 86988 | 396925 | -678616 | 17 | 19 | 396925 | -1678616
12 | 8 | 19 | 5 | 34.11 | 0 | 93.4203 | 42.7661 | 0 | 0 | 6.2557 | 19.0363 | 0 | 0 | 0 | 7.2 | 202.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53863.4 | 0 | 53863.4 | 311640 | -707888 | 17 | 19 | 311640 | -1707888
12 | 8 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.1361 | 0 | 5.9485 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38541.6 | 0 | 38541.6 | 179766 | -19726.2 | 17 | 19 | 179766 | -1019726.2
12 | 8 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 14.2812 | 0 | 5.9537 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34208.7 | 0 | 34208.7 | 186289 | -41037 | 17 | 19 | 186289 | -1041037
12 | 8 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.8745 | 0 | 5.9247 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21001.5 | 0 | 21001.5 | 167785 | -76192 | 18 | 20 | 167785 | -1076192
12 | 8 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.8464 | 0 | 5.9096 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11311.8 | 0 | 11311.8 | 153681 | -103551 | 19 | 21 | 153681 | -1103551
12 | 8 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.401 | 0 | 5.9048 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.83 | 0 | 9847.83 | 147319 | -119642 | 19 | 22 | 147319 | -1119642
12 | 9 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2094 | 0 | 5.903 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.98 | 0 | 9851.98 | 144578 | -134419 | 19 | 22 | 144578 | -1134419
12 | 9 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0818 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.25 | 0 | 9855.25 | 142889 | -145630 | 20 | 23 | 142889 | -1145630
12 | 9 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0433 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858.67 | 0 | 9858.67 | 142277 | -156075 | 20 | 23 | 142277 | -1156075
12 | 9 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.9245 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.39 | 0 | 9861.39 | 140528 | -161627 | 20 | 23 | 140528 | -1161627
12 | 9 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8594 | 0 | 5.9004 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.93 | 0 | 9863.93 | 139740 | -167163 | 20 | 24 | 139740 | -1167163
12 | 9 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7935 | 0 | 5.9 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.22 | 0 | 9866.22 | 138578 | -171460 | 20 | 24 | 138578 | -1171460
12 | 9 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.741 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.3314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9868.43 | 0 | 9868.43 | 137724 | -175209 | 21 | 24 | 137724 | -1175209
12 | 9 | 8 | 6 | 6.3328 | 0 | 42.7453 | 63.6423 | 0 | 0 | 6.2222 | 19.5673 | 0 | 0 | 0 | 0.8 | 139.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9870.55 | 0 | 9870.55 | 124479 | -1014070 | 21 | 25 | 124479 | -2014070
12 | 9 | 9 | 6 | 6.6488 | 0 | 42.7453 | 54.3074 | 0 | 0 | 6.2277 | 19.1952 | 0 | 0 | 0 | 0 | 129.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9872.31 | 0 | 9872.31 | 129357 | -883113 | 21 | 25 | 129357 | -1883113
12 | 9 | 10 | 6 | 7.0202 | 0 | 42.7453 | 44.8533 | 0 | 0 | 6.2299 | 18.9652 | 0 | 0 | 0 | 0 | 119.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.29 | 0 | 9859.29 | 126214 | -769135 | 22 | 26 | 126214 | -1769135
12 | 9 | 11 | 6 | 6.6681 | 0 | 42.7453 | 41.161 | 0 | 0 | 6.2312 | 18.8971 | 0 | 0 | 0 | 0 | 115.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.54 | 0 | 9855.54 | 125449 | -717715 | 23 | 27 | 125449 | -1717715
12 | 9 | 12 | 6 | 6.3053 | 0 | 42.7453 | 38.2587 | 0 | 0 | 6.233 | 18.8896 | 0 | 0 | 0 | 0 | 112.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.57 | 0 | 9853.57 | 124725 | -676058 | 23 | 28 | 124725 | -1676058
12 | 9 | 13 | 6 | 6.433 | 0 | 42.7453 | 36.2647 | 0 | 0 | 6.2341 | 18.8896 | 0 | 0 | 0 | 0 | 110.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.53 | 0 | 9852.53 | 124498 | -647065 | 24 | 29 | 124498 | -1647065
12 | 9 | 14 | 6 | 6.5195 | 0 | 42.7453 | 34.9885 | 0 | 0 | 6.2336 | 18.8896 | 0 | 0 | 0 | 0 | 109.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.87 | 0 | 9851.87 | 123671 | -630663 | 24 | 29 | 123671 | -1630663
12 | 9 | 15 | 6 | 7.0039 | 0 | 42.7453 | 0 | 9.997 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 78.4717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.38 | 0 | 9851.38 | 121207 | -17050.7 | 24 | 30 | 121207 | -1017050.7
12 | 9 | 16 | 6 | 7.7944 | 0 | 42.7453 | 0 | 10.4803 | 0 | 5.8978 | 15.3158 | 0 | 0 | 0 | 0 | 82.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.21 | 0 | 9851.21 | 129201 | -38774.9 | 25 | 30 | 129201 | -1038774.9
12 | 9 | 17 | 6 | 8.7213 | 0 | 42.7453 | 0 | 11.2308 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 2.4 | 88.3631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.57 | 0 | 9855.57 | 139962 | -62886.2 | 25 | 30 | 139962 | -1062886.2
12 | 9 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.962 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.1685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.46 | 0 | 9860.46 | 136222 | -85637.6 | 25 | 30 | 136222 | -1085637.6
12 | 9 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8561 | 0 | 5.8996 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.72 | 0 | 9863.72 | 134951 | -101854 | 25 | 30 | 134951 | -1101854
12 | 9 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7584 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.79 | 0 | 9866.79 | 133731 | -111258 | 25 | 30 | 133731 | -1111258
12 | 9 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6886 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9869.19 | 0 | 9869.19 | 132992 | -119894 | 25 | 30 | 132992 | -1119894
12 | 9 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6407 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9871.4 | 0 | 9871.4 | 132489 | -125480 | 26 | 30 | 132489 | -1125480
12 | 9 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.6076 | 0 | 5.8984 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.8123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9873.43 | 0 | 9873.43 | 132079 | -129763 | 26 | 30 | 132079 | -1129763
12 | 9 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.5652 | 0 | 5.8982 | 17.3638 | 0 | 0 | 0 | 5.6 | 90.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9875.33 | 0 | 9875.33 | 131431 | -132718 | 25 | 30 | 131431 | -1132718
12 | 10 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.5142 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.4267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3763.12 | 0 | 3763.12 | 130828 | -138377 | 26 | 30 | 130828 | -1138377
12 | 10 | 2 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4694 | 0 | 5.8979 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.3818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3764.85 | 0 | 3764.85 | 130329 | -144961 | 25 | 29 | 130329 | -1144961
12 | 10 | 3 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.4169 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.7 | 0 | 3766.7 | 129793 | -152384 | 25 | 29 | 129793 | -1152384
12 | 10 | 4 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3922 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3768.39 | 0 | 3768.39 | 129606 | -157325 | 25 | 29 | 129606 | -1157325
12 | 10 | 5 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3522 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3770.06 | 0 | 3770.06 | 128984 | -163094 | 25 | 28 | 128984 | -1163094
12 | 10 | 6 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3103 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3771.72 | 0 | 3771.72 | 128568 | -166732 | 25 | 28 | 128568 | -1166732
12 | 10 | 7 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.3339 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 3.2 | 84.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3773.33 | 0 | 3773.33 | 128898 | -169581 | 25 | 29 | 128898 | -1169581
12 | 10 | 8 | 7 | 5.0487 | 0 | 42.7453 | 0 | 10.2755 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0.8 | 82.1306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3774.88 | 0 | 3774.88 | 127954 | -169615 | 26 | 29 | 127954 | -1169615
12 | 10 | 9 | 7 | 4.966 | 0 | 42.7453 | 0 | 10.2754 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 81.2477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3776.44 | 0 | 3776.44 | 127953 | -164520 | 26 | 30 | 127953 | -1164520
12 | 10 | 10 | 7 | 4.2324 | 0 | 42.7453 | 0 | 10.2746 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 0 | 80.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.91 | 0 | 3777.91 | 127764 | -131796 | 27 | 31 | 127764 | -1131796
12 | 10 | 11 | 7 | 4.157 | 0 | 42.7453 | 0 | 10.3878 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.34 | 0 | 3779.34 | 128948 | -111143 | 29 | 33 | 128948 | -1111143
12 | 10 | 12 | 7 | 4.1514 | 0 | 42.7453 | 0 | 10.3956 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3780.7 | 0 | 3780.7 | 128321 | -94118.4 | 29 | 34 | 128321 | -1094118.4
12 | 10 | 13 | 7 | 4.1641 | 0 | 42.7453 | 0 | 10.4465 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.6172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3781.82 | 0 | 3781.82 | 128423 | -96102.4 | 30 | 34 | 128423 | -1096102.4
12 | 10 | 14 | 7 | 4.153 | 0 | 42.7453 | 0 | 10.4421 | 0 | 5.8976 | 17.3638 | 0 | 0 | 0 | 0 | 80.6017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3782.77 | 0 | 3782.77 | 128112 | -93186 | 30 | 35 | 128112 | -1093186
12 | 10 | 15 | 7 | 4.3581 | 0 | 42.7453 | 0 | 10.4765 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 0 | 80.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3783.59 | 0 | 3783.59 | 128410 | -104280 | 30 | 35 | 128410 | -1104280
12 | 10 | 16 | 7 | 5.0506 | 0 | 42.7453 | 0 | 10.4055 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 81.4627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3784.68 | 0 | 3784.68 | 127320 | -112107 | 29 | 34 | 127320 | -1112107
12 | 10 | 17 | 7 | 6.5616 | 0 | 42.7453 | 0 | 10.3583 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.3263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3785.71 | 0 | 3785.71 | 126925 | -135767 | 29 | 33 | 126925 | -1135767
12 | 10 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3116 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.3812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.92 | 0 | 3786.92 | 126611 | -150651 | 28 | 32 | 126611 | -1150651
12 | 10 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2727 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.12 | 0 | 3788.12 | 126444 | -158194 | 28 | 32 | 126444 | -1158194
12 | 10 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2446 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3789.33 | 0 | 3789.33 | 126250 | -163330 | 28 | 32 | 126250 | -1163330
12 | 10 | 21 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2226 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3790.5 | 0 | 3790.5 | 126036 | -166350 | 28 | 32 | 126036 | -1166350
12 | 10 | 22 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2072 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3791.67 | 0 | 3791.67 | 125920 | -171223 | 28 | 31 | 125920 | -1171223
12 | 10 | 23 | 7 | 6.6633 | 0 | 42.7453 | 10.1774 | 0 | 0 | 5.8957 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792.8 | 0 | 3792.8 | 125718 | -174844 | 27 | 31 | 125718 | -1174844
12 | 10 | 24 | 7 | 6.6633 | 0 | 42.7453 | 10.5212 | 0 | 0 | 5.8943 | 17.3638 | 0 | 0 | 0 | 5.6 | 88.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3793.91 | 0 | 3793.91 | 125526 | -180640 | 27 | 30 | 125526 | -1180640
12 | 11 | 1 | 1 | 10.8489 | 0 | 42.3304 | 10.7445 | 0 | 0 | 5.8937 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9909.03 | 0 | 9909.03 | 125697 | -185019 | 26 | 29 | 125697 | -1185019
12 | 11 | 2 | 1 | 10.8489 | 0 | 42.3304 | 11.0824 | 0 | 0 | 5.8939 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9910.14 | 0 | 9910.14 | 125620 | -191628 | 26 | 28 | 125620 | -1191628
12 | 11 | 3 | 1 | 10.8489 | 0 | 42.3304 | 11.4687 | 0 | 0 | 5.8934 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9910.41 | 0 | 9910.41 | 125446 | -197291 | 25 | 27 | 125446 | -1197291
12 | 11 | 4 | 1 | 10.8489 | 0 | 42.3304 | 11.6099 | 0 | 0 | 5.8938 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9911.21 | 0 | 9911.21 | 125356 | -201073 | 26 | 28 | 125356 | -1201073
12 | 11 | 5 | 1 | 11.8202 | 0 | 44.8242 | 11.9305 | 0 | 0 | 5.8924 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10995 | 0 | 10995 | 128571 | -203697 | 27 | 28 | 128571 | -1203697
12 | 11 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.602 | 0 | 5.937 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26543.4 | 0 | 26543.4 | 176101 | -163534 | 27 | 29 | 176101 | -1163534
12 | 11 | 7 | 1 | 49.0171 | 0 | 140.608 | 52.7159 | 0 | 0 | 6.2166 | 19.3834 | 0 | 0 | 0 | 3.2 | 271.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78447.7 | 0 | 78447.7 | 311527 | -916525 | 29 | 31 | 311527 | -1916525
12 | 11 | 8 | 1 | 51.2415 | 0 | 168.222 | 42.3826 | 0 | 0 | 6.2346 | 19.167 | 0 | 0 | 0 | 0.8 | 288.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95252.2 | 0 | 95252.2 | 374206 | -758082 | 30 | 32 | 374206 | -1758082
12 | 11 | 9 | 1 | 42.3388 | 0 | 173.795 | 28.2158 | 0 | 0 | 6.2463 | 19.0363 | 0 | 0 | 0 | 0 | 269.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131795 | 0 | 131795 | 393067 | -557926 | 32 | 34 | 393067 | -1557926
12 | 11 | 10 | 1 | 41.6688 | 0 | 172.186 | 0 | 25.3984 | 0 | 6.2725 | 19.0363 | 0 | 0 | 0 | 0 | 264.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155064 | 0 | 155064 | 391940 | -457223 | 34 | 37 | 391940 | -1457223
12 | 11 | 11 | 1 | 41.2978 | 0 | 163.102 | 0 | 27.0872 | 0 | 6.2938 | 19.0363 | 0 | 0 | 0 | 0 | 256.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158380 | 0 | 158380 | 401334 | -412195 | 36 | 40 | 401334 | -1412195
12 | 11 | 12 | 1 | 40.792 | 0 | 149.692 | 0 | 27.7638 | 0 | 6.2984 | 19.0363 | 0 | 0 | 0 | 0 | 243.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158377 | 0 | 158377 | 411122 | -374599 | 38 | 43 | 411122 | -1374599
12 | 11 | 13 | 1 | 39.8473 | 0 | 150.207 | 0 | 26.1978 | 0 | 6.3006 | 19.0363 | 0 | 0 | 0 | 0 | 241.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158374 | 0 | 158374 | 386878 | -340068 | 39 | 44 | 386878 | -1340068
12 | 11 | 14 | 1 | 41.3156 | 0 | 165.698 | 0 | 30.4778 | 0 | 6.3299 | 19.0363 | 0 | 0 | 0 | 0 | 262.857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158371 | 0 | 158371 | 438420 | -288385 | 40 | 46 | 438420 | -1288385
12 | 11 | 15 | 1 | 42.3165 | 0 | 172.702 | 0 | 32.3314 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156323 | 0 | 156323 | 456958 | -279240 | 41 | 47 | 456958 | -1279240
12 | 11 | 16 | 1 | 44.3108 | 0 | 173.986 | 0 | 31.6167 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 275.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142113 | 0 | 142113 | 450051 | -285895 | 40 | 46 | 450051 | -1285895
12 | 11 | 17 | 1 | 56.0719 | 0 | 169.782 | 0 | 31.5016 | 0 | 6.3271 | 19.0363 | 0 | 0 | 0 | 2.4 | 285.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116005 | 0 | 116005 | 457542 | -311167 | 40 | 44 | 457542 | -1311167
12 | 11 | 18 | 1 | 49.7836 | 0 | 152.497 | 0 | 27.6315 | 0 | 6.3108 | 19.0363 | 0 | 0 | 0 | 6.4 | 261.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86999.3 | 0 | 86999.3 | 413573 | -338488 | 39 | 43 | 413573 | -1338488
12 | 11 | 19 | 1 | 34.11 | 0 | 93.4203 | 0 | 24.2467 | 0 | 6.2908 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53872.5 | 0 | 53872.5 | 347371 | -415662 | 40 | 43 | 347371 | -1415662
12 | 11 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 8.8562 | 0 | 5.4861 | 12.9754 | 0 | 0 | 0 | 7.2 | 121.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38549.9 | 0 | 38549.9 | 178118 | 0 | 41 | 44 | 178118 | -1000000
12 | 11 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 10.0097 | 0 | 5.902 | 12.9754 | 0 | 0 | 0 | 7.2 | 109.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34218.4 | 0 | 34218.4 | 159068 | -8290.85 | 42 | 44 | 159068 | -1008290.85
12 | 11 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 9.87 | 0 | 5.8986 | 12.9754 | 0 | 0 | 0 | 7.2 | 98.6643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21012.2 | 0 | 21012.2 | 145840 | -11512.2 | 43 | 45 | 145840 | -1011512.2
12 | 11 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 9.2483 | 0 | 5.8968 | 12.9754 | 0 | 0 | 0 | 6.4 | 90.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11320.1 | 0 | 11320.1 | 135010 | -11765.7 | 44 | 47 | 135010 | -1011765.7
12 | 11 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 9.0827 | 0 | 5.8967 | 12.9754 | 0 | 0 | 0 | 5.6 | 86.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.82 | 0 | 9854.82 | 130549 | -12400.4 | 45 | 48 | 130549 | -1012400.4
12 | 12 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 8.8521 | 0 | 5.8969 | 12.8287 | 0 | 0 | 0 | 4.8 | 85.1321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.4 | 0 | 9857.4 | 129292 | -11749.5 | 46 | 48 | 129292 | -1011749.5
12 | 12 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.5569 | 0 | 5.8974 | 14.8767 | 0 | 0 | 0 | 4.8 | 87.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.25 | 0 | 9859.25 | 141377 | -13373.6 | 46 | 49 | 141377 | -1013373.6
12 | 12 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.3738 | 0 | 5.897 | 15.3158 | 0 | 0 | 0 | 4.8 | 88.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.73 | 0 | 9860.73 | 137739 | -12681.4 | 46 | 49 | 137739 | -1012681.4
12 | 12 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 9.3456 | 0 | 5.897 | 14.8767 | 0 | 0 | 0 | 4.8 | 87.6737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.93 | 0 | 9861.93 | 139414 | -13227.6 | 46 | 49 | 139414 | -1013227.6
12 | 12 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 9.5156 | 0 | 5.8974 | 15.0234 | 0 | 0 | 0 | 4.8 | 91.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10946.3 | 0 | 10946.3 | 141577 | -13782.6 | 46 | 49 | 141577 | -1013782.6
12 | 12 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 11.9813 | 0 | 5.927 | 15.4625 | 0 | 0 | 0 | 4.8 | 132.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26494.8 | 0 | 26494.8 | 187026 | -12634.3 | 46 | 49 | 187026 | -1012634.3
12 | 12 | 7 | 2 | 49.0171 | 0 | 140.608 | 0 | 23.8309 | 0 | 6.2862 | 19.0363 | 0 | 0 | 0 | 3.2 | 241.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78399.1 | 0 | 78399.1 | 323333 | -370558 | 47 | 50 | 323333 | -1370558
12 | 12 | 8 | 2 | 52.8883 | 0 | 168.222 | 0 | 31.4435 | 0 | 6.3106 | 19.0363 | 0 | 0 | 0 | 0.8 | 278.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95204.1 | 0 | 95204.1 | 433631 | -330134 | 47 | 50 | 433631 | -1330134
12 | 12 | 9 | 2 | 49.6149 | 0 | 173.795 | 0 | 33.1253 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 281.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131764 | 0 | 131764 | 448556 | -240784 | 48 | 51 | 448556 | -1240784
12 | 12 | 10 | 2 | 41.1567 | 0 | 172.186 | 0 | 33.4712 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 272.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155030 | 0 | 155030 | 446857 | -203042 | 49 | 52 | 446857 | -1203042
12 | 12 | 11 | 2 | 41.2601 | 0 | 163.102 | 0 | 32.5227 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 262.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158346 | 0 | 158346 | 425257 | -149349 | 50 | 54 | 425257 | -1149349
12 | 12 | 12 | 2 | 40.7911 | 0 | 149.692 | 0 | 31.583 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 247.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158342 | 0 | 158342 | 406463 | -128345 | 51 | 55 | 406463 | -1128345
12 | 12 | 13 | 2 | 39.8557 | 0 | 150.207 | 0 | 30.5829 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 246.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158339 | 0 | 158339 | 399813 | -116332 | 51 | 55 | 399813 | -1116332
12 | 12 | 14 | 2 | 41.4531 | 0 | 165.698 | 0 | 31.9739 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 264.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158336 | 0 | 158336 | 442661 | -101428 | 52 | 55 | 442661 | -1101428
12 | 12 | 15 | 2 | 47.8354 | 0 | 172.702 | 0 | 33.0264 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 278.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156288 | 0 | 156288 | 466433 | -96369.9 | 52 | 55 | 466433 | -1096369.9
12 | 12 | 16 | 2 | 50.1468 | 0 | 173.986 | 0 | 33.1216 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 0 | 282.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142079 | 0 | 142079 | 480426 | -97060.1 | 52 | 54 | 480426 | -1097060.1
12 | 12 | 17 | 2 | 56.9254 | 0 | 169.782 | 0 | 31.4491 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 2.4 | 285.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115973 | 0 | 115973 | 469067 | -97384.4 | 51 | 54 | 469067 | -1097384.4
12 | 12 | 18 | 2 | 49.7836 | 0 | 152.497 | 0 | 29.4832 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 6.4 | 263.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86968 | 0 | 86968 | 434761 | -116365 | 51 | 53 | 434761 | -1116365
12 | 12 | 19 | 2 | 34.11 | 0 | 93.4203 | 0 | 24.2176 | 0 | 6.332 | 19.0363 | 0 | 0 | 0 | 7.2 | 184.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53842 | 0 | 53842 | 322434 | -186507 | 48 | 51 | 322434 | -1186507
12 | 12 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 9.1082 | 0 | 5.4894 | 8.818 | 0 | 0 | 0 | 7.2 | 117.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38519.9 | 0 | 38519.9 | 184152 | 0 | 44 | 48 | 184152 | -1000000
12 | 12 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 8.1304 | 0 | 5.48 | 8.818 | 0 | 0 | 0 | 7.2 | 102.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34188 | 0 | 34188 | 164726 | 0 | 41 | 46 | 164726 | -1000000
12 | 12 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 10.7677 | 0 | 5.9028 | 12.9754 | 0 | 0 | 0 | 7.2 | 99.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20980.3 | 0 | 20980.3 | 151302 | -9159.3 | 36 | 40 | 151302 | -1009159.3
12 | 12 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 6.9957 | 0 | 5.4801 | 8.818 | 0 | 0 | 0 | 6.4 | 83.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11287.2 | 0 | 11287.2 | 140024 | 0 | 31 | 34 | 140024 | -1000000
12 | 12 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.1856 | 0 | 5.9008 | 12.9754 | 0 | 0 | 0 | 5.6 | 88.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9821.94 | 0 | 9821.94 | 135011 | -21262.2 | 26 | 28 | 135011 | -1021262.2
12 | 13 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 7.4186 | 0 | 5.8968 | 14.8767 | 0 | 0 | 0 | 4.8 | 86.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9824.98 | 0 | 9824.98 | 149713 | -17152.9 | 23 | 25 | 149713 | -1017152.9
12 | 13 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 12.3538 | 0 | 5.9131 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9827.98 | 0 | 9827.98 | 153411 | -51350.4 | 21 | 23 | 153411 | -1051350.4
12 | 13 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 12.077 | 0 | 5.9102 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.3303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9831.23 | 0 | 9831.23 | 151078 | -65845.5 | 18 | 20 | 151078 | -1065845.5
12 | 13 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.7322 | 0 | 5.9071 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9834.87 | 0 | 9834.87 | 148630 | -85186.8 | 18 | 20 | 148630 | -1085186.8
12 | 13 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.7032 | 0 | 5.9073 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10921.3 | 0 | 10921.3 | 149946 | -109154 | 18 | 20 | 149946 | -1109154
12 | 13 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.86 | 0 | 5.9706 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26472 | 0 | 26472 | 196789 | -101125 | 18 | 20 | 196789 | -1101125
12 | 13 | 7 | 3 | 49.0171 | 0 | 140.608 | 41.5403 | 0 | 0 | 6.2217 | 19.0363 | 0 | 0 | 0 | 3.2 | 259.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78378.7 | 0 | 78378.7 | 324398 | -785177 | 19 | 20 | 324398 | -1785177
12 | 13 | 8 | 3 | 52.9007 | 0 | 168.222 | 39.7285 | 0 | 0 | 6.2368 | 19.0363 | 0 | 0 | 0 | 0.8 | 286.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95185.3 | 0 | 95185.3 | 385360 | -735922 | 19 | 21 | 385360 | -1735922
12 | 13 | 9 | 3 | 46.31 | 0 | 173.795 | 31.8689 | 0 | 0 | 6.2415 | 19.0363 | 0 | 0 | 0 | 0 | 277.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131748 | 0 | 131748 | 404145 | -640713 | 20 | 21 | 404145 | -1640713
12 | 13 | 10 | 3 | 43.6427 | 0 | 172.186 | 33.2295 | 0 | 0 | 6.6873 | 19.0363 | 0 | 0 | 0 | 0 | 274.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155019 | 0 | 155019 | 401837 | -637709 | 20 | 21 | 401837 | -1637709
12 | 13 | 11 | 3 | 42.8289 | 0 | 163.102 | 36.131 | 0 | 0 | 6.7104 | 19.0363 | 0 | 0 | 0 | 0 | 267.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158339 | 0 | 158339 | 391195 | -649347 | 20 | 22 | 391195 | -1649347
12 | 13 | 12 | 3 | 41.6696 | 0 | 149.692 | 33.3021 | 0 | 0 | 6.264 | 19.0363 | 0 | 0 | 0 | 0 | 249.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158339 | 0 | 158339 | 376120 | -604206 | 20 | 22 | 376120 | -1604206
12 | 13 | 13 | 3 | 39.8335 | 0 | 150.207 | 32.1444 | 0 | 0 | 6.255 | 19.0363 | 0 | 0 | 0 | 0 | 247.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158337 | 0 | 158337 | 356073 | -600778 | 19 | 21 | 356073 | -1600778
12 | 13 | 14 | 3 | 41.3376 | 0 | 165.698 | 28.7786 | 0 | 0 | 6.2492 | 19.0363 | 0 | 0 | 0 | 0 | 261.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158335 | 0 | 158335 | 388976 | -570929 | 18 | 20 | 388976 | -1570929
12 | 13 | 15 | 3 | 40.9389 | 0 | 172.702 | 27.9979 | 0 | 0 | 6.2562 | 19.0363 | 0 | 0 | 0 | 0 | 266.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156289 | 0 | 156289 | 407370 | -555000 | 17 | 19 | 407370 | -1555000
12 | 13 | 16 | 3 | 43.4345 | 0 | 173.986 | 31.5044 | 0 | 0 | 6.25 | 19.0363 | 0 | 0 | 0 | 0 | 274.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142083 | 0 | 142083 | 410328 | -623867 | 15 | 17 | 410328 | -1623867
12 | 13 | 17 | 3 | 56.8235 | 0 | 169.782 | 34.9474 | 0 | 0 | 6.2468 | 19.0363 | 0 | 0 | 0 | 2.4 | 289.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115980 | 0 | 115980 | 400435 | -670582 | 14 | 16 | 400435 | -1670582
12 | 13 | 18 | 3 | 49.7836 | 0 | 152.497 | 42.354 | 0 | 0 | 6.238 | 19.0363 | 0 | 0 | 0 | 6.4 | 276.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86978.2 | 0 | 86978.2 | 392337 | -771173 | 12 | 14 | 392337 | -1771173
12 | 13 | 19 | 3 | 34.11 | 0 | 93.4203 | 47.2571 | 0 | 0 | 6.2467 | 19.0363 | 0 | 0 | 0 | 7.2 | 207.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53854 | 0 | 53854 | 309859 | -790038 | 11 | 13 | 309859 | -1790038
12 | 13 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 13.8651 | 0 | 5.9456 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38532.5 | 0 | 38532.5 | 180937 | -19460.2 | 10 | 12 | 180937 | -1019460.2
12 | 13 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 13.8653 | 0 | 5.9478 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34200 | 0 | 34200 | 186142 | -69663.5 | 9 | 11 | 186142 | -1069663.5
12 | 13 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 12.5484 | 0 | 5.9219 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20993 | 0 | 20993 | 168383 | -111532 | 9 | 10 | 168383 | -1111532
12 | 13 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 11.5737 | 0 | 5.9082 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11304.2 | 0 | 11304.2 | 154600 | -157701 | 8 | 10 | 154600 | -1157701
12 | 13 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.0779 | 0 | 5.9034 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9840.72 | 0 | 9840.72 | 148229 | -184535 | 8 | 9 | 148229 | -1184535
12 | 14 | 1 | 4 | 10.73 | 0 | 42.3304 | 10.8466 | 0 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9845.42 | 0 | 9845.42 | 145750 | -202295 | 7 | 9 | 145750 | -1202295
12 | 14 | 2 | 4 | 10.73 | 0 | 42.3304 | 11.8632 | 0 | 0 | 5.9106 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.21 | 0 | 9849.21 | 143971 | -218398 | 7 | 8 | 143971 | -1218398
12 | 14 | 3 | 4 | 10.73 | 0 | 42.3304 | 12.5349 | 0 | 0 | 5.9184 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.62 | 0 | 9852.62 | 142455 | -229091 | 7 | 8 | 142455 | -1229091
12 | 14 | 4 | 4 | 10.73 | 0 | 42.3304 | 13.1662 | 0 | 0 | 5.9285 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.73 | 0 | 9855.73 | 141333 | -241463 | 7 | 8 | 141333 | -1241463
12 | 14 | 5 | 4 | 11.8202 | 0 | 44.8242 | 13.7942 | 0 | 0 | 5.9398 | 17.5105 | 0 | 0 | 0 | 4.8 | 98.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10941.7 | 0 | 10941.7 | 142845 | -251115 | 7 | 8 | 142845 | -1251115
12 | 14 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 13.7731 | 0 | 5.9454 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26492 | 0 | 26492 | 189292 | -231216 | 7 | 8 | 189292 | -1231216
12 | 14 | 7 | 4 | 49.0171 | 0 | 140.608 | 63.7474 | 0 | 0 | 6.2064 | 19.3665 | 0 | 0 | 0 | 3.2 | 282.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78398.2 | 0 | 78398.2 | 320090 | -1160720 | 7 | 8 | 320090 | -2160720
12 | 14 | 8 | 4 | 52.382 | 0 | 168.222 | 57.2133 | 0 | 0 | 6.2043 | 19.1836 | 0 | 0 | 0 | 0.8 | 304.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95204.4 | 0 | 95204.4 | 382054 | -1081910 | 7 | 8 | 382054 | -2081910
12 | 14 | 9 | 4 | 41.8884 | 0 | 173.795 | 47.2773 | 0 | 0 | 8.427 | 19.0363 | 0 | 0 | 0 | 0 | 290.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131758 | 0 | 131758 | 401243 | -925673 | 7 | 8 | 401243 | -1925673
12 | 14 | 10 | 4 | 41.163 | 0 | 172.186 | 44.4834 | 0 | 0 | 9.9903 | 19.0363 | 0 | 0 | 0 | 0 | 286.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155030 | 0 | 155030 | 399081 | -870074 | 8 | 9 | 399081 | -1870074
12 | 14 | 11 | 4 | 41.5132 | 0 | 163.102 | 42.9086 | 0 | 0 | 7.4332 | 19.0363 | 0 | 0 | 0 | 0 | 273.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158349 | 0 | 158349 | 380203 | -821411 | 9 | 11 | 380203 | -1821411
12 | 14 | 12 | 4 | 40.9078 | 0 | 149.692 | 39.6785 | 0 | 0 | 6.2326 | 19.0363 | 0 | 0 | 0 | 0 | 255.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158349 | 0 | 158349 | 358965 | -729279 | 10 | 12 | 358965 | -1729279
12 | 14 | 13 | 4 | 39.8681 | 0 | 150.207 | 38.0888 | 0 | 0 | 6.2348 | 19.0363 | 0 | 0 | 0 | 0 | 253.435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158347 | 0 | 158347 | 353574 | -707252 | 11 | 13 | 353574 | -1707252
12 | 14 | 14 | 4 | 41.4675 | 0 | 165.698 | 32.3841 | 0 | 0 | 6.2387 | 19.0363 | 0 | 0 | 0 | 0 | 264.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158344 | 0 | 158344 | 386413 | -646997 | 12 | 14 | 386413 | -1646997
12 | 14 | 15 | 4 | 41.3876 | 0 | 172.702 | 31.9115 | 0 | 0 | 6.2476 | 19.0363 | 0 | 0 | 0 | 0 | 271.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156298 | 0 | 156298 | 405183 | -632321 | 12 | 15 | 405183 | -1632321
12 | 14 | 16 | 4 | 42.3618 | 0 | 173.986 | 34.9266 | 0 | 0 | 6.2412 | 19.0363 | 0 | 0 | 0 | 0 | 276.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142092 | 0 | 142092 | 408227 | -688241 | 11 | 13 | 408227 | -1688241
12 | 14 | 17 | 4 | 55.8062 | 0 | 169.782 | 38.9398 | 0 | 0 | 6.2296 | 19.0363 | 0 | 0 | 0 | 2.4 | 292.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115989 | 0 | 115989 | 398288 | -763632 | 10 | 12 | 398288 | -1763632
12 | 14 | 18 | 4 | 49.7836 | 0 | 152.497 | 47.4213 | 0 | 0 | 6.2227 | 19.0363 | 0 | 0 | 0 | 6.4 | 281.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86986.4 | 0 | 86986.4 | 390921 | -874159 | 8 | 10 | 390921 | -1874159
12 | 14 | 19 | 4 | 34.11 | 0 | 93.4203 | 53.2611 | 0 | 0 | 6.2284 | 19.0363 | 0 | 0 | 0 | 7.2 | 213.256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53861.8 | 0 | 53861.8 | 309499 | -893883 | 7 | 9 | 309499 | -1893883
12 | 14 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 15.8497 | 0 | 6.0078 | 17.5105 | 0 | 0 | 0 | 7.2 | 133.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38539.8 | 0 | 38539.8 | 213982 | -19723.6 | 6 | 7 | 213982 | -1019723.6
12 | 14 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 13.2538 | 0 | 5.9369 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34206.8 | 0 | 34206.8 | 180900 | -95742.5 | 5 | 6 | 180900 | -1095742.5
12 | 14 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 12.0136 | 0 | 5.9153 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21001.4 | 0 | 21001.4 | 164403 | -153360 | 4 | 5 | 164403 | -1153360
12 | 14 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.0605 | 0 | 5.904 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11312.7 | 0 | 11312.7 | 150674 | -197062 | 3 | 4 | 150674 | -1197062
12 | 14 | 24 | 4 | 10.3176 | 0 | 42.5403 | 12.1841 | 0 | 0 | 5.9104 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.0629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.21 | 0 | 9849.21 | 144773 | -225633 | 2 | 3 | 144773 | -1225633
12 | 15 | 1 | 5 | 10.8489 | 0 | 42.3304 | 13.3161 | 0 | 0 | 5.9294 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.88 | 0 | 9853.88 | 142423 | -245725 | 2 | 3 | 142423 | -1245725
12 | 15 | 2 | 5 | 10.8489 | 0 | 42.3304 | 14.205 | 0 | 0 | 5.9488 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.58 | 0 | 9857.58 | 140831 | -257656 | 2 | 3 | 140831 | -1257656
12 | 15 | 3 | 5 | 10.8489 | 0 | 42.3304 | 15.1429 | 0 | 0 | 5.9691 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.98 | 0 | 9860.98 | 139419 | -270503 | 2 | 3 | 139419 | -1270503
12 | 15 | 4 | 5 | 10.8489 | 0 | 42.3304 | 15.6774 | 0 | 0 | 5.9825 | 17.3638 | 0 | 0 | 0 | 4.8 | 97.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9864.05 | 0 | 9864.05 | 138581 | -280489 | 2 | 3 | 138581 | -1280489
12 | 15 | 5 | 5 | 11.8202 | 0 | 44.8242 | 16.2945 | 0 | 0 | 6.0017 | 17.5105 | 0 | 0 | 0 | 4.8 | 101.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10950 | 0 | 10950 | 139859 | -287846 | 3 | 4 | 139859 | -1287846
12 | 15 | 6 | 5 | 24.3093 | 0 | 69.9783 | 15.1985 | 0 | 0 | 5.9698 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26500.1 | 0 | 26500.1 | 186156 | -264936 | 3 | 4 | 186156 | -1264936
12 | 15 | 7 | 5 | 49.0171 | 0 | 140.608 | 67.5174 | 0 | 0 | 6.2108 | 19.49 | 0 | 0 | 0 | 3.2 | 286.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78406.3 | 0 | 78406.3 | 318489 | -1239250 | 5 | 6 | 318489 | -2239250
12 | 15 | 8 | 5 | 52.2825 | 0 | 168.222 | 59.1862 | 0 | 0 | 6.2049 | 19.2343 | 0 | 0 | 0 | 0.8 | 305.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95212.3 | 0 | 95212.3 | 380625 | -1122410 | 6 | 7 | 380625 | -2122410
12 | 15 | 9 | 5 | 41.5674 | 0 | 173.795 | 48.4492 | 0 | 0 | 15.3565 | 19.0483 | 0 | 0 | 0 | 0 | 298.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131764 | 0 | 131764 | 399955 | -942477 | 8 | 9 | 399955 | -1942477
12 | 15 | 10 | 5 | 40.8564 | 0 | 172.186 | 44.7724 | 0 | 0 | 25.2174 | 19.0363 | 0 | 0 | 0 | 0 | 302.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155035 | 0 | 155035 | 397861 | -867465 | 10 | 11 | 397861 | -1867465
12 | 15 | 11 | 5 | 41.2741 | 0 | 163.102 | 43.3268 | 0 | 0 | 7.0457 | 19.0363 | 0 | 0 | 0 | 0 | 273.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 379251 | -811834 | 12 | 14 | 379251 | -1811834
12 | 15 | 12 | 5 | 40.7959 | 0 | 149.692 | 41.6428 | 0 | 0 | 6.2387 | 19.0363 | 0 | 0 | 0 | 0 | 257.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 367607 | -739430 | 14 | 16 | 367607 | -1739430
12 | 15 | 13 | 5 | 39.8919 | 0 | 150.207 | 40.879 | 0 | 0 | 6.2399 | 19.0363 | 0 | 0 | 0 | 0 | 256.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158351 | 0 | 158351 | 352753 | -731924 | 15 | 17 | 352753 | -1731924
12 | 15 | 14 | 5 | 41.6067 | 0 | 165.698 | 34.361 | 0 | 0 | 6.242 | 19.0363 | 0 | 0 | 0 | 0 | 266.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158348 | 0 | 158348 | 385881 | -654084 | 16 | 19 | 385881 | -1654084
12 | 15 | 15 | 5 | 45.3797 | 0 | 172.702 | 32.4334 | 0 | 0 | 6.2463 | 19.0363 | 0 | 0 | 0 | 0 | 275.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156301 | 0 | 156301 | 404615 | -633037 | 17 | 20 | 404615 | -1633037
12 | 15 | 16 | 5 | 51.2089 | 0 | 173.986 | 31.9939 | 0 | 0 | 6.2447 | 19.0363 | 0 | 0 | 0 | 0 | 282.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142095 | 0 | 142095 | 407663 | -633645 | 18 | 20 | 407663 | -1633645
12 | 15 | 17 | 5 | 56.9199 | 0 | 169.782 | 35.5381 | 0 | 0 | 6.249 | 19.0363 | 0 | 0 | 0 | 2.4 | 289.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115991 | 0 | 115991 | 398077 | -665111 | 18 | 20 | 398077 | -1665111
12 | 15 | 18 | 5 | 49.7836 | 0 | 152.497 | 40.0463 | 0 | 0 | 6.2462 | 19.0363 | 0 | 0 | 0 | 6.4 | 274.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86987.9 | 0 | 86987.9 | 386339 | -715892 | 18 | 20 | 386339 | -1715892
12 | 15 | 19 | 5 | 34.11 | 0 | 93.4203 | 44.1021 | 0 | 0 | 6.2559 | 19.0363 | 0 | 0 | 0 | 7.2 | 204.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53863 | 0 | 53863 | 304967 | -728463 | 18 | 20 | 304967 | -1728463
12 | 15 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.0906 | 0 | 5.9475 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38540.7 | 0 | 38540.7 | 179299 | -19594.3 | 18 | 20 | 179299 | -1019594.3
12 | 15 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 14.2454 | 0 | 5.9524 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34208 | 0 | 34208 | 185222 | -43752.6 | 18 | 20 | 185222 | -1043752.6
12 | 15 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.8575 | 0 | 5.9239 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21001 | 0 | 21001 | 166681 | -82302.1 | 17 | 19 | 166681 | -1082302.1
12 | 15 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.8438 | 0 | 5.9092 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11311.4 | 0 | 11311.4 | 152553 | -117095 | 16 | 18 | 152553 | -1117095
12 | 15 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.3063 | 0 | 5.904 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.53 | 0 | 9847.53 | 146310 | -141384 | 15 | 17 | 146310 | -1141384
12 | 16 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.052 | 0 | 5.9021 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.7 | 0 | 9851.7 | 143616 | -167352 | 15 | 16 | 143616 | -1167352
12 | 16 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8834 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.98 | 0 | 9854.98 | 141900 | -183859 | 14 | 15 | 141900 | -1183859
12 | 16 | 3 | 6 | 6.3817 | 0 | 42.7453 | 10.9532 | 0 | 0 | 5.9016 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858.6 | 0 | 9858.6 | 140475 | -199469 | 13 | 14 | 140475 | -1199469
12 | 16 | 4 | 6 | 6.3817 | 0 | 42.7453 | 11.7654 | 0 | 0 | 5.9086 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.48 | 0 | 9861.48 | 139225 | -213072 | 12 | 13 | 139225 | -1213072
12 | 16 | 5 | 6 | 6.3817 | 0 | 42.7453 | 12.6875 | 0 | 0 | 5.9161 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.8944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9864.26 | 0 | 9864.26 | 138018 | -226456 | 11 | 12 | 138018 | -1226456
12 | 16 | 6 | 6 | 6.3817 | 0 | 42.7453 | 13.2703 | 0 | 0 | 5.923 | 17.3638 | 0 | 0 | 0 | 4.8 | 90.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.87 | 0 | 9866.87 | 136852 | -238268 | 10 | 11 | 136852 | -1238268
12 | 16 | 7 | 6 | 6.3817 | 0 | 42.7453 | 13.4164 | 0 | 0 | 5.9255 | 17.3638 | 0 | 0 | 0 | 3.2 | 89.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9869.42 | 0 | 9869.42 | 135919 | -242099 | 12 | 13 | 135919 | -1242099
12 | 16 | 8 | 6 | 6.2782 | 0 | 42.7453 | 72.8126 | 0 | 0 | 6.2099 | 19.8201 | 0 | 0 | 0 | 0.8 | 148.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9871.88 | 0 | 9871.88 | 123547 | -1156120 | 14 | 15 | 123547 | -2156120
12 | 16 | 9 | 6 | 5.3369 | 0 | 42.7453 | 60.4707 | 0 | 0 | 6.8285 | 19.2407 | 0 | 0 | 0 | 0 | 134.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9873.99 | 0 | 9873.99 | 122858 | -963534 | 16 | 17 | 122858 | -1963534
12 | 16 | 10 | 6 | 5.7087 | 0 | 42.7453 | 46.7909 | 0 | 0 | 6.288 | 18.91 | 0 | 0 | 0 | 0 | 120.443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.91 | 0 | 9859.91 | 122363 | -787601 | 18 | 19 | 122363 | -1787601
12 | 16 | 11 | 6 | 5.5973 | 0 | 42.7453 | 39.9179 | 0 | 0 | 6.2356 | 18.8896 | 0 | 0 | 0 | 0 | 113.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.11 | 0 | 9856.11 | 121902 | -688599 | 20 | 22 | 121902 | -1688599
12 | 16 | 12 | 6 | 5.5437 | 0 | 42.7453 | 35.4816 | 0 | 0 | 6.2391 | 18.8896 | 0 | 0 | 0 | 0 | 108.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.89 | 0 | 9853.89 | 121417 | -622306 | 21 | 24 | 121417 | -1622306
12 | 16 | 13 | 6 | 5.4861 | 0 | 42.7453 | 32.4365 | 0 | 0 | 6.2447 | 18.8896 | 0 | 0 | 0 | 0 | 105.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.71 | 0 | 9852.71 | 121072 | -581018 | 22 | 25 | 121072 | -1581018
12 | 16 | 14 | 6 | 5.5019 | 0 | 42.7453 | 30.0514 | 0 | 0 | 6.248 | 18.8896 | 0 | 0 | 0 | 0 | 103.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.95 | 0 | 9851.95 | 120682 | -548089 | 23 | 27 | 120682 | -1548089
12 | 16 | 15 | 6 | 5.5682 | 0 | 42.7453 | 0 | 9.8559 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 76.8947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.38 | 0 | 9851.38 | 121159 | -19396.1 | 24 | 28 | 121159 | -1019396.1
12 | 16 | 16 | 6 | 5.8094 | 0 | 42.7453 | 0 | 10.5906 | 0 | 5.8983 | 15.3158 | 0 | 0 | 0 | 0 | 80.3593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.14 | 0 | 9851.14 | 131472 | -38655 | 22 | 25 | 131472 | -1038655
12 | 16 | 17 | 6 | 8.5838 | 0 | 42.7453 | 0 | 11.3045 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 2.4 | 88.3001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.83 | 0 | 9855.83 | 142097 | -52471.6 | 20 | 23 | 142097 | -1052471.6
12 | 16 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9317 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.1383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.32 | 0 | 9859.32 | 137178 | -85293.1 | 18 | 20 | 137178 | -1085293.1
12 | 16 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 11.0991 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.86 | 0 | 9862.86 | 137877 | -103199 | 17 | 18 | 137877 | -1103199
12 | 16 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8347 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.8402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9865.93 | 0 | 9865.93 | 132515 | -113025 | 16 | 17 | 132515 | -1113025
12 | 16 | 21 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.9541 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9868.69 | 0 | 9868.69 | 133554 | -133880 | 14 | 15 | 133554 | -1133880
12 | 16 | 22 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7833 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9870.83 | 0 | 9870.83 | 130606 | -148308 | 13 | 13 | 130606 | -1148308
12 | 16 | 23 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.8314 | 0 | 5.8989 | 17.3638 | 0 | 0 | 0 | 6.4 | 92.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9872.79 | 0 | 9872.79 | 131049 | -161413 | 11 | 12 | 131049 | -1161413
12 | 16 | 24 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.7229 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.1276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9874.45 | 0 | 9874.45 | 129212 | -170537 | 10 | 10 | 129212 | -1170537
12 | 17 | 1 | 7 | 5.1054 | 0 | 42.7453 | 0 | 10.6656 | 0 | 5.8981 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3761.99 | 0 | 3761.99 | 128457 | -178995 | 11 | 11 | 128457 | -1178995
12 | 17 | 2 | 7 | 5.1054 | 0 | 42.7453 | 10.9136 | 0 | 0 | 5.8992 | 17.3638 | 0 | 0 | 0 | 4.8 | 86.8273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3763.45 | 0 | 3763.45 | 128138 | -183560 | 11 | 12 | 128138 | -1183560
12 | 17 | 3 | 7 | 5.1054 | 0 | 42.7453 | 11.2484 | 0 | 0 | 5.9012 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3765 | 0 | 3765 | 127414 | -188942 | 12 | 13 | 127414 | -1188942
12 | 17 | 4 | 7 | 5.1054 | 0 | 42.7453 | 11.6347 | 0 | 0 | 5.9042 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.39 | 0 | 3766.39 | 126975 | -195427 | 13 | 13 | 126975 | -1195427
12 | 17 | 5 | 7 | 5.1054 | 0 | 42.7453 | 11.5873 | 0 | 0 | 5.9044 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3767.75 | 0 | 3767.75 | 126555 | -200845 | 13 | 14 | 126555 | -1200845
12 | 17 | 6 | 7 | 5.1054 | 0 | 42.7453 | 12.4799 | 0 | 0 | 5.9105 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3769.03 | 0 | 3769.03 | 126129 | -222841 | 13 | 14 | 126129 | -1222841
12 | 17 | 7 | 7 | 5.1054 | 0 | 42.7453 | 13.2146 | 0 | 0 | 5.9203 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3770.27 | 0 | 3770.27 | 125753 | -234323 | 14 | 15 | 125753 | -1234323
12 | 17 | 8 | 7 | 5.0334 | 0 | 42.7453 | 13.5997 | 0 | 0 | 5.9271 | 17.3638 | 0 | 0 | 0 | 0.8 | 85.4693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3772.08 | 0 | 3772.08 | 125386 | -240532 | 14 | 15 | 125386 | -1240532
12 | 17 | 9 | 7 | 4.4688 | 0 | 42.7453 | 12.7502 | 0 | 0 | 5.917 | 17.3638 | 0 | 0 | 0 | 0 | 83.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3774.16 | 0 | 3774.16 | 125132 | -226232 | 15 | 16 | 125132 | -1226232
12 | 17 | 10 | 7 | 4.2324 | 0 | 42.7453 | 11.4742 | 0 | 0 | 5.9028 | 17.3638 | 0 | 0 | 0 | 0 | 81.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3776.23 | 0 | 3776.23 | 125165 | -198739 | 17 | 19 | 125165 | -1198739
12 | 17 | 11 | 7 | 4.179 | 0 | 42.7453 | 10.5878 | 0 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 0 | 80.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3778.18 | 0 | 3778.18 | 126603 | -183221 | 20 | 21 | 126603 | -1183221
12 | 17 | 12 | 7 | 4.152 | 0 | 42.7453 | 0 | 9.917 | 0 | 5.8968 | 17.3638 | 0 | 0 | 0 | 0 | 80.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3780.02 | 0 | 3780.02 | 125382 | -141645 | 22 | 24 | 125382 | -1141645
12 | 17 | 13 | 7 | 4.1527 | 0 | 42.7453 | 0 | 10.1051 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 0 | 80.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3781.68 | 0 | 3781.68 | 125742 | -138097 | 23 | 26 | 125742 | -1138097
12 | 17 | 14 | 7 | 4.1531 | 0 | 42.7453 | 0 | 10.2086 | 0 | 5.8971 | 17.3638 | 0 | 0 | 0 | 0 | 80.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3783.13 | 0 | 3783.13 | 125467 | -126732 | 24 | 27 | 125467 | -1126732
12 | 17 | 15 | 7 | 4.2208 | 0 | 42.7453 | 0 | 10.4235 | 0 | 5.8975 | 17.3638 | 0 | 0 | 0 | 0 | 80.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3783.9 | 0 | 3783.9 | 127327 | -130094 | 25 | 29 | 127327 | -1130094
12 | 17 | 16 | 7 | 5.6581 | 0 | 42.7453 | 0 | 10.3369 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 0 | 82.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3784.93 | 0 | 3784.93 | 125145 | -142086 | 25 | 28 | 125145 | -1142086
12 | 17 | 17 | 7 | 6.6404 | 0 | 42.7453 | 0 | 10.4375 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 2.4 | 85.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3785.79 | 0 | 3785.79 | 125896 | -156933 | 25 | 27 | 125896 | -1156933
12 | 17 | 18 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.3927 | 0 | 5.8972 | 17.3638 | 0 | 0 | 0 | 6.4 | 89.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.76 | 0 | 3786.76 | 124715 | -160332 | 24 | 26 | 124715 | -1160332
12 | 17 | 19 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.4157 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3787.71 | 0 | 3787.71 | 124626 | -167988 | 23 | 25 | 124626 | -1167988
12 | 17 | 20 | 7 | 6.6633 | 0 | 42.7453 | 0 | 10.2453 | 0 | 5.897 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.1147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.57 | 0 | 3788.57 | 124327 | -173379 | 22 | 24 | 124327 | -1173379
12 | 17 | 21 | 7 | 6.6633 | 0 | 42.7453 | 10.9653 | 0 | 0 | 5.9002 | 17.3638 | 0 | 0 | 0 | 7.2 | 90.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3789.39 | 0 | 3789.39 | 124119 | -197494 | 21 | 23 | 124119 | -1197494
12 | 17 | 22 | 7 | 6.6633 | 0 | 42.7453 | 11.6049 | 0 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 7.2 | 91.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3790.18 | 0 | 3790.18 | 123924 | -198162 | 20 | 22 | 123924 | -1198162
12 | 17 | 23 | 7 | 6.6633 | 0 | 42.7453 | 12.6748 | 0 | 0 | 5.9041 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3791.54 | 0 | 3791.54 | 125501 | -219945 | 19 | 21 | 125501 | -1219945
12 | 17 | 24 | 7 | 6.6633 | 0 | 42.7453 | 12.8336 | 0 | 0 | 5.9051 | 17.3638 | 0 | 0 | 0 | 5.6 | 91.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792.86 | 0 | 3792.86 | 123476 | -220516 | 18 | 20 | 123476 | -1220516
12 | 18 | 1 | 1 | 10.8489 | 0 | 42.3304 | 13.6156 | 0 | 0 | 5.9176 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9908.37 | 0 | 9908.37 | 130571 | -231378 | 18 | 19 | 130571 | -1231378
12 | 18 | 2 | 1 | 10.8489 | 0 | 42.3304 | 12.7002 | 0 | 0 | 5.8999 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.9433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9909.69 | 0 | 9909.69 | 123559 | -214646 | 18 | 19 | 123559 | -1214646
12 | 18 | 3 | 1 | 10.8489 | 0 | 42.3304 | 14.0262 | 0 | 0 | 5.9187 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9910.12 | 0 | 9910.12 | 125779 | -248893 | 17 | 18 | 125779 | -1248893
12 | 18 | 4 | 1 | 10.8489 | 0 | 42.3304 | 14.1198 | 0 | 0 | 5.9195 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.3824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9910.54 | 0 | 9910.54 | 123179 | -246406 | 17 | 18 | 123179 | -1246406
12 | 18 | 5 | 1 | 11.8202 | 0 | 44.8242 | 14.8851 | 0 | 0 | 5.9389 | 17.5105 | 0 | 0 | 0 | 4.8 | 99.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10994.7 | 0 | 10994.7 | 129996 | -264037 | 17 | 18 | 129996 | -1264037
12 | 18 | 6 | 1 | 24.3093 | 0 | 69.9783 | 0 | 13.1957 | 0 | 5.9224 | 17.5105 | 0 | 0 | 0 | 4.8 | 135.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26543.2 | 0 | 26543.2 | 173384 | -213542 | 17 | 18 | 173384 | -1213542
12 | 18 | 7 | 1 | 49.0171 | 0 | 140.608 | 62.7064 | 0 | 0 | 6.2043 | 19.6038 | 0 | 0 | 0 | 3.2 | 281.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78448 | 0 | 78448 | 309127 | -1112070 | 18 | 19 | 309127 | -2112070
12 | 18 | 8 | 1 | 52.64 | 0 | 168.222 | 52.2904 | 0 | 0 | 6.2107 | 19.2573 | 0 | 0 | 0 | 0.8 | 299.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95252.5 | 0 | 95252.5 | 371730 | -950076 | 19 | 20 | 371730 | -1950076
12 | 18 | 9 | 1 | 48.6917 | 0 | 173.795 | 43.0875 | 0 | 0 | 6.224 | 19.0695 | 0 | 0 | 0 | 0 | 290.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131795 | 0 | 131795 | 391141 | -804821 | 20 | 21 | 391141 | -1804821
12 | 18 | 10 | 1 | 42.8885 | 0 | 172.186 | 41.0412 | 0 | 0 | 6.2341 | 19.0363 | 0 | 0 | 0 | 0 | 281.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155065 | 0 | 155065 | 389669 | -752970 | 21 | 23 | 389669 | -1752970
12 | 18 | 11 | 1 | 42.7102 | 0 | 163.102 | 41.7839 | 0 | 0 | 6.2386 | 19.0363 | 0 | 0 | 0 | 0 | 272.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158382 | 0 | 158382 | 374339 | -744609 | 23 | 24 | 374339 | -1744609
12 | 18 | 12 | 1 | 42.0039 | 0 | 149.692 | 38.2817 | 0 | 0 | 6.2521 | 19.0363 | 0 | 0 | 0 | 0 | 255.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158380 | 0 | 158380 | 357884 | -667909 | 23 | 26 | 357884 | -1667909
12 | 18 | 13 | 1 | 40.1294 | 0 | 150.207 | 36.3532 | 0 | 0 | 6.2478 | 19.0363 | 0 | 0 | 0 | 0 | 251.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158377 | 0 | 158377 | 346239 | -658640 | 24 | 26 | 346239 | -1658640
12 | 18 | 14 | 1 | 42.8998 | 0 | 165.698 | 30.5093 | 0 | 0 | 6.2493 | 19.0363 | 0 | 0 | 0 | 0 | 264.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158374 | 0 | 158374 | 379679 | -587692 | 25 | 27 | 379679 | -1587692
12 | 18 | 15 | 1 | 42.3714 | 0 | 172.702 | 28.5494 | 0 | 0 | 6.2506 | 19.0363 | 0 | 0 | 0 | 0 | 268.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156327 | 0 | 156327 | 398461 | -570389 | 26 | 27 | 398461 | -1570389
12 | 18 | 16 | 1 | 49.6785 | 0 | 173.986 | 27.6998 | 0 | 0 | 6.2565 | 19.0363 | 0 | 0 | 0 | 0 | 276.657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142119 | 0 | 142119 | 401808 | -546662 | 27 | 28 | 401808 | -1546662
12 | 18 | 17 | 1 | 56.7224 | 0 | 169.782 | 27.9896 | 0 | 0 | 6.2675 | 19.0363 | 0 | 0 | 0 | 2.4 | 282.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116014 | 0 | 116014 | 393025 | -533028 | 28 | 30 | 393025 | -1533028
12 | 18 | 18 | 1 | 49.7836 | 0 | 152.497 | 31.1678 | 0 | 0 | 6.2691 | 19.0363 | 0 | 0 | 0 | 6.4 | 265.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87010.1 | 0 | 87010.1 | 379679 | -558691 | 29 | 31 | 379679 | -1558691
12 | 18 | 19 | 1 | 34.11 | 0 | 93.4203 | 34.8064 | 0 | 0 | 6.274 | 19.0363 | 0 | 0 | 0 | 7.2 | 194.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53883.9 | 0 | 53883.9 | 292975 | -591821 | 29 | 31 | 292975 | -1591821
12 | 18 | 20 | 1 | 24.2281 | 0 | 62.7906 | 0 | 14.2448 | 0 | 5.9467 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38561.3 | 0 | 38561.3 | 175251 | -14366.4 | 30 | 32 | 175251 | -1014366.4
12 | 18 | 21 | 1 | 18.7229 | 0 | 54.6418 | 0 | 12.6378 | 0 | 5.9169 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34228.7 | 0 | 34228.7 | 156361 | -23210 | 30 | 32 | 156361 | -1023210
12 | 18 | 22 | 1 | 13.825 | 0 | 48.8953 | 0 | 13.115 | 0 | 5.9251 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21022.2 | 0 | 21022.2 | 164355 | -42485 | 30 | 31 | 164355 | -1042485
12 | 18 | 23 | 1 | 11.1963 | 0 | 44.3342 | 0 | 12.0088 | 0 | 5.9091 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11331.4 | 0 | 11331.4 | 149227 | -69777 | 30 | 31 | 149227 | -1069777
12 | 18 | 24 | 1 | 10.3176 | 0 | 42.5403 | 0 | 11.481 | 0 | 5.9039 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.07 | 0 | 9867.07 | 142803 | -83559.8 | 29 | 30 | 142803 | -1083559.8
12 | 19 | 1 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.2563 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9870.75 | 0 | 9870.75 | 140468 | -100774 | 30 | 30 | 140468 | -1100774
12 | 19 | 2 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.1357 | 0 | 5.9014 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9873.58 | 0 | 9873.58 | 139270 | -109023 | 30 | 31 | 139270 | -1109023
12 | 19 | 3 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.0756 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9876.03 | 0 | 9876.03 | 138338 | -117997 | 30 | 31 | 138338 | -1117997
12 | 19 | 4 | 2 | 10.424 | 0 | 42.3304 | 0 | 11.0224 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9878.1 | 0 | 9878.1 | 137534 | -123837 | 30 | 31 | 137534 | -1123837
12 | 19 | 5 | 2 | 11.8202 | 0 | 44.8242 | 0 | 11.2034 | 0 | 5.9019 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10963 | 0 | 10963 | 140209 | -126563 | 30 | 32 | 140209 | -1126563
12 | 19 | 6 | 2 | 24.3093 | 0 | 69.9783 | 0 | 14.5781 | 0 | 5.9587 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26512.1 | 0 | 26512.1 | 187757 | -100803 | 30 | 32 | 187757 | -1100803
12 | 19 | 7 | 2 | 49.0171 | 0 | 140.608 | 40.313 | 0 | 0 | 6.2326 | 19.1286 | 0 | 0 | 0 | 3.2 | 258.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78417.2 | 0 | 78417.2 | 319638 | -735749 | 30 | 32 | 319638 | -1735749
12 | 19 | 8 | 2 | 52.8166 | 0 | 168.222 | 35.8498 | 0 | 0 | 6.2422 | 19.0477 | 0 | 0 | 0 | 0.8 | 282.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95222.4 | 0 | 95222.4 | 381534 | -668683 | 30 | 31 | 381534 | -1668683
12 | 19 | 9 | 2 | 49.4902 | 0 | 173.795 | 27.389 | 0 | 0 | 6.2533 | 19.0363 | 0 | 0 | 0 | 0 | 275.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131776 | 0 | 131776 | 400396 | -554760 | 31 | 31 | 400396 | -1554760
12 | 19 | 10 | 2 | 41.8524 | 0 | 172.186 | 26.7847 | 0 | 0 | 6.4963 | 19.0363 | 0 | 0 | 0 | 0 | 266.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155045 | 0 | 155045 | 398345 | -529505 | 30 | 31 | 398345 | -1529505
12 | 19 | 11 | 2 | 42.1945 | 0 | 163.102 | 29.007 | 0 | 0 | 7.0735 | 19.0363 | 0 | 0 | 0 | 0 | 260.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158362 | 0 | 158362 | 389959 | -541199 | 30 | 30 | 389959 | -1541199
12 | 19 | 12 | 2 | 41.3487 | 0 | 149.692 | 26.4814 | 0 | 0 | 6.2733 | 19.0363 | 0 | 0 | 0 | 0 | 242.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158361 | 0 | 158361 | 374379 | -497463 | 30 | 30 | 374379 | -1497463
12 | 19 | 13 | 2 | 39.9678 | 0 | 150.207 | 26.042 | 0 | 0 | 6.2673 | 19.0363 | 0 | 0 | 0 | 0 | 241.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158359 | 0 | 158359 | 353716 | -502349 | 30 | 30 | 353716 | -1502349
12 | 19 | 14 | 2 | 42.3663 | 0 | 165.698 | 0 | 24.5254 | 0 | 6.2697 | 19.0363 | 0 | 0 | 0 | 0 | 257.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158357 | 0 | 158357 | 386873 | -456649 | 29 | 30 | 386873 | -1456649
12 | 19 | 15 | 2 | 41.82 | 0 | 172.702 | 0 | 25.6862 | 0 | 6.2748 | 19.0363 | 0 | 0 | 0 | 0 | 265.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156309 | 0 | 156309 | 405227 | -451768 | 29 | 30 | 405227 | -1451768
12 | 19 | 16 | 2 | 47.3737 | 0 | 173.986 | 0 | 25.8879 | 0 | 6.2767 | 19.0363 | 0 | 0 | 0 | 0 | 272.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142101 | 0 | 142101 | 408234 | -455431 | 28 | 30 | 408234 | -1455431
12 | 19 | 17 | 2 | 56.7149 | 0 | 169.782 | 0 | 25.4239 | 0 | 6.2733 | 19.0363 | 0 | 0 | 0 | 2.4 | 279.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115997 | 0 | 115997 | 400854 | -487636 | 28 | 29 | 400854 | -1487636
12 | 19 | 18 | 2 | 49.7836 | 0 | 152.497 | 29.1916 | 0 | 0 | 6.2701 | 19.0363 | 0 | 0 | 0 | 6.4 | 263.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86992.8 | 0 | 86992.8 | 388005 | -537050 | 27 | 29 | 388005 | -1537050
12 | 19 | 19 | 2 | 34.11 | 0 | 93.4203 | 32.5752 | 0 | 0 | 6.2792 | 19.0363 | 0 | 0 | 0 | 7.2 | 192.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53867.5 | 0 | 53867.5 | 301302 | -565488 | 28 | 29 | 301302 | -1565488
12 | 19 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 14.5754 | 0 | 5.9551 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38545.2 | 0 | 38545.2 | 180345 | -14824 | 28 | 30 | 180345 | -1014824
12 | 19 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 12.9743 | 0 | 5.9223 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34213.2 | 0 | 34213.2 | 161240 | -22810.4 | 28 | 30 | 161240 | -1022810.4
12 | 19 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 13.6219 | 0 | 5.9349 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21006.3 | 0 | 21006.3 | 171705 | -35145.3 | 28 | 30 | 171705 | -1035145.3
12 | 19 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 12.4802 | 0 | 5.9154 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.8366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11315.5 | 0 | 11315.5 | 156002 | -59587.7 | 28 | 30 | 156002 | -1059587.7
12 | 19 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 11.9396 | 0 | 5.9086 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.8166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.32 | 0 | 9851.32 | 149208 | -69412.3 | 28 | 30 | 149208 | -1069412.3
12 | 20 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.6954 | 0 | 5.9061 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.9446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.26 | 0 | 9855.26 | 146323 | -88106.8 | 26 | 28 | 146323 | -1088106.8
12 | 20 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.5002 | 0 | 5.9045 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.7478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858.28 | 0 | 9858.28 | 144511 | -105608 | 24 | 26 | 144511 | -1105608
12 | 20 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.3058 | 0 | 5.9031 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.04 | 0 | 9861.04 | 142991 | -125727 | 22 | 24 | 142991 | -1125727
12 | 20 | 4 | 3 | 10.8489 | 0 | 42.3304 | 0 | 11.141 | 0 | 5.902 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.39 | 0 | 9863.39 | 141805 | -141662 | 22 | 23 | 141805 | -1141662
12 | 20 | 5 | 3 | 11.8202 | 0 | 44.8242 | 0 | 11.2367 | 0 | 5.903 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10948.8 | 0 | 10948.8 | 143956 | -153791 | 21 | 23 | 143956 | -1153791
12 | 20 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.4752 | 0 | 5.9597 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26498.4 | 0 | 26498.4 | 190967 | -135505 | 20 | 22 | 190967 | -1135505
12 | 20 | 7 | 3 | 49.0171 | 0 | 140.608 | 48.9313 | 0 | 0 | 6.2125 | 19.1728 | 0 | 0 | 0 | 3.2 | 267.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78404.1 | 0 | 78404.1 | 321416 | -894293 | 20 | 22 | 321416 | -1894293
12 | 20 | 8 | 3 | 53.0993 | 0 | 168.222 | 45.0339 | 0 | 0 | 6.2219 | 19.0686 | 0 | 0 | 0 | 0.8 | 292.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95209.9 | 0 | 95209.9 | 383172 | -826547 | 20 | 21 | 383172 | -1826547
12 | 20 | 9 | 3 | 46.9259 | 0 | 173.795 | 36.5554 | 0 | 0 | 6.68 | 19.0363 | 0 | 0 | 0 | 0 | 282.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131766 | 0 | 131766 | 402053 | -719255 | 19 | 21 | 402053 | -1719255
12 | 20 | 10 | 3 | 41.9829 | 0 | 172.186 | 36.2601 | 0 | 0 | 7.4383 | 19.0363 | 0 | 0 | 0 | 0 | 276.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155036 | 0 | 155036 | 400079 | -683901 | 20 | 22 | 400079 | -1683901
12 | 20 | 11 | 3 | 41.3842 | 0 | 163.102 | 37.1439 | 0 | 0 | 7.0796 | 19.0363 | 0 | 0 | 0 | 0 | 267.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158355 | 0 | 158355 | 385614 | -670300 | 21 | 23 | 385614 | -1670300
12 | 20 | 12 | 3 | 40.7912 | 0 | 149.692 | 33.4828 | 0 | 0 | 6.2617 | 19.0363 | 0 | 0 | 0 | 0 | 249.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158354 | 0 | 158354 | 371942 | -601508 | 21 | 24 | 371942 | -1601508
12 | 20 | 13 | 3 | 40.0212 | 0 | 150.207 | 34.0928 | 0 | 0 | 6.2535 | 19.0363 | 0 | 0 | 0 | 0 | 249.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158352 | 0 | 158352 | 354821 | -628846 | 21 | 23 | 354821 | -1628846
12 | 20 | 14 | 3 | 43.0108 | 0 | 165.698 | 29.882 | 0 | 0 | 6.2495 | 19.0363 | 0 | 0 | 0 | 0 | 263.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158349 | 0 | 158349 | 387765 | -585080 | 21 | 23 | 387765 | -1585080
12 | 20 | 15 | 3 | 42.0475 | 0 | 172.702 | 29.3553 | 0 | 0 | 6.2516 | 19.0363 | 0 | 0 | 0 | 0 | 269.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156303 | 0 | 156303 | 406227 | -583664 | 20 | 22 | 406227 | -1583664
12 | 20 | 16 | 3 | 50.6161 | 0 | 173.986 | 30.2057 | 0 | 0 | 6.2519 | 19.0363 | 0 | 0 | 0 | 0 | 280.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142096 | 0 | 142096 | 409137 | -596306 | 19 | 21 | 409137 | -1596306
12 | 20 | 17 | 3 | 56.7064 | 0 | 169.782 | 33.3367 | 0 | 0 | 6.2556 | 19.0363 | 0 | 0 | 0 | 2.4 | 287.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115993 | 0 | 115993 | 399567 | -627071 | 19 | 21 | 399567 | -1627071
12 | 20 | 18 | 3 | 49.7836 | 0 | 152.497 | 38.9697 | 0 | 0 | 6.2498 | 19.0363 | 0 | 0 | 0 | 6.4 | 272.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86990 | 0 | 86990 | 390063 | -697648 | 18 | 20 | 390063 | -1697648
12 | 20 | 19 | 3 | 34.11 | 0 | 93.4203 | 42.8861 | 0 | 0 | 6.2605 | 19.0363 | 0 | 0 | 0 | 7.2 | 202.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53865.1 | 0 | 53865.1 | 306661 | -709523 | 18 | 20 | 306661 | -1709523
12 | 20 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.2423 | 0 | 5.9504 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38543.2 | 0 | 38543.2 | 180482 | -19052.6 | 18 | 20 | 180482 | -1019052.6
12 | 20 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 14.457 | 0 | 5.9568 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34210.5 | 0 | 34210.5 | 187064 | -40474.4 | 18 | 20 | 187064 | -1040474.4
12 | 20 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 13.0573 | 0 | 5.9269 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21003.4 | 0 | 21003.4 | 168328 | -75720.8 | 18 | 19 | 168328 | -1075720.8
12 | 20 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.0184 | 0 | 5.911 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11313.7 | 0 | 11313.7 | 154114 | -104949 | 17 | 18 | 154114 | -1104949
12 | 20 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.518 | 0 | 5.9055 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9849.75 | 0 | 9849.75 | 147734 | -129993 | 16 | 17 | 147734 | -1129993
12 | 21 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.3009 | 0 | 5.9036 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9853.92 | 0 | 9853.92 | 145265 | -146882 | 16 | 17 | 145265 | -1146882
12 | 21 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.1676 | 0 | 5.9026 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.17 | 0 | 9857.17 | 143726 | -161855 | 16 | 17 | 143726 | -1161855
12 | 21 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.0409 | 0 | 5.9017 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.01 | 0 | 9860.01 | 142428 | -170806 | 16 | 17 | 142428 | -1170806
12 | 21 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.9257 | 0 | 5.901 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.5 | 0 | 9862.5 | 141254 | -182550 | 15 | 16 | 141254 | -1182550
12 | 21 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.0536 | 0 | 5.902 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10947.9 | 0 | 10947.9 | 143184 | -188583 | 15 | 16 | 143184 | -1188583
12 | 21 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.9045 | 0 | 5.9727 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26497.6 | 0 | 26497.6 | 198477 | -167604 | 14 | 15 | 198477 | -1167604
12 | 21 | 7 | 4 | 49.0171 | 0 | 140.608 | 53.38 | 0 | 0 | 6.2059 | 19.2298 | 0 | 0 | 0 | 3.2 | 271.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78403.3 | 0 | 78403.3 | 320722 | -980412 | 15 | 16 | 320722 | -1980412
12 | 21 | 8 | 4 | 52.8423 | 0 | 168.222 | 47.2361 | 0 | 0 | 6.2144 | 19.0815 | 0 | 0 | 0 | 0.8 | 294.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95209 | 0 | 95209 | 382751 | -878923 | 16 | 17 | 382751 | -1878923
12 | 21 | 9 | 4 | 47.2683 | 0 | 173.795 | 39 | 0 | 0 | 25.2345 | 19.0363 | 0 | 0 | 0 | 0 | 304.334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131764 | 0 | 131764 | 401808 | -744576 | 17 | 18 | 401808 | -1744576
12 | 21 | 10 | 4 | 41.9838 | 0 | 172.186 | 37.231 | 0 | 0 | 25.2432 | 19.0363 | 0 | 0 | 0 | 0 | 295.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155034 | 0 | 155034 | 399747 | -704641 | 18 | 19 | 399747 | -1704641
12 | 21 | 11 | 4 | 42.2074 | 0 | 163.102 | 37.8269 | 0 | 0 | 25.2514 | 19.0363 | 0 | 0 | 0 | 0 | 287.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158353 | 0 | 158353 | 386385 | -689471 | 19 | 21 | 386385 | -1689471
12 | 21 | 12 | 4 | 40.7847 | 0 | 149.692 | 34.0745 | 0 | 0 | 8.2287 | 19.0363 | 0 | 0 | 0 | 0 | 251.816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158352 | 0 | 158352 | 369692 | -599915 | 20 | 22 | 369692 | -1599915
12 | 21 | 13 | 4 | 39.823 | 0 | 150.207 | 31.7722 | 0 | 0 | 6.2591 | 19.0363 | 0 | 0 | 0 | 0 | 247.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158350 | 0 | 158350 | 354558 | -586369 | 20 | 22 | 354558 | -1586369
12 | 21 | 14 | 4 | 43.1027 | 0 | 165.698 | 29.2205 | 0 | 0 | 6.2544 | 19.0363 | 0 | 0 | 0 | 0 | 263.312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158347 | 0 | 158347 | 387504 | -570910 | 20 | 22 | 387504 | -1570910
12 | 21 | 15 | 4 | 43.0172 | 0 | 172.702 | 28.343 | 0 | 0 | 6.2546 | 19.0363 | 0 | 0 | 0 | 0 | 269.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156299 | 0 | 156299 | 406127 | -563456 | 20 | 22 | 406127 | -1563456
12 | 21 | 16 | 4 | 48.347 | 0 | 173.986 | 28.9241 | 0 | 0 | 6.2553 | 19.0363 | 0 | 0 | 0 | 0 | 276.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142092 | 0 | 142092 | 409098 | -571038 | 20 | 22 | 409098 | -1571038
12 | 21 | 17 | 4 | 56.8916 | 0 | 169.782 | 31.8169 | 0 | 0 | 6.2598 | 19.0363 | 0 | 0 | 0 | 2.4 | 286.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115989 | 0 | 115989 | 400640 | -600696 | 20 | 22 | 400640 | -1600696
12 | 21 | 18 | 4 | 49.7836 | 0 | 152.497 | 37.0882 | 0 | 0 | 6.2564 | 19.0363 | 0 | 0 | 0 | 6.4 | 271.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86985.7 | 0 | 86985.7 | 390154 | -659280 | 20 | 22 | 390154 | -1659280
12 | 21 | 19 | 4 | 34.11 | 0 | 93.4203 | 40.7987 | 0 | 0 | 6.3769 | 19.0363 | 0 | 0 | 0 | 7.2 | 200.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53860.8 | 0 | 53860.8 | 306291 | -674132 | 20 | 22 | 306291 | -1674132
12 | 21 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.3895 | 0 | 5.9526 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38538.5 | 0 | 38538.5 | 180608 | -17353.5 | 21 | 22 | 180608 | -1017353.5
12 | 21 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.0032 | 0 | 5.9444 | 15.0234 | 0 | 0 | 0 | 7.2 | 115.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34206.1 | 0 | 34206.1 | 178620 | -30182 | 21 | 22 | 178620 | -1030182
12 | 21 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 13.2108 | 0 | 5.9285 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20998.9 | 0 | 20998.9 | 168404 | -64460.6 | 21 | 22 | 168404 | -1064460.6
12 | 21 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 12.1857 | 0 | 5.9125 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11308.5 | 0 | 11308.5 | 154856 | -87456.6 | 22 | 23 | 154856 | -1087456.6
12 | 21 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.6711 | 0 | 5.9066 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.5461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9844.64 | 0 | 9844.64 | 148475 | -111127 | 22 | 23 | 148475 | -1111127
12 | 22 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.4258 | 0 | 5.9045 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9848.79 | 0 | 9848.79 | 145940 | -120951 | 23 | 23 | 145940 | -1120951
12 | 22 | 2 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.3122 | 0 | 5.9036 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.08 | 0 | 9852.08 | 144732 | -133781 | 23 | 24 | 144732 | -1133781
12 | 22 | 3 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.2125 | 0 | 5.9027 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.95 | 0 | 9854.95 | 143177 | -141182 | 23 | 24 | 143177 | -1141182
12 | 22 | 4 | 5 | 10.8489 | 0 | 42.3304 | 0 | 11.1549 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.51 | 0 | 9857.51 | 142267 | -146700 | 24 | 25 | 142267 | -1146700
12 | 22 | 5 | 5 | 11.8202 | 0 | 44.8242 | 0 | 11.3226 | 0 | 5.9035 | 17.5105 | 0 | 0 | 0 | 4.8 | 96.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10942.9 | 0 | 10942.9 | 144524 | -149314 | 25 | 26 | 144524 | -1149314
12 | 22 | 6 | 5 | 24.3093 | 0 | 69.9783 | 0 | 14.5773 | 0 | 5.962 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26492.4 | 0 | 26492.4 | 191869 | -122920 | 26 | 27 | 191869 | -1122920
12 | 22 | 7 | 5 | 49.0171 | 0 | 140.608 | 43.6981 | 0 | 0 | 6.2278 | 19.1422 | 0 | 0 | 0 | 3.2 | 261.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78397.9 | 0 | 78397.9 | 322338 | -787048 | 28 | 29 | 322338 | -1787048
12 | 22 | 8 | 5 | 52.8539 | 0 | 168.222 | 37.1006 | 0 | 0 | 6.2433 | 19.0487 | 0 | 0 | 0 | 0.8 | 284.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95203.6 | 0 | 95203.6 | 384405 | -680013 | 30 | 30 | 384405 | -1680013
12 | 22 | 9 | 5 | 46.816 | 0 | 173.795 | 26.7011 | 0 | 0 | 8.7668 | 19.0363 | 0 | 0 | 0 | 0 | 275.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131759 | 0 | 131759 | 403129 | -542067 | 31 | 32 | 403129 | -1542067
12 | 22 | 10 | 5 | 42.3702 | 0 | 172.186 | 25.9082 | 0 | 0 | 13.3819 | 19.0363 | 0 | 0 | 0 | 0 | 272.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155029 | 0 | 155029 | 401053 | -511772 | 32 | 32 | 401053 | -1511772
12 | 22 | 11 | 5 | 42.4976 | 0 | 163.102 | 26.523 | 0 | 0 | 20.9199 | 19.0363 | 0 | 0 | 0 | 0 | 272.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158347 | 0 | 158347 | 391506 | -496959 | 32 | 33 | 391506 | -1496959
12 | 22 | 12 | 5 | 41.513 | 0 | 149.692 | 0 | 25.1413 | 0 | 6.2828 | 19.0363 | 0 | 0 | 0 | 0 | 241.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158345 | 0 | 158345 | 378315 | -453163 | 33 | 33 | 378315 | -1453163
12 | 22 | 13 | 5 | 39.9556 | 0 | 150.207 | 0 | 23.0579 | 0 | 6.2785 | 19.0363 | 0 | 0 | 0 | 0 | 238.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158344 | 0 | 158344 | 356178 | -429876 | 33 | 34 | 356178 | -1429876
12 | 22 | 14 | 5 | 42.261 | 0 | 165.698 | 0 | 24.7356 | 0 | 6.287 | 19.0363 | 0 | 0 | 0 | 0 | 258.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158342 | 0 | 158342 | 389689 | -377999 | 34 | 34 | 389689 | -1377999
12 | 22 | 15 | 5 | 41.8524 | 0 | 172.702 | 0 | 25.8785 | 0 | 6.2992 | 19.0363 | 0 | 0 | 0 | 0 | 265.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156295 | 0 | 156295 | 407596 | -357681 | 34 | 35 | 407596 | -1357681
12 | 22 | 16 | 5 | 46.1635 | 0 | 173.986 | 0 | 26.0756 | 0 | 6.2997 | 19.0363 | 0 | 0 | 0 | 0 | 271.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142087 | 0 | 142087 | 410594 | -369610 | 34 | 34 | 410594 | -1369610
12 | 22 | 17 | 5 | 56.2904 | 0 | 169.782 | 0 | 25.6152 | 0 | 6.2982 | 19.0363 | 0 | 0 | 0 | 2.4 | 279.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115982 | 0 | 115982 | 403125 | -380417 | 33 | 34 | 403125 | -1380417
12 | 22 | 18 | 5 | 49.7836 | 0 | 152.497 | 0 | 25.1684 | 0 | 6.2821 | 19.0363 | 0 | 0 | 0 | 6.4 | 259.168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86977.6 | 0 | 86977.6 | 388904 | -439988 | 33 | 33 | 388904 | -1439988
12 | 22 | 19 | 5 | 34.11 | 0 | 93.4203 | 26.5365 | 0 | 0 | 6.2904 | 19.0363 | 0 | 0 | 0 | 7.2 | 186.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53851.9 | 0 | 53851.9 | 298895 | -475876 | 32 | 33 | 298895 | -1475876
12 | 22 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 13.9922 | 0 | 5.9482 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38529.9 | 0 | 38529.9 | 182357 | -12139.2 | 32 | 33 | 182357 | -1012139.2
12 | 22 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 12.5214 | 0 | 5.919 | 12.9754 | 0 | 0 | 0 | 7.2 | 111.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34197.7 | 0 | 34197.7 | 163147 | -17697.3 | 32 | 33 | 163147 | -1017697.3
12 | 22 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.1944 | 0 | 5.9106 | 12.9754 | 0 | 0 | 0 | 7.2 | 101.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20990.3 | 0 | 20990.3 | 149623 | -22081.3 | 30 | 31 | 149623 | -1022081.3
12 | 22 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 12.9545 | 0 | 5.9219 | 17.5105 | 0 | 0 | 0 | 6.4 | 98.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11299 | 0 | 11299 | 161385 | -38847.5 | 28 | 30 | 161385 | -1038847.5
12 | 22 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 12.3058 | 0 | 5.9127 | 17.5105 | 0 | 0 | 0 | 5.6 | 94.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9834.38 | 0 | 9834.38 | 153103 | -62369.4 | 27 | 28 | 153103 | -1062369.4
12 | 23 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.9316 | 0 | 5.9086 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9838.47 | 0 | 9838.47 | 149473 | -79137.8 | 26 | 27 | 149473 | -1079137.8
12 | 23 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.6696 | 0 | 5.9062 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9841.89 | 0 | 9841.89 | 147060 | -98208.3 | 25 | 26 | 147060 | -1098208.3
12 | 23 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4756 | 0 | 5.9046 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9845.58 | 0 | 9845.58 | 145304 | -113573 | 24 | 25 | 145304 | -1113573
12 | 23 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2983 | 0 | 5.9032 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9848.66 | 0 | 9848.66 | 143713 | -130127 | 22 | 24 | 143713 | -1130127
12 | 23 | 5 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.1497 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.3426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9851.5 | 0 | 9851.5 | 142366 | -147758 | 21 | 22 | 142366 | -1147758
12 | 23 | 6 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.9946 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.1867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9854.19 | 0 | 9854.19 | 141169 | -161407 | 19 | 21 | 141169 | -1161407
12 | 23 | 7 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.8559 | 0 | 5.9005 | 17.3638 | 0 | 0 | 0 | 3.2 | 86.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.77 | 0 | 9856.77 | 140075 | -175253 | 19 | 20 | 140075 | -1175253
12 | 23 | 8 | 6 | 6.3113 | 0 | 42.7453 | 63.3206 | 0 | 0 | 6.2241 | 19.5007 | 0 | 0 | 0 | 0.8 | 138.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.27 | 0 | 9859.27 | 125758 | -1010420 | 18 | 20 | 125758 | -2010420
12 | 23 | 9 | 6 | 5.5433 | 0 | 42.7453 | 55.0824 | 0 | 0 | 7.0203 | 19.1823 | 0 | 0 | 0 | 0 | 129.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.5 | 0 | 9861.5 | 126429 | -907071 | 17 | 19 | 126429 | -1907071
12 | 23 | 10 | 6 | 5.5681 | 0 | 42.7453 | 43.02 | 0 | 0 | 6.5622 | 18.8896 | 0 | 0 | 0 | 0 | 116.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.43 | 0 | 9852.43 | 124362 | -747489 | 18 | 19 | 124362 | -1747489
12 | 23 | 11 | 6 | 5.4772 | 0 | 42.7453 | 40.3055 | 0 | 0 | 6.228 | 18.8896 | 0 | 0 | 0 | 0 | 113.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9848.6 | 0 | 9848.6 | 123751 | -710095 | 18 | 20 | 123751 | -1710095
12 | 23 | 12 | 6 | 5.4765 | 0 | 42.7453 | 38.0981 | 0 | 0 | 6.228 | 18.8896 | 0 | 0 | 0 | 0 | 111.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9847.2 | 0 | 9847.2 | 123141 | -678237 | 18 | 20 | 123141 | -1678237
12 | 23 | 13 | 6 | 5.4793 | 0 | 42.7453 | 36.528 | 0 | 0 | 6.2273 | 18.8896 | 0 | 0 | 0 | 0 | 109.869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9846.35 | 0 | 9846.35 | 122608 | -654955 | 18 | 20 | 122608 | -1654955
12 | 23 | 14 | 6 | 5.4788 | 0 | 42.7453 | 33.5045 | 0 | 0 | 6.2317 | 18.8896 | 0 | 0 | 0 | 0 | 106.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9846.01 | 0 | 9846.01 | 122092 | -612338 | 18 | 20 | 122092 | -1612338
12 | 23 | 15 | 6 | 5.4935 | 0 | 42.7453 | 0 | 9.7431 | 0 | 5.8967 | 12.8287 | 0 | 0 | 0 | 0 | 76.7073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9845.78 | 0 | 9845.78 | 122562 | -19394.8 | 17 | 20 | 122562 | -1019394.8
12 | 23 | 16 | 6 | 5.7239 | 0 | 42.7453 | 0 | 11.3235 | 0 | 5.9038 | 17.3638 | 0 | 0 | 0 | 0 | 83.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9845.92 | 0 | 9845.92 | 145745 | -48629.9 | 16 | 18 | 145745 | -1048629.9
12 | 23 | 17 | 6 | 8.4455 | 0 | 42.7453 | 0 | 10.8668 | 0 | 5.9006 | 17.3638 | 0 | 0 | 0 | 2.4 | 87.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9850.55 | 0 | 9850.55 | 140501 | -74819.3 | 14 | 15 | 140501 | -1074819.3
12 | 23 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.47 | 0 | 5.8987 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.13 | 0 | 9855.13 | 136565 | -116799 | 11 | 13 | 136565 | -1116799
12 | 23 | 19 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.1911 | 0 | 5.8977 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.1952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9858.93 | 0 | 9858.93 | 133992 | -156100 | 11 | 12 | 133992 | -1156100
12 | 23 | 20 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.038 | 0 | 5.8973 | 17.3638 | 0 | 0 | 0 | 7.2 | 92.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.64 | 0 | 9862.64 | 132648 | -184987 | 10 | 12 | 132648 | -1184987
12 | 23 | 21 | 6 | 8.7973 | 0 | 42.7453 | 11.1721 | 0 | 0 | 5.9043 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.14 | 0 | 9866.14 | 131838 | -208284 | 10 | 11 | 131838 | -1208284
12 | 23 | 22 | 6 | 8.7973 | 0 | 42.7453 | 12.0116 | 0 | 0 | 5.9141 | 17.3638 | 0 | 0 | 0 | 7.2 | 94.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9869.25 | 0 | 9869.25 | 130760 | -221247 | 9 | 10 | 130760 | -1221247
12 | 23 | 23 | 6 | 8.7973 | 0 | 42.7453 | 13.0104 | 0 | 0 | 5.9271 | 17.3638 | 0 | 0 | 0 | 6.4 | 94.2439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9872.13 | 0 | 9872.13 | 129838 | -238026 | 7 | 8 | 129838 | -1238026
12 | 23 | 24 | 6 | 8.7973 | 0 | 42.7453 | 13.814 | 0 | 0 | 5.9391 | 17.3638 | 0 | 0 | 0 | 5.6 | 94.2594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9874.87 | 0 | 9874.87 | 128995 | -251342 | 6 | 7 | 128995 | -1251342
12 | 24 | 1 | 7 | 5.1054 | 0 | 42.7453 | 15.3017 | 0 | 0 | 5.9754 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3763.52 | 0 | 3763.52 | 127927 | -281243 | 4 | 5 | 127927 | -1281243
12 | 24 | 2 | 7 | 5.1054 | 0 | 42.7453 | 16.3448 | 0 | 0 | 6.0081 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.16 | 0 | 3766.16 | 127069 | -295210 | 3 | 4 | 127069 | -1295210
12 | 24 | 3 | 7 | 5.1054 | 0 | 42.7453 | 17.9965 | 0 | 0 | 6.0679 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3768.97 | 0 | 3768.97 | 126357 | -320372 | 1 | 2 | 126357 | -1320372
12 | 24 | 4 | 7 | 5.1054 | 0 | 42.7453 | 18.9948 | 0 | 0 | 6.1041 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3771.62 | 0 | 3771.62 | 125700 | -334037 | 1 | 2 | 125700 | -1334037
12 | 24 | 5 | 7 | 5.1054 | 0 | 42.7453 | 19.8801 | 0 | 0 | 6.1467 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3774.27 | 0 | 3774.27 | 126083 | -352467 | 0 | 1 | 126083 | -1352467
12 | 24 | 6 | 7 | 5.1054 | 0 | 42.7453 | 20.3325 | 0 | 0 | 6.1699 | 17.3638 | 0 | 0 | 0 | 4.8 | 96.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3776.86 | 0 | 3776.86 | 124536 | -359079 | 0 | 1 | 124536 | -1359079
12 | 24 | 7 | 7 | 5.1054 | 0 | 42.7453 | 21.3763 | 0 | 0 | 6.2233 | 17.3638 | 0 | 0 | 0 | 3.2 | 96.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.43 | 0 | 3779.43 | 125221 | -373148 | 0 | 1 | 125221 | -1373148
12 | 24 | 8 | 7 | 5.0182 | 0 | 42.7453 | 21.2675 | 0 | 0 | 6.2138 | 17.3638 | 0 | 0 | 0 | 0.8 | 93.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3781.3 | 0 | 3781.3 | 123621 | -372692 | -1 | 0 | 123621 | -1372692
12 | 24 | 9 | 7 | 4.3484 | 0 | 42.7453 | 20.61 | 0 | 0 | 6.1738 | 17.3638 | 0 | 0 | 0 | 0 | 91.2412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3782.96 | 0 | 3782.96 | 123319 | -360226 | -1 | 0 | 123319 | -1360226
12 | 24 | 10 | 7 | 4.1512 | 0 | 42.7453 | 19.2127 | 0 | 0 | 6.1005 | 17.3638 | 0 | 0 | 0 | 0 | 89.5735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3784.48 | 0 | 3784.48 | 123284 | -336132 | 0 | 1 | 123284 | -1336132
12 | 24 | 11 | 7 | 4.1504 | 0 | 42.7453 | 17.0194 | 0 | 0 | 6.0014 | 17.3638 | 0 | 0 | 0 | 0 | 87.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3785.89 | 0 | 3785.89 | 123045 | -294831 | 1 | 3 | 123045 | -1294831
12 | 24 | 12 | 7 | 4.2062 | 0 | 42.7453 | 18.3199 | 0 | 0 | 6.0569 | 17.3638 | 0 | 0 | 0 | 0 | 88.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3787.21 | 0 | 3787.21 | 125878 | -326660 | 2 | 4 | 125878 | -1326660
12 | 24 | 13 | 7 | 4.8099 | 0 | 42.7453 | 18.8482 | 0 | 0 | 6.081 | 17.3638 | 0 | 0 | 0 | 0 | 89.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.44 | 0 | 3788.44 | 122558 | -332543 | 2 | 4 | 122558 | -1332543
12 | 24 | 14 | 7 | 4.7622 | 0 | 42.7453 | 19.2952 | 0 | 0 | 6.1034 | 17.3638 | 0 | 0 | 0 | 0 | 90.2699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3789.62 | 0 | 3789.62 | 123427 | -341385 | 2 | 4 | 123427 | -1341385
12 | 24 | 15 | 7 | 5.0745 | 0 | 42.7453 | 19.9442 | 0 | 0 | 6.1365 | 17.3638 | 0 | 0 | 0 | 0 | 91.2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3790.87 | 0 | 3790.87 | 121910 | -352153 | 2 | 4 | 121910 | -1352153
12 | 24 | 16 | 7 | 4.597 | 0 | 42.7453 | 20.3352 | 0 | 0 | 6.1563 | 17.3638 | 0 | 0 | 0 | 0 | 91.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792.06 | 0 | 3792.06 | 121804 | -356519 | 0 | 1 | 121804 | -1356519
12 | 24 | 17 | 7 | 6.3676 | 0 | 42.7453 | 21.5851 | 0 | 0 | 6.2274 | 17.3638 | 0 | 0 | 0 | 2.4 | 96.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3793.25 | 0 | 3793.25 | 121071 | -376123 | -3 | -2 | 121071 | -1376123
12 | 24 | 18 | 7 | 6.6633 | 0 | 42.7453 | 23.7517 | 0 | 0 | 6.2675 | 17.3638 | 0 | 0 | 0 | 6.4 | 103.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3794.44 | 0 | 3794.44 | 120532 | -411508 | -6 | -5 | 120532 | -1411508
12 | 24 | 19 | 7 | 6.6633 | 0 | 42.7453 | 25.2279 | 0 | 0 | 6.2657 | 17.3638 | 0 | 0 | 0 | 7.2 | 105.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3795.6 | 0 | 3795.6 | 119952 | -430763 | -8 | -8 | 119952 | -1430763
12 | 24 | 20 | 7 | 6.6633 | 0 | 42.7453 | 26.7162 | 0 | 0 | 6.2645 | 17.3638 | 0 | 0 | 0 | 7.2 | 106.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3796.78 | 0 | 3796.78 | 119401 | -452622 | -11 | -10 | 119401 | -1452622
12 | 24 | 21 | 7 | 6.6633 | 0 | 42.7453 | 28.0901 | 0 | 0 | 6.2637 | 17.3638 | 0 | 0 | 0 | 7.2 | 108.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.94 | 0 | 3797.94 | 118866 | -470489 | -13 | -13 | 118866 | -1470489
12 | 24 | 22 | 7 | 6.6633 | 0 | 42.7453 | 29.0011 | 0 | 0 | 6.2632 | 17.3638 | 0 | 0 | 0 | 7.2 | 109.237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3799.08 | 0 | 3799.08 | 118415 | -483861 | -13 | -13 | 118415 | -1483861
12 | 24 | 23 | 7 | 6.6633 | 0 | 42.7453 | 29.5193 | 0 | 0 | 6.2631 | 17.3638 | 0 | 0 | 0 | 6.4 | 108.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3800.17 | 0 | 3800.17 | 118070 | -491212 | -13 | -12 | 118070 | -1491212
12 | 24 | 24 | 7 | 6.6633 | 0 | 42.7453 | 30.0045 | 0 | 0 | 6.2628 | 17.3638 | 0 | 0 | 0 | 5.6 | 108.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3801.21 | 0 | 3801.21 | 117724 | -497756 | -13 | -12 | 117724 | -1497756
12 | 25 | 1 | 8 | 5.1054 | 0 | 42.7453 | 31.2316 | 0 | 0 | 6.2613 | 17.3638 | 0 | 0 | 0 | 4.8 | 107.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3802.21 | 0 | 3802.21 | 117593 | -516819 | -13 | -13 | 117593 | -1516819
12 | 25 | 2 | 8 | 5.1054 | 0 | 42.7453 | 31.7333 | 0 | 0 | 6.2607 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.19 | 0 | 3803.19 | 116905 | -521881 | -14 | -13 | 116905 | -1521881
12 | 25 | 3 | 8 | 5.1054 | 0 | 42.7453 | 32.2866 | 0 | 0 | 6.2606 | 17.3638 | 0 | 0 | 0 | 4.8 | 108.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3804.12 | 0 | 3804.12 | 116928 | -530063 | -15 | -14 | 116928 | -1530063
12 | 25 | 4 | 8 | 5.1054 | 0 | 42.7453 | 32.8037 | 0 | 0 | 6.2603 | 17.3638 | 0 | 0 | 0 | 4.8 | 109.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805.04 | 0 | 3805.04 | 116499 | -536328 | -15 | -15 | 116499 | -1536328
12 | 25 | 5 | 8 | 5.1054 | 0 | 42.7453 | 33.0407 | 0 | 0 | 6.2601 | 17.3638 | 0 | 0 | 0 | 4.8 | 109.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805.92 | 0 | 3805.92 | 115907 | -539290 | -16 | -16 | 115907 | -1539290
12 | 25 | 6 | 8 | 5.1054 | 0 | 42.7453 | 33.7746 | 0 | 0 | 6.2598 | 17.3638 | 0 | 0 | 0 | 4.8 | 110.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3806.79 | 0 | 3806.79 | 115986 | -549687 | -17 | -17 | 115986 | -1549687
12 | 25 | 7 | 8 | 5.1054 | 0 | 42.7453 | 33.7211 | 0 | 0 | 6.2602 | 17.3638 | 0 | 0 | 0 | 3.2 | 108.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3807.64 | 0 | 3807.64 | 115323 | -548090 | -16 | -16 | 115323 | -1548090
12 | 25 | 8 | 8 | 5.1052 | 0 | 42.7453 | 33.7398 | 0 | 0 | 6.261 | 17.3638 | 0 | 0 | 0 | 0.8 | 106.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3808.45 | 0 | 3808.45 | 118862 | -548918 | -15 | -15 | 118862 | -1548918
12 | 25 | 9 | 8 | 5.2866 | 0 | 42.7453 | 32.2867 | 0 | 0 | 6.2628 | 17.3638 | 0 | 0 | 0 | 0 | 103.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3809.23 | 0 | 3809.23 | 115093 | -523487 | -15 | -14 | 115093 | -1523487
12 | 25 | 10 | 8 | 5.1695 | 0 | 42.7453 | 30.652 | 0 | 0 | 6.2662 | 17.3638 | 0 | 0 | 0 | 0 | 102.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3809.98 | 0 | 3809.98 | 123166 | -500258 | -13 | -12 | 123166 | -1500258
12 | 25 | 11 | 8 | 4.852 | 0 | 42.7453 | 27.5082 | 0 | 0 | 6.2693 | 17.3638 | 0 | 0 | 0 | 0 | 98.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3810.67 | 0 | 3810.67 | 115244 | -448200 | -11 | -10 | 115244 | -1448200
12 | 25 | 12 | 8 | 4.7332 | 0 | 42.7453 | 26.4545 | 0 | 0 | 6.2717 | 17.3638 | 0 | 0 | 0 | 0 | 97.5684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3811.27 | 0 | 3811.27 | 120208 | -439481 | -9 | -8 | 120208 | -1439481
12 | 25 | 13 | 8 | 4.8412 | 0 | 42.7453 | 24.7833 | 0 | 0 | 6.2714 | 17.3638 | 0 | 0 | 0 | 0 | 96.0049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3811.77 | 0 | 3811.77 | 115581 | -413131 | -6 | -6 | 115581 | -1413131
12 | 25 | 14 | 8 | 4.7921 | 0 | 42.7453 | 23.7622 | 0 | 0 | 6.2726 | 17.3638 | 0 | 0 | 0 | 0 | 94.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3812.24 | 0 | 3812.24 | 119110 | -402515 | -4 | -3 | 119110 | -1402515
12 | 25 | 15 | 8 | 4.9951 | 0 | 42.7453 | 22.7752 | 0 | 0 | 6.2714 | 17.3638 | 0 | 0 | 0 | 0 | 94.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3812.7 | 0 | 3812.7 | 115840 | -387026 | -2 | -1 | 115840 | -1387026
12 | 25 | 16 | 8 | 5.7548 | 0 | 42.7453 | 22.9896 | 0 | 0 | 6.2694 | 17.3638 | 0 | 0 | 0 | 0 | 95.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3813.16 | 0 | 3813.16 | 118589 | -394753 | -1 | 0 | 118589 | -1394753
12 | 25 | 17 | 8 | 6.572 | 0 | 42.7453 | 22.8616 | 0 | 0 | 6.2675 | 17.3638 | 0 | 0 | 0 | 2.4 | 98.2101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3813.62 | 0 | 3813.62 | 115806 | -391753 | 0 | 1 | 115806 | -1391753
12 | 25 | 18 | 8 | 6.6633 | 0 | 42.7453 | 24.2658 | 0 | 0 | 6.2653 | 17.3638 | 0 | 0 | 0 | 6.4 | 103.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3814.08 | 0 | 3814.08 | 115752 | -420554 | 0 | 2 | 115752 | -1420554
12 | 25 | 19 | 8 | 6.6633 | 0 | 42.7453 | 23.8941 | 0 | 0 | 6.2643 | 17.3638 | 0 | 0 | 0 | 7.2 | 104.131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3814.55 | 0 | 3814.55 | 115769 | -410014 | 1 | 3 | 115769 | -1410014
12 | 25 | 20 | 8 | 6.6633 | 0 | 42.7453 | 25.1311 | 0 | 0 | 6.264 | 17.3638 | 0 | 0 | 0 | 7.2 | 105.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3815.14 | 0 | 3815.14 | 118540 | -436036 | 2 | 3 | 118540 | -1436036
12 | 25 | 21 | 8 | 6.6633 | 0 | 42.7453 | 24.6784 | 0 | 0 | 6.2634 | 17.3638 | 0 | 0 | 0 | 7.2 | 104.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3815.74 | 0 | 3815.74 | 115756 | -426260 | 3 | 4 | 115756 | -1426260
12 | 25 | 22 | 8 | 6.6633 | 0 | 42.7453 | 24.9758 | 0 | 0 | 6.2633 | 17.3638 | 0 | 0 | 0 | 7.2 | 105.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3816.28 | 0 | 3816.28 | 118482 | -434799 | 4 | 5 | 118482 | -1434799
12 | 25 | 23 | 8 | 6.6633 | 0 | 42.7453 | 24.1916 | 0 | 0 | 6.2632 | 17.3638 | 0 | 0 | 0 | 6.4 | 103.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3816.82 | 0 | 3816.82 | 115906 | -421019 | 5 | 7 | 115906 | -1421019
12 | 25 | 24 | 8 | 6.6633 | 0 | 42.7453 | 24.1647 | 0 | 0 | 6.2632 | 17.3638 | 0 | 0 | 0 | 5.6 | 102.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3817.3 | 0 | 3817.3 | 118682 | -424207 | 7 | 8 | 118682 | -1424207
12 | 26 | 1 | 2 | 10.424 | 0 | 42.3304 | 23.4785 | 0 | 0 | 6.2626 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9931.79 | 0 | 9931.79 | 116451 | -414203 | 7 | 9 | 116451 | -1414203
12 | 26 | 2 | 2 | 10.424 | 0 | 42.3304 | 23.5495 | 0 | 0 | 6.2624 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.23 | 0 | 9932.23 | 118823 | -417104 | 8 | 9 | 118823 | -1417104
12 | 26 | 3 | 2 | 10.424 | 0 | 42.3304 | 22.8726 | 0 | 0 | 6.2624 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.14 | 0 | 9932.14 | 116749 | -405273 | 8 | 10 | 116749 | -1405273
12 | 26 | 4 | 2 | 10.424 | 0 | 42.3304 | 22.7356 | 0 | 0 | 6.2625 | 17.3638 | 0 | 0 | 0 | 4.8 | 103.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9932.35 | 0 | 9932.35 | 118963 | -405762 | 10 | 11 | 118963 | -1405762
12 | 26 | 5 | 2 | 11.8202 | 0 | 44.8242 | 22.4411 | 0 | 0 | 6.2639 | 17.5105 | 0 | 0 | 0 | 4.8 | 107.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11015.7 | 0 | 11015.7 | 120082 | -396279 | 11 | 12 | 120082 | -1396279
12 | 26 | 6 | 2 | 24.3093 | 0 | 69.9783 | 19.7409 | 0 | 0 | 6.1263 | 17.5105 | 0 | 0 | 0 | 4.8 | 142.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26563.4 | 0 | 26563.4 | 167158 | -348017 | 12 | 13 | 167158 | -1348017
12 | 26 | 7 | 2 | 49.0171 | 0 | 140.608 | 74.7491 | 0 | 0 | 25.2157 | 20.259 | 0 | 0 | 0 | 3.2 | 313.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78467.3 | 0 | 78467.3 | 304946 | -1331510 | 13 | 14 | 304946 | -2331510
12 | 26 | 8 | 2 | 53.0149 | 0 | 168.222 | 63.44 | 0 | 0 | 25.2074 | 19.5672 | 0 | 0 | 0 | 0.8 | 330.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95272.5 | 0 | 95272.5 | 367755 | -1150070 | 14 | 15 | 367755 | -2150070
12 | 26 | 9 | 2 | 47.6655 | 0 | 173.795 | 51.8527 | 0 | 0 | 11.7924 | 19.2363 | 0 | 0 | 0 | 0 | 304.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131810 | 0 | 131810 | 387481 | -969894 | 15 | 16 | 387481 | -1969894
12 | 26 | 10 | 2 | 42.3428 | 0 | 172.186 | 49.6618 | 0 | 0 | 10.0289 | 19.0975 | 0 | 0 | 0 | 0 | 293.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155080 | 0 | 155080 | 385986 | -920754 | 16 | 17 | 385986 | -1920754
12 | 26 | 11 | 2 | 42.5582 | 0 | 163.102 | 49.5396 | 0 | 0 | 8.1648 | 19.0363 | 0 | 0 | 0 | 0 | 282.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158397 | 0 | 158397 | 368262 | -888923 | 18 | 19 | 368262 | -1888923
12 | 26 | 12 | 2 | 41.543 | 0 | 149.692 | 46.7968 | 0 | 0 | 6.9244 | 19.0363 | 0 | 0 | 0 | 0 | 263.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158395 | 0 | 158395 | 347556 | -812476 | 19 | 20 | 347556 | -1812476
12 | 26 | 13 | 2 | 39.9556 | 0 | 150.207 | 44.5685 | 0 | 0 | 6.4746 | 19.0363 | 0 | 0 | 0 | 0 | 260.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158392 | 0 | 158392 | 342869 | -779545 | 20 | 21 | 342869 | -1779545
12 | 26 | 14 | 2 | 42.6415 | 0 | 165.698 | 38.3293 | 0 | 0 | 6.2691 | 19.0363 | 0 | 0 | 0 | 0 | 271.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158389 | 0 | 158389 | 376431 | -712381 | 21 | 22 | 376431 | -1712381
12 | 26 | 15 | 2 | 41.9317 | 0 | 172.702 | 34.8877 | 0 | 0 | 6.2374 | 19.0363 | 0 | 0 | 0 | 0 | 274.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156341 | 0 | 156341 | 395383 | -679368 | 21 | 23 | 395383 | -1679368
12 | 26 | 16 | 2 | 47.8195 | 0 | 173.986 | 34.1689 | 0 | 0 | 6.3007 | 19.0363 | 0 | 0 | 0 | 0 | 281.311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142133 | 0 | 142133 | 398840 | -670778 | 22 | 23 | 398840 | -1670778
12 | 26 | 17 | 2 | 56.2062 | 0 | 169.782 | 37.156 | 0 | 0 | 6.3446 | 19.0363 | 0 | 0 | 0 | 2.4 | 290.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116028 | 0 | 116028 | 389883 | -681649 | 22 | 23 | 389883 | -1681649
12 | 26 | 18 | 2 | 49.7836 | 0 | 152.497 | 41.2943 | 0 | 0 | 6.2928 | 19.0363 | 0 | 0 | 0 | 6.4 | 275.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87024.1 | 0 | 87024.1 | 374674 | -728941 | 21 | 23 | 374674 | -1728941
12 | 26 | 19 | 2 | 34.11 | 0 | 93.4203 | 45.841 | 0 | 0 | 6.3755 | 19.0363 | 0 | 0 | 0 | 7.2 | 205.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53898.1 | 0 | 53898.1 | 292562 | -749883 | 22 | 23 | 292562 | -1749883
12 | 26 | 20 | 2 | 24.2281 | 0 | 62.7906 | 0 | 13.6633 | 0 | 5.9371 | 12.9754 | 0 | 0 | 0 | 7.2 | 126.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38575.2 | 0 | 38575.2 | 172303 | -19266.5 | 22 | 23 | 172303 | -1019266.5
12 | 26 | 21 | 2 | 18.7229 | 0 | 54.6418 | 0 | 13.5193 | 0 | 5.9354 | 17.5105 | 0 | 0 | 0 | 7.2 | 117.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34242.2 | 0 | 34242.2 | 174330 | -58736.8 | 22 | 23 | 174330 | -1058736.8
12 | 26 | 22 | 2 | 13.825 | 0 | 48.8953 | 0 | 12.1731 | 0 | 5.9131 | 17.5105 | 0 | 0 | 0 | 7.2 | 105.517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21036.7 | 0 | 21036.7 | 156548 | -95866.8 | 22 | 23 | 156548 | -1095866.8
12 | 26 | 23 | 2 | 11.1963 | 0 | 44.3342 | 0 | 11.1933 | 0 | 5.9027 | 17.5105 | 0 | 0 | 0 | 6.4 | 96.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11347.2 | 0 | 11347.2 | 143231 | -132578 | 22 | 23 | 143231 | -1132578
12 | 26 | 24 | 2 | 10.3176 | 0 | 42.5403 | 0 | 10.7639 | 0 | 5.8998 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.6321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9883.11 | 0 | 9883.11 | 137748 | -151509 | 22 | 23 | 137748 | -1151509
12 | 27 | 1 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.6056 | 0 | 5.899 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.99 | 0 | 9886.99 | 135917 | -169014 | 23 | 23 | 135917 | -1169014
12 | 27 | 2 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.5271 | 0 | 5.8986 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9889.75 | 0 | 9889.75 | 134867 | -176867 | 23 | 24 | 134867 | -1176867
12 | 27 | 3 | 3 | 10.8489 | 0 | 42.3304 | 0 | 10.4815 | 0 | 5.8983 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9892.13 | 0 | 9892.13 | 134047 | -183146 | 23 | 24 | 134047 | -1183146
12 | 27 | 4 | 3 | 10.8489 | 0 | 42.3304 | 10.6453 | 0 | 0 | 5.8991 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9894.17 | 0 | 9894.17 | 133460 | -186831 | 25 | 25 | 133460 | -1186831
12 | 27 | 5 | 3 | 11.8202 | 0 | 44.8242 | 10.7156 | 0 | 0 | 5.8994 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10979 | 0 | 10979 | 136197 | -187249 | 26 | 27 | 136197 | -1187249
12 | 27 | 6 | 3 | 24.3093 | 0 | 69.9783 | 0 | 14.1983 | 0 | 5.9524 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26528.1 | 0 | 26528.1 | 186949 | -153185 | 28 | 28 | 186949 | -1153185
12 | 27 | 7 | 3 | 49.0171 | 0 | 140.608 | 51.1995 | 0 | 0 | 12.2312 | 19.331 | 0 | 0 | 0 | 3.2 | 275.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78433.2 | 0 | 78433.2 | 317016 | -905623 | 28 | 28 | 317016 | -1905623
12 | 27 | 8 | 3 | 52.899 | 0 | 168.222 | 43.8713 | 0 | 0 | 7.0075 | 19.1388 | 0 | 0 | 0 | 0.8 | 291.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95238.3 | 0 | 95238.3 | 379074 | -784579 | 27 | 28 | 379074 | -1784579
12 | 27 | 9 | 3 | 45.4253 | 0 | 173.795 | 33.5609 | 0 | 0 | 25.2392 | 19.0363 | 0 | 0 | 0 | 0 | 297.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131788 | 0 | 131788 | 398011 | -663392 | 27 | 28 | 398011 | -1663392
12 | 27 | 10 | 3 | 41.82 | 0 | 172.186 | 32.6075 | 0 | 0 | 25.2497 | 19.0363 | 0 | 0 | 0 | 0 | 290.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155057 | 0 | 155057 | 396269 | -627853 | 27 | 28 | 396269 | -1627853
12 | 27 | 11 | 3 | 42.275 | 0 | 163.102 | 33.6718 | 0 | 0 | 25.2616 | 19.0363 | 0 | 0 | 0 | 0 | 283.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158374 | 0 | 158374 | 385160 | -612154 | 27 | 29 | 385160 | -1612154
12 | 27 | 12 | 3 | 41.3042 | 0 | 149.692 | 30.3406 | 0 | 0 | 25.2664 | 19.0363 | 0 | 0 | 0 | 0 | 265.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158372 | 0 | 158372 | 369851 | -557361 | 27 | 29 | 369851 | -1557361
12 | 27 | 13 | 3 | 39.913 | 0 | 150.207 | 28.864 | 0 | 0 | 20.0422 | 19.0363 | 0 | 0 | 0 | 0 | 258.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158370 | 0 | 158370 | 351961 | -547272 | 27 | 29 | 351961 | -1547272
12 | 27 | 14 | 3 | 42.4084 | 0 | 165.698 | 25.8914 | 0 | 0 | 25.26 | 19.0363 | 0 | 0 | 0 | 0 | 278.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158367 | 0 | 158367 | 385111 | -516371 | 27 | 28 | 385111 | -1516371
12 | 27 | 15 | 3 | 41.6908 | 0 | 172.702 | 0 | 25.5609 | 0 | 6.2641 | 19.0363 | 0 | 0 | 0 | 0 | 265.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156321 | 0 | 156321 | 403596 | -502374 | 27 | 28 | 403596 | -1502374
12 | 27 | 16 | 3 | 45.3566 | 0 | 173.986 | 0 | 25.7668 | 0 | 6.2649 | 19.0363 | 0 | 0 | 0 | 0 | 270.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142113 | 0 | 142113 | 406691 | -508477 | 27 | 28 | 406691 | -1508477
12 | 27 | 17 | 3 | 56.1815 | 0 | 169.782 | 26.7605 | 0 | 0 | 25.2682 | 19.0363 | 0 | 0 | 0 | 2.4 | 299.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116009 | 0 | 116009 | 397388 | -527427 | 27 | 28 | 397388 | -1527427
12 | 27 | 18 | 3 | 49.7836 | 0 | 152.497 | 31.82 | 0 | 0 | 25.268 | 19.0363 | 0 | 0 | 0 | 6.4 | 284.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87004.7 | 0 | 87004.7 | 386773 | -575827 | 27 | 28 | 386773 | -1575827
12 | 27 | 19 | 3 | 34.11 | 0 | 93.4203 | 35.1986 | 0 | 0 | 25.2763 | 19.0363 | 0 | 0 | 0 | 7.2 | 214.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53879.1 | 0 | 53879.1 | 300082 | -602844 | 27 | 28 | 300082 | -1602844
12 | 27 | 20 | 3 | 24.2281 | 0 | 62.7906 | 0 | 14.3943 | 0 | 5.9514 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38556.8 | 0 | 38556.8 | 178912 | -16301.8 | 27 | 28 | 178912 | -1016301.8
12 | 27 | 21 | 3 | 18.7229 | 0 | 54.6418 | 0 | 12.7435 | 0 | 5.9195 | 12.9754 | 0 | 0 | 0 | 7.2 | 112.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34224.4 | 0 | 34224.4 | 159926 | -25697.4 | 27 | 28 | 159926 | -1025697.4
12 | 27 | 22 | 3 | 13.825 | 0 | 48.8953 | 0 | 13.2463 | 0 | 5.9284 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21017.6 | 0 | 21017.6 | 167840 | -49777.3 | 27 | 27 | 167840 | -1049777.3
12 | 27 | 23 | 3 | 11.1963 | 0 | 44.3342 | 0 | 12.0784 | 0 | 5.9108 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11327 | 0 | 11327 | 152546 | -76780.2 | 26 | 27 | 152546 | -1076780.2
12 | 27 | 24 | 3 | 10.3176 | 0 | 42.5403 | 0 | 11.5699 | 0 | 5.9053 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.95 | 0 | 9862.95 | 146071 | -96694.6 | 25 | 26 | 146071 | -1096694.6
12 | 28 | 1 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.328 | 0 | 5.9033 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9866.87 | 0 | 9866.87 | 143522 | -114697 | 24 | 25 | 143522 | -1114697
12 | 28 | 2 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.1733 | 0 | 5.9022 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9869.94 | 0 | 9869.94 | 142038 | -132705 | 23 | 24 | 142038 | -1132705
12 | 28 | 3 | 4 | 10.73 | 0 | 42.3304 | 0 | 11.039 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9872.61 | 0 | 9872.61 | 140770 | -147068 | 22 | 23 | 140770 | -1147068
12 | 28 | 4 | 4 | 10.73 | 0 | 42.3304 | 0 | 10.9223 | 0 | 5.9007 | 17.3638 | 0 | 0 | 0 | 4.8 | 92.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9874.91 | 0 | 9874.91 | 139748 | -157960 | 22 | 23 | 139748 | -1157960
12 | 28 | 5 | 4 | 11.8202 | 0 | 44.8242 | 0 | 11.0513 | 0 | 5.9017 | 17.5105 | 0 | 0 | 0 | 4.8 | 95.9079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10960.1 | 0 | 10960.1 | 141973 | -166883 | 22 | 23 | 141973 | -1166883
12 | 28 | 6 | 4 | 24.3093 | 0 | 69.9783 | 0 | 14.2377 | 0 | 5.9547 | 17.5105 | 0 | 0 | 0 | 4.8 | 136.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26509.6 | 0 | 26509.6 | 189064 | -144756 | 22 | 23 | 189064 | -1144756
12 | 28 | 7 | 4 | 49.0171 | 0 | 140.608 | 49.9771 | 0 | 0 | 7.2073 | 19.2564 | 0 | 0 | 0 | 3.2 | 269.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78415.1 | 0 | 78415.1 | 320681 | -900196 | 23 | 24 | 320681 | -1900196
12 | 28 | 8 | 4 | 53.0239 | 0 | 168.222 | 43.9494 | 0 | 0 | 6.7416 | 19.0968 | 0 | 0 | 0 | 0.8 | 291.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95220.6 | 0 | 95220.6 | 382566 | -796011 | 24 | 24 | 382566 | -1796011
12 | 28 | 9 | 4 | 46.31 | 0 | 173.795 | 33.6161 | 0 | 0 | 25.2374 | 19.0363 | 0 | 0 | 0 | 0 | 297.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131774 | 0 | 131774 | 401489 | -671680 | 24 | 25 | 401489 | -1671680
12 | 28 | 10 | 4 | 41.9736 | 0 | 172.186 | 33.8474 | 0 | 0 | 25.2471 | 19.0363 | 0 | 0 | 0 | 0 | 292.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155044 | 0 | 155044 | 399307 | -647804 | 24 | 25 | 399307 | -1647804
12 | 28 | 11 | 4 | 42.3555 | 0 | 163.102 | 37.2329 | 0 | 0 | 25.2567 | 19.0363 | 0 | 0 | 0 | 0 | 286.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158362 | 0 | 158362 | 389364 | -665672 | 24 | 24 | 389364 | -1665672
12 | 28 | 12 | 4 | 41.3783 | 0 | 149.692 | 33.4528 | 0 | 0 | 25.2619 | 19.0363 | 0 | 0 | 0 | 0 | 268.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158360 | 0 | 158360 | 371393 | -609791 | 23 | 24 | 371393 | -1609791
12 | 28 | 13 | 4 | 39.913 | 0 | 150.207 | 32.1803 | 0 | 0 | 6.2542 | 19.0363 | 0 | 0 | 0 | 0 | 247.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158359 | 0 | 158359 | 354222 | -603148 | 23 | 24 | 354222 | -1603148
12 | 28 | 14 | 4 | 42.3452 | 0 | 165.698 | 28.2084 | 0 | 0 | 6.251 | 19.0363 | 0 | 0 | 0 | 0 | 261.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158356 | 0 | 158356 | 387295 | -560041 | 23 | 24 | 387295 | -1560041
12 | 28 | 15 | 4 | 41.82 | 0 | 172.702 | 28.0257 | 0 | 0 | 6.2562 | 19.0363 | 0 | 0 | 0 | 0 | 267.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156310 | 0 | 156310 | 405820 | -555696 | 23 | 24 | 405820 | -1555696
12 | 28 | 16 | 4 | 46.1635 | 0 | 173.986 | 28.459 | 0 | 0 | 6.2571 | 19.0363 | 0 | 0 | 0 | 0 | 273.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142102 | 0 | 142102 | 408674 | -561936 | 23 | 24 | 408674 | -1561936
12 | 28 | 17 | 4 | 56.1553 | 0 | 169.782 | 31.0393 | 0 | 0 | 6.2575 | 19.0363 | 0 | 0 | 0 | 2.4 | 284.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115999 | 0 | 115999 | 399156 | -597126 | 22 | 23 | 399156 | -1597126
12 | 28 | 18 | 4 | 49.7836 | 0 | 152.497 | 37.0069 | 0 | 0 | 6.2584 | 19.0363 | 0 | 0 | 0 | 6.4 | 270.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86995.5 | 0 | 86995.5 | 388274 | -651869 | 22 | 23 | 388274 | -1651869
12 | 28 | 19 | 4 | 34.11 | 0 | 93.4203 | 41.4155 | 0 | 0 | 6.5817 | 19.0363 | 0 | 0 | 0 | 7.2 | 201.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53870.5 | 0 | 53870.5 | 305702 | -686593 | 21 | 22 | 305702 | -1686593
12 | 28 | 20 | 4 | 24.2281 | 0 | 62.7906 | 0 | 14.1794 | 0 | 5.9492 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38548.4 | 0 | 38548.4 | 180040 | -19199.4 | 19 | 21 | 180040 | -1019199.4
12 | 28 | 21 | 4 | 18.7229 | 0 | 54.6418 | 0 | 14.2998 | 0 | 5.9536 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34215.9 | 0 | 34215.9 | 185799 | -42990 | 18 | 20 | 185799 | -1042990
12 | 28 | 22 | 4 | 13.825 | 0 | 48.8953 | 0 | 12.817 | 0 | 5.9237 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21009.2 | 0 | 21009.2 | 166882 | -88398.3 | 14 | 16 | 166882 | -1088398.3
12 | 28 | 23 | 4 | 11.1963 | 0 | 44.3342 | 0 | 11.6754 | 0 | 5.9081 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11319.7 | 0 | 11319.7 | 152533 | -131534 | 11 | 12 | 152533 | -1131534
12 | 28 | 24 | 4 | 10.3176 | 0 | 42.5403 | 0 | 11.0683 | 0 | 5.9028 | 17.5105 | 0 | 0 | 0 | 5.6 | 92.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.92 | 0 | 9855.92 | 146047 | -170897 | 7 | 8 | 146047 | -1170897
12 | 29 | 1 | 5 | 10.8489 | 0 | 42.3304 | 0 | 10.7539 | 0 | 5.9009 | 17.3638 | 0 | 0 | 0 | 4.8 | 91.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.38 | 0 | 9860.38 | 143574 | -203531 | 6 | 7 | 143574 | -1203531
12 | 29 | 2 | 5 | 10.8489 | 0 | 42.3304 | 12.3841 | 0 | 0 | 5.9131 | 17.3638 | 0 | 0 | 0 | 4.8 | 93.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.93 | 0 | 9863.93 | 141837 | -226579 | 6 | 6 | 141837 | -1226579
12 | 29 | 3 | 5 | 10.8489 | 0 | 42.3304 | 13.1985 | 0 | 0 | 5.9235 | 17.3638 | 0 | 0 | 0 | 4.8 | 94.4652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.23 | 0 | 9867.23 | 140357 | -240306 | 5 | 5 | 140357 | -1240306
12 | 29 | 4 | 5 | 10.8489 | 0 | 42.3304 | 14.1666 | 0 | 0 | 5.9436 | 17.3638 | 0 | 0 | 0 | 4.8 | 95.4533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9870.28 | 0 | 9870.28 | 139497 | -259875 | 3 | 3 | 139497 | -1259875
12 | 29 | 5 | 5 | 11.8202 | 0 | 44.8242 | 15.2729 | 0 | 0 | 5.9714 | 17.5105 | 0 | 0 | 0 | 4.8 | 100.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10956.2 | 0 | 10956.2 | 140430 | -275922 | 1 | 2 | 140430 | -1275922
12 | 29 | 6 | 5 | 24.3093 | 0 | 69.9783 | 14.9159 | 0 | 0 | 5.9629 | 17.5105 | 0 | 0 | 0 | 4.8 | 137.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26506.3 | 0 | 26506.3 | 186405 | -261938 | -1 | 0 | 186405 | -1261938
12 | 29 | 7 | 5 | 49.0171 | 0 | 140.608 | 68.7365 | 0 | 0 | 11.6626 | 19.5181 | 0 | 0 | 0 | 3.2 | 292.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78412.4 | 0 | 78412.4 | 318614 | -1284870 | -1 | 0 | 318614 | -2284870
12 | 29 | 8 | 5 | 52.4108 | 0 | 168.222 | 61.6035 | 0 | 0 | 12.294 | 19.2505 | 0 | 0 | 0 | 0.8 | 314.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95218.5 | 0 | 95218.5 | 380614 | -1192050 | -1 | 0 | 380614 | -2192050
12 | 29 | 9 | 5 | 42.5393 | 0 | 173.795 | 51.6723 | 0 | 0 | 25.2089 | 19.0363 | 0 | 0 | 0 | 0 | 312.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131771 | 0 | 131771 | 400005 | -1012240 | -1 | 0 | 400005 | -2012240
12 | 29 | 10 | 5 | 41.1468 | 0 | 172.186 | 46.9445 | 0 | 0 | 25.2144 | 19.0363 | 0 | 0 | 0 | 0 | 304.528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155042 | 0 | 155042 | 397805 | -912766 | 2 | 3 | 397805 | -1912766
12 | 29 | 11 | 5 | 41.2514 | 0 | 163.102 | 48.5378 | 0 | 0 | 25.2166 | 19.0363 | 0 | 0 | 0 | 0 | 297.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158361 | 0 | 158361 | 382560 | -923992 | 5 | 6 | 382560 | -1923992
12 | 29 | 12 | 5 | 40.7788 | 0 | 149.692 | 43.3751 | 0 | 0 | 12.5859 | 19.0363 | 0 | 0 | 0 | 0 | 265.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158361 | 0 | 158361 | 356304 | -789317 | 7 | 9 | 356304 | -1789317
12 | 29 | 13 | 5 | 39.8283 | 0 | 150.207 | 41.2998 | 0 | 0 | 6.2283 | 19.0363 | 0 | 0 | 0 | 0 | 256.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158359 | 0 | 158359 | 352364 | -767115 | 9 | 10 | 352364 | -1767115
12 | 29 | 14 | 5 | 41.3067 | 0 | 165.698 | 35.4401 | 0 | 0 | 6.2285 | 19.0363 | 0 | 0 | 0 | 0 | 267.709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158355 | 0 | 158355 | 385322 | -703001 | 10 | 12 | 385322 | -1703001
12 | 29 | 15 | 5 | 40.7182 | 0 | 172.702 | 32.3106 | 0 | 0 | 6.2427 | 19.0363 | 0 | 0 | 0 | 0 | 271.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156309 | 0 | 156309 | 404225 | -639323 | 11 | 13 | 404225 | -1639323
12 | 29 | 16 | 5 | 41.2052 | 0 | 173.986 | 35.0836 | 0 | 0 | 6.2385 | 19.0363 | 0 | 0 | 0 | 0 | 275.549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142102 | 0 | 142102 | 407317 | -692164 | 11 | 13 | 407317 | -1692164
12 | 29 | 17 | 5 | 54.699 | 0 | 169.782 | 37.272 | 0 | 0 | 6.2342 | 19.0363 | 0 | 0 | 0 | 2.4 | 289.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115998 | 0 | 115998 | 397455 | -733107 | 11 | 12 | 397455 | -1733107
12 | 29 | 18 | 5 | 49.7836 | 0 | 152.497 | 43.2059 | 0 | 0 | 6.2312 | 19.0363 | 0 | 0 | 0 | 6.4 | 277.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86995.3 | 0 | 86995.3 | 386208 | -795938 | 11 | 12 | 386208 | -1795938
12 | 29 | 19 | 5 | 34.11 | 0 | 93.4203 | 46.2861 | 0 | 0 | 6.2474 | 19.0363 | 0 | 0 | 0 | 7.2 | 206.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53870.4 | 0 | 53870.4 | 306282 | -776021 | 12 | 13 | 306282 | -1776021
12 | 29 | 20 | 5 | 24.2281 | 0 | 62.7906 | 0 | 14.0784 | 0 | 5.9469 | 12.9754 | 0 | 0 | 0 | 7.2 | 127.219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38547.8 | 0 | 38547.8 | 178711 | -12783.1 | 13 | 14 | 178711 | -1012783.1
12 | 29 | 21 | 5 | 18.7229 | 0 | 54.6418 | 0 | 14.3203 | 0 | 5.952 | 17.5105 | 0 | 0 | 0 | 7.2 | 118.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34214.4 | 0 | 34214.4 | 183245 | -57674.3 | 14 | 15 | 183245 | -1057674.3
12 | 29 | 22 | 5 | 13.825 | 0 | 48.8953 | 0 | 12.8151 | 0 | 5.9228 | 17.5105 | 0 | 0 | 0 | 7.2 | 106.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21006.3 | 0 | 21006.3 | 165288 | -96295.3 | 14 | 15 | 165288 | -1096295.3
12 | 29 | 23 | 5 | 11.1963 | 0 | 44.3342 | 0 | 11.7672 | 0 | 5.9082 | 17.5105 | 0 | 0 | 0 | 6.4 | 97.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11316.6 | 0 | 11316.6 | 151349 | -120908 | 14 | 16 | 151349 | -1120908
12 | 29 | 24 | 5 | 10.3176 | 0 | 42.5403 | 0 | 11.5499 | 0 | 5.9055 | 17.5105 | 0 | 0 | 0 | 5.6 | 93.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9852.62 | 0 | 9852.62 | 147122 | -141955 | 15 | 16 | 147122 | -1141955
12 | 30 | 1 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.4427 | 0 | 5.9037 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.91 | 0 | 9856.91 | 142864 | -151064 | 15 | 16 | 142864 | -1151064
12 | 30 | 2 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.2329 | 0 | 5.9023 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9860.12 | 0 | 9860.12 | 141277 | -158166 | 15 | 16 | 141277 | -1158166
12 | 30 | 3 | 6 | 6.3817 | 0 | 42.7453 | 0 | 11.0206 | 0 | 5.9013 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.2126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9863.22 | 0 | 9863.22 | 140739 | -177747 | 15 | 16 | 140739 | -1177747
12 | 30 | 4 | 6 | 6.3817 | 0 | 42.7453 | 0 | 10.7959 | 0 | 5.9001 | 17.3638 | 0 | 0 | 0 | 4.8 | 87.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9865.29 | 0 | 9865.29 | 138861 | -191158 | 15 | 16 | 138861 | -1191158
12 | 30 | 5 | 6 | 6.3817 | 0 | 42.7453 | 11.4756 | 0 | 0 | 5.904 | 17.3638 | 0 | 0 | 0 | 4.8 | 88.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.91 | 0 | 9867.91 | 138838 | -207014 | 15 | 16 | 138838 | -1207014
12 | 30 | 6 | 6 | 6.3817 | 0 | 42.7453 | 11.9332 | 0 | 0 | 5.9069 | 17.3638 | 0 | 0 | 0 | 4.8 | 89.1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9870.29 | 0 | 9870.29 | 136731 | -210626 | 15 | 16 | 136731 | -1210626
12 | 30 | 7 | 6 | 6.3817 | 0 | 42.7453 | 12.2832 | 0 | 0 | 5.9097 | 17.3638 | 0 | 0 | 0 | 3.2 | 87.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9872.76 | 0 | 9872.76 | 136398 | -218689 | 15 | 16 | 136398 | -1218689
12 | 30 | 8 | 6 | 6.3544 | 0 | 42.7453 | 70.3462 | 0 | 0 | 6.2117 | 19.7736 | 0 | 0 | 0 | 0.8 | 146.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9875.08 | 0 | 9875.08 | 123424 | -1120550 | 15 | 16 | 123424 | -2120550
12 | 30 | 9 | 6 | 6.5232 | 0 | 42.7453 | 61.6971 | 0 | 0 | 25.2238 | 19.3499 | 0 | 0 | 0 | 0 | 155.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9877.06 | 0 | 9877.06 | 122776 | -988291 | 15 | 16 | 122776 | -1988291
12 | 30 | 10 | 6 | 6.7571 | 0 | 42.7453 | 51.3492 | 0 | 0 | 25.2251 | 19.0569 | 0 | 0 | 0 | 0 | 145.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9862.43 | 0 | 9862.43 | 122235 | -869389 | 15 | 16 | 122235 | -1869389
12 | 30 | 11 | 6 | 6.187 | 0 | 42.7453 | 47.124 | 0 | 0 | 25.2269 | 18.9463 | 0 | 0 | 0 | 0 | 140.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9859.7 | 0 | 9859.7 | 121700 | -810488 | 16 | 17 | 121700 | -1810488
12 | 30 | 12 | 6 | 6.231 | 0 | 42.7453 | 45.9489 | 0 | 0 | 7.2059 | 18.913 | 0 | 0 | 0 | 0 | 121.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.67 | 0 | 9857.67 | 121201 | -797663 | 16 | 17 | 121201 | -1797663
12 | 30 | 13 | 6 | 6.2031 | 0 | 42.7453 | 44.6879 | 0 | 0 | 6.2227 | 18.8896 | 0 | 0 | 0 | 0 | 118.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856.62 | 0 | 9856.62 | 120752 | -781769 | 16 | 17 | 120752 | -1781769
12 | 30 | 14 | 6 | 6.3422 | 0 | 42.7453 | 44.4249 | 0 | 0 | 6.2217 | 18.8896 | 0 | 0 | 0 | 0 | 118.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9856 | 0 | 9856 | 120283 | -780677 | 16 | 17 | 120283 | -1780677
12 | 30 | 15 | 6 | 6.5499 | 0 | 42.7453 | 0 | 10.7063 | 0 | 5.8992 | 15.3158 | 0 | 0 | 0 | 0 | 81.2164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.55 | 0 | 9855.55 | 135743 | -19329.2 | 16 | 17 | 135743 | -1019329.2
12 | 30 | 16 | 6 | 7.0569 | 0 | 42.7453 | 0 | 10.7172 | 0 | 5.8997 | 17.3638 | 0 | 0 | 0 | 0 | 83.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9855.49 | 0 | 9855.49 | 138518 | -81336.3 | 14 | 15 | 138518 | -1081336.3
12 | 30 | 17 | 6 | 8.6289 | 0 | 42.7453 | 0 | 10.326 | 0 | 5.898 | 17.3638 | 0 | 0 | 0 | 2.4 | 87.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9861.14 | 0 | 9861.14 | 134217 | -129039 | 12 | 14 | 134217 | -1129039
12 | 30 | 18 | 6 | 8.7973 | 0 | 42.7453 | 0 | 10.0897 | 0 | 5.8974 | 17.3638 | 0 | 0 | 0 | 6.4 | 91.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9867.32 | 0 | 9867.32 | 132133 | -182918 | 11 | 12 | 132133 | -1182918
12 | 30 | 19 | 6 | 8.7973 | 0 | 42.7453 | 11.3273 | 0 | 0 | 5.9055 | 17.3638 | 0 | 0 | 0 | 7.2 | 93.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9871.02 | 0 | 9871.02 | 130666 | -212402 | 5 | 7 | 130666 | -1212402
12 | 30 | 20 | 6 | 8.7973 | 0 | 42.7453 | 13.2837 | 0 | 0 | 5.9312 | 17.3638 | 0 | 0 | 0 | 7.2 | 95.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9874.68 | 0 | 9874.68 | 129362 | -247722 | 0 | 1 | 129362 | -1247722
12 | 30 | 21 | 6 | 8.7973 | 0 | 42.7453 | 15.6629 | 0 | 0 | 5.9876 | 17.3638 | 0 | 0 | 0 | 7.2 | 97.7568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9877.74 | 0 | 9877.74 | 128095 | -283269 | -5 | -4 | 128095 | -1283269
12 | 30 | 22 | 6 | 8.7973 | 0 | 42.7453 | 17.8183 | 0 | 0 | 6.064 | 17.3638 | 0 | 0 | 0 | 7.2 | 99.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9880.74 | 0 | 9880.74 | 127070 | -315450 | -8 | -7 | 127070 | -1315450
12 | 30 | 23 | 6 | 8.7973 | 0 | 42.7453 | 19.9463 | 0 | 0 | 6.1609 | 17.3638 | 0 | 0 | 0 | 6.4 | 101.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9883.78 | 0 | 9883.78 | 126044 | -347827 | -11 | -10 | 126044 | -1347827
12 | 30 | 24 | 6 | 8.7973 | 0 | 42.7453 | 22.0115 | 0 | 0 | 6.2746 | 17.3638 | 0 | 0 | 0 | 5.6 | 102.792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9886.91 | 0 | 9886.91 | 124994 | -378411 | -14 | -13 | 124994 | -1378411
12 | 31 | 1 | 7 | 5.1054 | 0 | 42.7453 | 24.3367 | 0 | 0 | 6.29 | 17.3638 | 0 | 0 | 0 | 4.8 | 100.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3776.08 | 0 | 3776.08 | 123884 | -415410 | -14 | -13 | 123884 | -1415410
12 | 31 | 2 | 7 | 5.1054 | 0 | 42.7453 | 26.3496 | 0 | 0 | 6.277 | 17.3638 | 0 | 0 | 0 | 4.8 | 102.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3779.19 | 0 | 3779.19 | 123085 | -442612 | -14 | -13 | 123085 | -1442612
12 | 31 | 3 | 7 | 5.1054 | 0 | 42.7453 | 27.7491 | 0 | 0 | 6.267 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3782.5 | 0 | 3782.5 | 122387 | -464501 | -14 | -13 | 122387 | -1464501
12 | 31 | 4 | 7 | 5.1054 | 0 | 42.7453 | 28.5136 | 0 | 0 | 6.2656 | 17.3638 | 0 | 0 | 0 | 4.8 | 104.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3784.64 | 0 | 3784.64 | 121764 | -480268 | -14 | -13 | 121764 | -1480268
12 | 31 | 5 | 7 | 5.1054 | 0 | 42.7453 | 29.3984 | 0 | 0 | 6.2641 | 17.3638 | 0 | 0 | 0 | 4.8 | 105.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.43 | 0 | 3786.43 | 121580 | -493336 | -14 | -13 | 121580 | -1493336
12 | 31 | 6 | 7 | 5.1054 | 0 | 42.7453 | 30.1375 | 0 | 0 | 6.2604 | 17.3638 | 0 | 0 | 0 | 4.8 | 106.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.04 | 0 | 3788.04 | 120660 | -502638 | -14 | -13 | 120660 | -1502638
12 | 31 | 7 | 7 | 5.1054 | 0 | 42.7453 | 30.6534 | 0 | 0 | 6.2596 | 17.3638 | 0 | 0 | 0 | 3.2 | 105.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3789.54 | 0 | 3789.54 | 120674 | -511647 | -14 | -13 | 120674 | -1511647
12 | 31 | 8 | 7 | 5.026 | 0 | 42.7453 | 30.497 | 0 | 0 | 6.2611 | 17.3638 | 0 | 0 | 0 | 0.8 | 102.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3790.95 | 0 | 3790.95 | 119793 | -507830 | -14 | -13 | 119793 | -1507830
12 | 31 | 9 | 7 | 4.0793 | 0 | 42.7453 | 27.3825 | 0 | 0 | 6.2705 | 17.3638 | 0 | 0 | 0 | 0 | 97.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792.31 | 0 | 3792.31 | 119711 | -453708 | -14 | -13 | 119711 | -1453708
12 | 31 | 10 | 7 | 4.28 | 0 | 42.7453 | 24.3217 | 0 | 0 | 6.28 | 17.3638 | 0 | 0 | 0 | 0 | 94.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3793.61 | 0 | 3793.61 | 119822 | -403455 | -13 | -12 | 119822 | -1403455
12 | 31 | 11 | 7 | 4.1793 | 0 | 42.7453 | 22.6467 | 0 | 0 | 6.2793 | 17.3638 | 0 | 0 | 0 | 0 | 93.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3794.82 | 0 | 3794.82 | 119829 | -378574 | -11 | -10 | 119829 | -1378574
12 | 31 | 12 | 7 | 4.1588 | 0 | 42.7453 | 22.124 | 0 | 0 | 6.2467 | 17.3638 | 0 | 0 | 0 | 0 | 92.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3795.85 | 0 | 3795.85 | 119794 | -370061 | -10 | -9 | 119794 | -1370061
12 | 31 | 13 | 7 | 4.153 | 0 | 42.7453 | 21.7534 | 0 | 0 | 6.2245 | 17.3638 | 0 | 0 | 0 | 0 | 92.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3796.89 | 0 | 3796.89 | 119366 | -365132 | -10 | -9 | 119366 | -1365132
12 | 31 | 14 | 7 | 4.1534 | 0 | 42.7453 | 21.1435 | 0 | 0 | 6.1882 | 17.3638 | 0 | 0 | 0 | 0 | 91.5942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3797.89 | 0 | 3797.89 | 118973 | -354811 | -11 | -10 | 118973 | -1354811
12 | 31 | 15 | 7 | 4.1646 | 0 | 42.7453 | 21.472 | 0 | 0 | 6.2084 | 17.3638 | 0 | 0 | 0 | 0 | 91.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3798.96 | 0 | 3798.96 | 118707 | -363822 | -11 | -10 | 118707 | -1363822
12 | 31 | 16 | 7 | 4.3033 | 0 | 42.7453 | 23.5598 | 0 | 0 | 6.2767 | 17.3638 | 0 | 0 | 0 | 0 | 94.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3800 | 0 | 3800 | 120129 | -398883 | -11 | -10 | 120129 | -1398883
12 | 31 | 17 | 7 | 6.1862 | 0 | 42.7453 | 26.5655 | 0 | 0 | 6.2722 | 17.3638 | 0 | 0 | 0 | 2.4 | 101.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3800.99 | 0 | 3800.99 | 118086 | -448931 | -12 | -11 | 118086 | -1448931
12 | 31 | 18 | 7 | 6.6633 | 0 | 42.7453 | 29.4176 | 0 | 0 | 6.2645 | 17.3638 | 0 | 0 | 0 | 6.4 | 108.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3802.02 | 0 | 3802.02 | 117818 | -492264 | -12 | -11 | 117818 | -1492264
12 | 31 | 19 | 7 | 6.6633 | 0 | 42.7453 | 30.5924 | 0 | 0 | 6.2618 | 17.3638 | 0 | 0 | 0 | 7.2 | 110.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.04 | 0 | 3803.04 | 117369 | -510097 | -12 | -11 | 117369 | -1510097
12 | 31 | 20 | 7 | 6.6633 | 0 | 42.7453 | 31.0332 | 0 | 0 | 6.261 | 17.3638 | 0 | 0 | 0 | 7.2 | 111.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3804.05 | 0 | 3804.05 | 116661 | -516635 | -11 | -10 | 116661 | -1516635
12 | 31 | 21 | 7 | 6.6633 | 0 | 42.7453 | 31.4934 | 0 | 0 | 6.2604 | 17.3638 | 0 | 0 | 0 | 7.2 | 111.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805.03 | 0 | 3805.03 | 117599 | -523432 | -11 | -10 | 117599 | -1523432
12 | 31 | 22 | 7 | 6.6633 | 0 | 42.7453 | 31.515 | 0 | 0 | 6.2601 | 17.3638 | 0 | 0 | 0 | 7.2 | 111.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805.95 | 0 | 3805.95 | 116124 | -522792 | -11 | -10 | 116124 | -1522792
12 | 31 | 23 | 7 | 6.6633 | 0 | 42.7453 | 32.0562 | 0 | 0 | 6.2597 | 17.3638 | 0 | 0 | 0 | 6.4 | 111.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3806.83 | 0 | 3806.83 | 116840 | -531342 | -11 | -11 | 116840 | -1531342
12 | 31 | 24 | 7 | 6.6633 | 0 | 42.7453 | 32.2231 | 0 | 0 | 6.2595 | 17.3638 | 0 | 0 | 0 | 5.6 | 110.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3807.69 | 0 | 3807.69 | 115591 | -531711 | -12 | -11 | 115591 | -1531711

## mod for DHRC
Use the pumps in eQUEST
Zero the pumps in TRNSYS
Set the BHE to zero
Then, either:
1 | Sum the chiller, CW pump, and tower elec consump from eQUEST, and use with SUM of load to calc an annual global CHW COP
Make this the COP of the air cooled chiller in TRNSYS
Use linear curves for off peak performance (all 1's in both sets of chiller curves)
For basic, single energy analysis
2 | Sum the chiller, CW pump, and tower peak power from eQUEST, and use with peak load to calc a peak CHW system COP
Make this the COP of the air cooled chiller in TRNSYS
Use the eQUEST off peak performance curves to create equivalent curves in TRNSYS
For detailed analysis, optimization, sizing, control analysis
3 | Modify the COP of the chiller in TRNSYS until the annual average COP of the CHW systems in both TRNSYS and eQUEST is equal
For ???